Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07618 | 148.81 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07823 | 149.61 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09275 | 152.28 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09275 | 159.07 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09275 | 161.78 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09275 | 163.27 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.10438 | 163.49 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07681 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07681 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08994 | 118.97 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09394 | 109.05 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09394 | 109.05 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09413 | 108.48 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09413 | 108.48 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09415 | 108.87 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09416 | 108.48 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09416 | 108.65 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.39 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.46 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.48 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.64 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.64 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.67 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.67 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.79 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.82 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.82 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.87 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.89 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.9 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.9 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.92 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.94 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.94 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.99 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.99 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.03 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.04 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.14 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.15 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.15 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.16 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.17 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.17 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.17 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.18 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.18 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.18 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.22 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.22 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.23 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.24 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.26 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.3 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.37 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.4 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.49 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.49 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.49 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.49 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.49 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.53 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.53 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.53 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.58 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.58 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.59 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.69 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.69 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.69 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.75 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.75 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.78 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 110.66 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 110.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 111.04 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 111.24 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 113.28 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09422 | 108.45 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09422 | 108.45 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09422 | 108.45 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09424 | 108.69 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09424 | 108.76 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09425 | 108.77 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09426 | 108.28 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09427 | 108.82 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09427 | 108.9 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09427 | 108.9 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09438 | 108.98 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0944 | 108.95 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09445 | 108.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09446 | 109.13 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09446 | 109.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09456 | 109.44 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09464 | 108.99 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09468 | 109.39 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09468 | 109.39 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09521 | 111.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09521 | 111.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09525 | 111.09 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09536 | 110.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09536 | 110.68 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09537 | 110.71 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09537 | 110.82 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09556 | 110.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09559 | 110.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09585 | 113.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09614 | 112.35 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09614 | 112.35 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09631 | 112.1 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09669 | 111.42 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09709 | 111.03 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0971 | 111.04 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09804 | 115.8 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0981 | 115.86 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09826 | 116.15 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09826 | 116.15 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09975 | 116.25 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09997 | 117.38 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1021 | 117.14 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1021 | 117.29 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11095 | 121.61 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11095 | 122.52 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13458 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14392 | 138.42 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14459 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14459 | 131.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14459 | 135.41 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14459 | 135.88 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14459 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14459 | 139.6 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14459 | 139.63 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14459 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15603 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06694 | 104.17 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06694 | 104.17 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07838 | 103.69 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08544 | 100.92 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08549 | 100.97 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08563 | 101.22 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08563 | 101.22 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08693 | 101.31 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08712 | 102.3 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08898 | 102.08 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08898 | 102.22 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09669 | 105.99 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09669 | 106.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11728 | 108.27 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12542 | 120.63 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12601 | 111.76 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12601 | 115 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12601 | 118.01 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12601 | 118.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12601 | 120.96 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12601 | 121.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12601 | 121.68 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12601 | 122.33 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15057 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.07799 | 102.88 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15607 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17154 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17684 | 104.54 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18124 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18487 | 100.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18487 | 100.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18487 | 100.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18487 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18487 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18487 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18487 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18487 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18487 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18487 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18487 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18487 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18487 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18487 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18636 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18636 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1864 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18655 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18655 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18657 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18657 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18683 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18684 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18695 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18718 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18718 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18801 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18856 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18924 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18926 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19035 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19044 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1906 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19065 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19067 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19268 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19306 | 107.18 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19312 | 106.47 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19312 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19644 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20322 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21022 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26899 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26934 | 154.86 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34984 | 187.42 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.35135 | 188.13 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.35255 | 183.57 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.35255 | 183.59 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.35255 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.35255 | 195.61 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.19288 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2468 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2691 | 155.38 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.34949 | 187.81 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.35101 | 188.56 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.35219 | 184.02 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.35219 | 184.11 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.35219 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.35219 | 196.06 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07681 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07681 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07681 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08994 | 119.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09198 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09394 | 109.42 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09394 | 109.42 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09413 | 108.86 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09413 | 108.86 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09415 | 109.24 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09416 | 108.86 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09416 | 109.03 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.77 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.84 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.86 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.02 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.02 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.07 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.07 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.17 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.19 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.19 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.25 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.27 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.27 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.27 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.29 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.31 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.31 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.36 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.36 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.4 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.41 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.51 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.52 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.52 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.53 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.54 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.54 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.54 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.54 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.55 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.55 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.59 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.59 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.6 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.6 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.62 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.66 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.73 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.77 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.85 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.85 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.85 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.85 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.85 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.89 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.89 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.9 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.95 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.95 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 109.95 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 110.17 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 110.17 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 110.17 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 110.25 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 110.25 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 110.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 111.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 111.53 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 111.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 114.16 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09422 | 108.84 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09422 | 108.84 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09422 | 108.84 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09424 | 109.07 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09424 | 109.14 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09425 | 109.14 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09426 | 108.67 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09427 | 109.19 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09427 | 109.27 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09427 | 109.27 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09438 | 109.35 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0944 | 109.33 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09445 | 109.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09446 | 109.5 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09446 | 109.62 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09456 | 109.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09464 | 109.36 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09468 | 109.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09468 | 109.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09521 | 111.45 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09521 | 111.45 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09525 | 111.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09536 | 111 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09536 | 111 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09537 | 111.03 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09537 | 111.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09556 | 111.06 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09559 | 110.42 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09585 | 113.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09614 | 112.76 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09614 | 112.76 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09631 | 112.34 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09669 | 111.7 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09709 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0971 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09804 | 116 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0981 | 116.05 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09826 | 116.33 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09826 | 116.33 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09975 | 116.57 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1021 | 117.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1021 | 117.33 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11095 | 121.98 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11095 | 122.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13458 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14392 | 141.25 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14459 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14459 | 134.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14459 | 137.98 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14459 | 138.46 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14459 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14459 | 142.35 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14459 | 142.4 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14459 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15603 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06694 | 103.3 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06694 | 105.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06694 | 105.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07838 | 104.3 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08544 | 101.1 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08549 | 101.14 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08563 | 101.39 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08563 | 101.39 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08693 | 101.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08898 | 102.12 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08898 | 102.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09669 | 106.31 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09669 | 107.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11728 | 108.62 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12542 | 123.1 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12601 | 113.4 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12601 | 117.19 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12601 | 120.26 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12601 | 120.67 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12601 | 123.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12601 | 124.06 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12601 | 124.1 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12601 | 124.76 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15057 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.07655 | 112.72 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09572 | 119.45 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09597 | 111.33 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.096 | 106.79 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.096 | 109.48 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.096 | 114.6 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.096 | 115.27 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.096 | 119.86 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.096 | 120.54 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.096 | 120.55 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.096 | 121.12 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11514 | 108.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11514 | 108.49 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08443 | 105.19 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08451 | 106.48 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08452 | 106.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08477 | 103.66 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08477 | 106.75 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08484 | 104.31 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08484 | 106.39 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08501 | 103.96 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08505 | 103.86 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08518 | 103.86 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0852 | 104.29 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0852 | 104.3 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08522 | 104.25 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08522 | 104.25 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08525 | 103.62 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0853 | 103.95 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08534 | 104.21 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08538 | 103.7 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 103.19 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 103.19 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 103.22 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 103.36 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 103.65 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 103.87 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 103.87 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 103.87 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 103.87 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 103.87 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 103.94 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 103.95 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 104.01 | P13:NBEC#1 GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 104.1 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 104.18 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 104.28 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 104.31 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 104.65 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 104.66 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 104.71 | 531504 CIMWD2 7 345 3WXFMR CIMRNWND2 MPT 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 104.71 | GEN-2010-009_POI_531501_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 104.74 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 104.75 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 104.75 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 104.75 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 104.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 104.87 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 104.87 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 105.04 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 105.14 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 105.15 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 105.37 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 105.37 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 105.49 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 105.49 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 105.51 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 105.53 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 105.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 105.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 105.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 105.74 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 105.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 105.91 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 111.31 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08543 | 103.2 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08543 | 103.33 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08543 | 105.63 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08544 | 103.48 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08546 | 103.41 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08546 | 103.46 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08546 | 103.48 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08547 | 103.3 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08547 | 103.92 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08547 | 103.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08547 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08548 | 103.26 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08548 | 103.62 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08549 | 104.56 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0855 | 103.43 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08553 | 103.51 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08553 | 103.92 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08553 | 104.02 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08555 | 103.93 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08555 | 104.19 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 104.29 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08558 | 104.28 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08559 | 103.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0856 | 104.21 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0856 | 104.21 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08561 | 103.53 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08562 | 103.72 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08562 | 103.77 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08563 | 104.04 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08568 | 103.96 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08569 | 105.27 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08571 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08571 | 104.43 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08571 | 105.48 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 103.64 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08598 | 104.27 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08602 | 104.71 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08602 | 104.71 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08605 | 104.64 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08606 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08607 | 104.3 | P12:345:WERE:VIOL-WICH-345:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08641 | 104.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08651 | 104.7 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08651 | 104.71 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08665 | 104.54 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08667 | 111.68 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08674 | 104.05 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08679 | 106 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08715 | 104.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08715 | 104.73 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08727 | 104.85 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08727 | 104.85 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08732 | 104.84 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08735 | 106.71 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08744 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08744 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08744 | 105.45 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0879 | 106.65 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0879 | 106.7 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08802 | 106.03 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0881 | 105.86 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08907 | 109.43 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08945 | 107.32 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08945 | 107.46 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08945 | 107.57 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08945 | 109.51 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09069 | 108.97 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09234 | 104.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09234 | 105.34 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09365 | 109.15 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09372 | 111.96 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09553 | 120.22 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09553 | 120.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09553 | 120.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09553 | 120.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09553 | 120.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10296 | 124.48 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10296 | 124.48 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10296 | 124.48 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11052 | 126.32 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11052 | 126.32 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11052 | 126.32 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11254 | 135.92 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11254 | 135.92 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09814 | 106.45 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09814 | 106.46 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09814 | 106.46 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09814 | 106.46 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09814 | 106.46 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10556 | 110.51 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10556 | 110.51 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10556 | 110.51 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11313 | 112.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11313 | 112.81 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11313 | 112.81 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11514 | 122.53 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11514 | 122.53 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06811 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06811 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.06125 | 111.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.05221 | 106.67 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.07637 | 115.99 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0536 | 162.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0536 | 164.73 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0536 | 164.73 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0536 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05399 | 165.04 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05399 | 165.04 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05461 | 164.89 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05468 | 165.64 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05891 | 139.19 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05898 | 138.87 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05965 | 135.64 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05965 | 135.64 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05968 | 135.15 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05972 | 135.16 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05975 | 135.07 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05976 | 135.48 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.02 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.07 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.14 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.15 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.15 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.17 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.44 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.47 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.47 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.49 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.52 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.52 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.52 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.52 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.55 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.55 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.57 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.59 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.62 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.62 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.7 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.7 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.7 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.7 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.72 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.72 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.72 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.73 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.73 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.73 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.75 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.75 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.76 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.77 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.78 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.83 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.95 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.95 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.95 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.95 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.95 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.98 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.98 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 136 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 136.02 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 136.02 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 136.02 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 136.24 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 136.24 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 136.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 136.47 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 136.47 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 136.47 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 137.36 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 139.3 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0598 | 135.15 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0598 | 135.15 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0598 | 135.15 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0598 | 135.16 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0598 | 135.39 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05981 | 135.44 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05981 | 135.45 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05982 | 135.02 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05982 | 135.49 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05982 | 135.56 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05982 | 135.56 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05988 | 135.63 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05988 | 135.65 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05988 | 135.73 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05989 | 135.61 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05992 | 135.62 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05997 | 136 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06001 | 135.63 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 135.96 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 135.96 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0603 | 137.34 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0603 | 137.43 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0603 | 137.43 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06034 | 137.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06035 | 137.04 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06035 | 137.04 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06038 | 137.06 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06038 | 137.16 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06044 | 137.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06044 | 137.41 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06044 | 137.41 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06048 | 136.61 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06065 | 139.39 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06094 | 138.33 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06114 | 137.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06123 | 137.58 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06123 | 137.59 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06172 | 141.34 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06175 | 141.38 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 141.62 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 141.62 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06234 | 141.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06373 | 142.78 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06373 | 142.94 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06831 | 147.71 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06831 | 148.81 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07674 | 149.61 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09185 | 163.49 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09229 | 152.28 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09229 | 159.07 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09229 | 161.78 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09229 | 163.27 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10202 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10202 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10521 | 118.97 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10637 | 109.05 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10637 | 109.05 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10656 | 108.48 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10656 | 108.48 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10658 | 108.48 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10658 | 108.65 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10658 | 108.87 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.39 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.46 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.48 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.64 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.64 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.67 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.67 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.79 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.82 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.82 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.87 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.89 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.9 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.9 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.92 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.94 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.94 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.99 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.99 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.03 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.04 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.14 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.15 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.15 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.16 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.17 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.17 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.17 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.18 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.18 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.18 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.22 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.22 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.23 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.24 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.26 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.3 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.37 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.4 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.49 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.49 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.49 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.49 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.49 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.53 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.53 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.53 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.58 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.58 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.59 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.69 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.69 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.69 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.75 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.75 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.78 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 110.66 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 110.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 111.04 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 111.24 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 113.28 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10665 | 108.45 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10665 | 108.45 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10665 | 108.45 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10666 | 108.69 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10667 | 108.76 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10668 | 108.77 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10669 | 108.28 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10669 | 108.82 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10669 | 108.9 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10669 | 108.9 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1068 | 108.98 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10681 | 108.95 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10687 | 108.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10687 | 109.13 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10687 | 109.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10697 | 109.44 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10705 | 108.99 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10708 | 109.39 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10708 | 109.39 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1076 | 111.09 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10761 | 111.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10761 | 111.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10771 | 110.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10771 | 110.68 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10776 | 110.71 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10776 | 110.82 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10786 | 110.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10788 | 110.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1083 | 113.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10859 | 112.35 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10859 | 112.35 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10868 | 112.1 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10905 | 111.42 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10908 | 111.03 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10909 | 111.04 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11028 | 115.8 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11035 | 115.86 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11051 | 116.15 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11051 | 116.15 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11156 | 116.25 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11214 | 117.38 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11367 | 117.14 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11367 | 117.29 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12086 | 121.61 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12086 | 122.52 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1405 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16743 | 138.42 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16822 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16822 | 131.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16822 | 135.41 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16822 | 135.88 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16822 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16822 | 139.6 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16822 | 139.63 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16822 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17663 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08891 | 104.17 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08891 | 104.17 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09168 | 103.69 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09611 | 100.92 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09617 | 100.97 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0963 | 101.22 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0963 | 101.22 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09722 | 101.31 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09773 | 102.3 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09906 | 102.08 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09906 | 102.22 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10533 | 105.99 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10533 | 106.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12244 | 108.27 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14591 | 120.63 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14659 | 111.76 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14659 | 115 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14659 | 118.01 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14659 | 118.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14659 | 120.96 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14659 | 121.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14659 | 121.68 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14659 | 122.33 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17044 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11076 | 102.88 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21414 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21646 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21677 | 104.54 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 100.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 100.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 100.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21907 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21908 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21908 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21922 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21922 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2193 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2193 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21946 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2195 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21964 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21999 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21999 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22065 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2207 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22123 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22136 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22137 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22287 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22296 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22312 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22317 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22318 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2246 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22547 | 107.18 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22553 | 106.47 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22553 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22797 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23632 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2392 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28822 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31335 | 154.86 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41059 | 188.13 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4115 | 187.42 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41505 | 183.57 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41505 | 183.59 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41505 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41505 | 195.61 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21946 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.26444 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31307 | 155.38 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41019 | 188.56 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41109 | 187.81 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41463 | 184.02 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41463 | 184.11 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41463 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41463 | 196.06 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10042 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10202 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10202 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10202 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10521 | 119.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10637 | 109.42 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10637 | 109.42 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10656 | 108.86 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10656 | 108.86 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10658 | 108.86 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10658 | 109.03 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10658 | 109.24 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.77 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.84 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.86 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.02 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.02 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.07 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.07 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.17 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.19 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.19 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.25 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.27 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.27 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.27 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.29 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.31 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.31 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.36 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.36 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.4 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.41 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.51 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.52 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.52 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.53 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.54 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.54 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.54 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.54 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.55 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.55 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.59 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.59 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.6 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.6 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.62 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.66 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.73 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.77 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.85 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.85 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.85 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.85 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.85 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.89 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.89 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.9 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.95 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.95 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 109.95 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 110.17 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 110.17 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 110.17 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 110.25 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 110.25 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 110.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 111.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 111.53 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 111.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 114.16 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10665 | 108.84 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10665 | 108.84 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10665 | 108.84 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10666 | 109.07 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10667 | 109.14 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10668 | 109.14 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10669 | 108.67 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10669 | 109.19 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10669 | 109.27 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10669 | 109.27 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1068 | 109.35 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10681 | 109.33 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10687 | 109.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10687 | 109.5 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10687 | 109.62 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10697 | 109.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10705 | 109.36 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10708 | 109.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10708 | 109.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1076 | 111.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10761 | 111.45 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10761 | 111.45 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10771 | 111 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10771 | 111 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10776 | 111.03 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10776 | 111.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10786 | 110.42 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10788 | 111.06 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1083 | 113.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10859 | 112.76 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10859 | 112.76 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10868 | 112.34 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10905 | 111.7 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10908 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10909 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11028 | 116 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11035 | 116.05 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11051 | 116.33 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11051 | 116.33 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11156 | 116.57 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11367 | 117.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11367 | 117.33 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12086 | 121.98 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12086 | 122.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1405 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16743 | 141.25 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16822 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16822 | 134.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16822 | 137.98 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16822 | 138.46 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16822 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16822 | 142.35 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16822 | 142.4 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16822 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17663 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08891 | 103.3 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08891 | 105.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08891 | 105.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09168 | 104.3 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09611 | 101.1 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09617 | 101.14 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0963 | 101.39 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0963 | 101.39 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09722 | 101.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09906 | 102.12 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09906 | 102.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10533 | 106.31 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10533 | 107.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12244 | 108.62 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14591 | 123.1 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14659 | 113.4 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14659 | 117.19 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14659 | 120.26 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14659 | 120.67 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14659 | 123.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14659 | 124.06 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14659 | 124.1 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14659 | 124.76 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17044 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10112 | 112.72 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11659 | 111.33 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.12857 | 119.45 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.12889 | 106.79 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.12889 | 109.48 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.12889 | 114.6 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.12889 | 115.27 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.12889 | 119.86 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.12889 | 120.54 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.12889 | 120.55 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.12889 | 121.12 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.0565 | 139.38 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.0565 | 139.57 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.0565 | 139.79 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.0565 | 139.79 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.0565 | 141.57 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0565 | 133.85 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0565 | 134.04 | POI 515800_22 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0565 | 134.04 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0565 | 134.12 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0565 | 134.12 | Potential P4 Event - POI 560078_2 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.0565 | 137.92 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.0565 | 138.2 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.0565 | 138.5 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.0565 | 138.5 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.0565 | 140.52 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 1 | 159 | 159 | 0.05213 | 119.64 | P12:115:SPS:T08_2_SPRMN_PRNGLE:::: | Cumulative Impact | Rebuild the existing SPEARMAN3 to PRINGLE3 115 kV CKT1 line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 1 | 159 | 159 | 0.05644 | 104.88 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing SPEARMAN3 to PRINGLE3 115 kV CKT1 line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | 353 | 353 | 0.17267 | 108.18 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing STLN-DEMARCO6 to G23-101-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.13252 | 108.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.13252 | 108.49 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10058 | 105.19 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10065 | 106.48 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10066 | 106.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10087 | 103.66 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10092 | 106.75 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10099 | 104.31 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10099 | 106.39 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10116 | 103.96 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1012 | 103.86 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10133 | 103.86 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10135 | 104.29 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10135 | 104.3 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10137 | 104.25 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10137 | 104.25 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1014 | 103.62 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10144 | 103.95 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10148 | 104.21 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10153 | 103.7 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 103.19 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 103.19 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 103.2 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 103.22 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 103.36 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 103.65 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 103.87 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 103.87 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 103.87 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 103.87 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 103.87 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 103.94 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 103.95 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 104.01 | P13:NBEC#1 GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 104.1 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 104.18 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 104.28 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 104.31 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 104.65 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 104.66 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 104.71 | 531504 CIMWD2 7 345 3WXFMR CIMRNWND2 MPT 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 104.71 | GEN-2010-009_POI_531501_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 104.74 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 104.75 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 104.75 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 104.75 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 104.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 104.87 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 104.87 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 105.04 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 105.14 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 105.15 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 105.37 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 105.37 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 105.49 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 105.49 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 105.51 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 105.53 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 105.63 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 105.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 105.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 105.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 105.74 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 105.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 105.91 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 111.31 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10158 | 103.33 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10159 | 103.48 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1016 | 103.46 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1016 | 103.48 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10161 | 103.3 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10161 | 103.41 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10161 | 103.62 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10161 | 103.92 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10161 | 103.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10161 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10162 | 103.26 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10163 | 104.56 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10164 | 103.43 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10167 | 103.51 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10167 | 103.92 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10167 | 104.02 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10168 | 104.19 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10169 | 103.93 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10169 | 104.29 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10171 | 104.28 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10173 | 103.53 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10174 | 103.72 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10174 | 103.77 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10174 | 103.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10174 | 104.21 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10174 | 104.21 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10178 | 103.96 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10178 | 104.04 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1018 | 105.27 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10182 | 105.48 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10183 | 104.43 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10184 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 104.27 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10207 | 103.64 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10208 | 104.71 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10208 | 104.71 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1021 | 104.3 | P12:345:WERE:VIOL-WICH-345:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10211 | 104.64 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10248 | 104.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10252 | 104.05 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10262 | 104.54 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10274 | 106 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10298 | 111.68 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10303 | 104.7 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10303 | 104.71 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10306 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10306 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10306 | 105.45 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1032 | 104.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1032 | 104.73 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10323 | 104.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10323 | 105.34 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10323 | 106.71 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10324 | 104.84 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10326 | 104.85 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10326 | 104.85 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10403 | 106.03 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10411 | 105.86 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10489 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10551 | 106.65 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10551 | 106.7 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10586 | 109.43 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10631 | 107.32 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10631 | 107.46 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10631 | 107.57 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10631 | 109.51 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10797 | 108.97 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10961 | 109.15 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11029 | 111.96 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11346 | 120.22 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11346 | 120.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11346 | 120.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11346 | 120.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11346 | 120.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12808 | 126.32 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12808 | 126.32 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12808 | 126.32 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12946 | 124.48 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12946 | 124.48 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12946 | 124.48 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12991 | 135.92 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12991 | 135.92 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11607 | 106.45 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11607 | 106.46 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11607 | 106.46 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11607 | 106.46 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11607 | 106.46 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.13069 | 112.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.13069 | 112.81 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.13069 | 112.81 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.13207 | 110.51 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.13207 | 110.51 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.13207 | 110.51 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.13252 | 122.53 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.13252 | 122.53 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40427 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40667 | 139.38 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40708 | 139.3 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40789 | 137.63 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40802 | 133.93 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40867 | 136.02 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4093 | 138.87 | Potential P4 Event - POI 773600_4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40932 | 138.88 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40932 | 138.88 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40935 | 132.94 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40935 | 133 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40936 | 133.01 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40938 | 132.62 | 514796 IODINE-4 138 515376 WWRDEHV4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40938 | 132.62 | 514796 IODINE-4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40938 | 132.82 | 532792 FR2EAST7 345 588364 G16-153-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40938 | 132.87 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40939 | 132.92 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4094 | 132.81 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4094 | 132.83 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4094 | 132.85 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40941 | 132.88 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40941 | 132.88 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40942 | 133.45 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.45 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.59 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.61 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.81 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.81 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.84 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.84 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.84 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.86 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.9 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.9 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.93 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.94 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.95 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.96 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.96 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.96 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.96 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.98 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.99 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.99 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.99 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.99 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133 | P12:EHV:EES::8ISES%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.01 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.01 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.04 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.04 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.05 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.05 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.05 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.06 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.06 | P11:HV:EES::1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.06 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.06 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.06 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.07 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.09 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.09 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.09 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.09 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.09 | P23:345:MEC:CBEC 908 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.1 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.11 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.11 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.11 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.11 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.15 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.18 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.19 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.19 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.21 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.28 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.3 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.47 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.76 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.88 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.24 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.42 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.43 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.91 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.91 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 138.67 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 138.67 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40944 | 132.91 | P12:069:GLHP:COLE-TURPIN-BEARD-ADAMS-JEFFERSON:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40944 | 133.04 | P23:500:EES-EAI:INDEP2:B6126 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40953 | 133.26 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40958 | 133.29 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40967 | 133.51 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40968 | 133.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40978 | 133.56 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40979 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40981 | 133.57 | P42:345:OKGE:SB_SEOL7385:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40986 | 133.2 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40987 | 133.33 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41005 | 133.61 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41005 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41005 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41074 | 135.99 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.411 | 136.22 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.411 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.411 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41216 | 134.9 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41216 | 134.91 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41216 | 135.3 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41216 | 135.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41256 | 137.34 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41339 | 138.51 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41378 | 163.83 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41414 | 163.21 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41414 | 163.21 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41422 | 161.82 | Potential P4 Event - POI 527656_9 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41428 | 138.61 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41437 | 161.31 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41437 | 161.31 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41437 | 164.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41437 | 164.87 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41559 | 140.79 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41906 | 137.06 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.46082 | 163.65 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4623 | 157.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4623 | 157.17 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4623 | 157.17 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40427 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40667 | 141.48 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40708 | 142.25 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40789 | 138.3 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40802 | 135.66 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40867 | 137.76 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40907 | 134.6 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4093 | 142.83 | Potential P4 Event - POI 773600_1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40932 | 142.91 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40932 | 142.91 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40935 | 134.9 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40935 | 134.92 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40936 | 134.93 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40937 | 134.94 | P11:345:WERE:JECU3-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40938 | 134.63 | 514787 DEWEY 4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40938 | 134.83 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40939 | 134.63 | 514789 MENOTAP4 138 514790 IMO 4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40939 | 134.82 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4094 | 134.83 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40941 | 134.83 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40941 | 134.83 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40942 | 135.25 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.3 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.64 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.82 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.82 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.83 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.83 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.86 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.87 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.89 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.92 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.92 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.92 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.93 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.93 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.93 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.94 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.94 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.95 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.96 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.96 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.96 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.97 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.97 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.97 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.98 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.98 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.99 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.99 | P23:345:MEC:LOUISA 954 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.01 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.02 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.02 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.02 | P23:500:EES-EAI:WH_BLF:B7942 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.03 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.04 | P11:26:EES-EAI:INDEP2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.04 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.04 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.04 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.05 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.05 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.05 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.06 | ASGI-2021-001_POI_766031_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.06 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.06 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.06 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.07 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.1 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.11 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.11 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.14 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.14 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.14 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.21 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.23 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.27 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.34 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 137.63 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 137.79 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 137.99 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 138.62 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 138.62 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 139.4 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 139.4 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 142.7 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 142.7 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40944 | 134.97 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40967 | 135.31 | P42:345:OKGE:SB_BVTY7387:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40967 | 135.72 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40968 | 135.59 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40978 | 135.28 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40979 | 135.05 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40986 | 134.98 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40987 | 135.19 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41005 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41005 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41005 | 135.54 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41074 | 138.08 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.411 | 137.62 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.411 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.411 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41216 | 136.85 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41216 | 136.86 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41216 | 137.23 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41216 | 137.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41256 | 139.06 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41339 | 140.57 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41378 | 167.97 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41414 | 167.9 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41414 | 167.9 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4142 | 166.55 | Potential P4 Event - POI 527656_10 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41428 | 140.18 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41437 | 165.89 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41437 | 165.89 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41437 | 169.93 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41437 | 169.93 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41559 | 142.88 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41906 | 139.08 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.46082 | 165.72 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4623 | 159.05 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4623 | 159.06 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4623 | 159.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05117 | 152.28 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05117 | 159.07 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05117 | 161.78 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05117 | 163.27 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05169 | 147.71 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05169 | 148.81 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10478 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10671 | 109.05 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10671 | 109.05 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1069 | 108.48 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1069 | 108.48 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10692 | 108.65 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10692 | 108.87 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.39 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.46 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.48 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.48 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.64 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.64 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.67 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.67 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.79 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.82 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.82 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.87 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.89 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.9 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.9 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.92 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.94 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.94 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.99 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.99 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.03 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.04 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.14 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.15 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.15 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.16 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.17 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.17 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.17 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.18 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.18 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.18 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.22 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.22 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.23 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.24 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.26 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.3 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.37 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.4 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.49 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.49 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.49 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.49 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.49 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.53 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.53 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.53 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.58 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.58 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.59 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.69 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.69 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.69 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.75 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.75 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.78 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 110.66 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 110.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 111.04 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 111.24 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 113.28 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10699 | 108.45 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10699 | 108.45 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10699 | 108.45 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10701 | 108.69 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10702 | 108.76 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10703 | 108.28 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10703 | 108.77 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10705 | 108.82 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10705 | 108.9 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10705 | 108.9 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10717 | 108.98 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10719 | 108.95 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10722 | 108.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10734 | 109.44 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10744 | 108.99 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10749 | 109.39 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10749 | 109.39 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10781 | 109.13 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10781 | 109.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10807 | 111.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10807 | 111.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10823 | 110.71 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10823 | 110.82 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10826 | 111.09 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10837 | 110.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10837 | 110.68 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10848 | 110.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10866 | 110.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10912 | 112.1 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10953 | 111.42 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10956 | 111.03 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10957 | 111.04 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11013 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11013 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11135 | 115.8 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1114 | 115.86 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11157 | 116.15 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11157 | 116.15 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11349 | 117.38 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11484 | 116.25 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11553 | 117.14 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11553 | 117.29 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1171 | 113.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11739 | 112.35 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11739 | 112.35 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12087 | 121.61 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12087 | 122.52 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12118 | 138.42 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12175 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12175 | 131.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12175 | 135.41 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12175 | 135.88 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12175 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12175 | 139.6 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12175 | 139.63 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12175 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1503 | 118.97 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17719 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09131 | 108.27 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09598 | 104.17 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09598 | 104.17 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09704 | 100.92 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09708 | 100.97 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09723 | 101.22 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09723 | 101.22 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0989 | 102.3 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10008 | 101.31 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10068 | 102.08 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10068 | 102.22 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10534 | 105.99 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10534 | 106.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10561 | 120.63 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1061 | 111.76 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1061 | 115 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1061 | 118.01 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1061 | 118.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1061 | 120.96 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1061 | 121.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1061 | 121.68 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1061 | 122.33 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13098 | 103.69 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17099 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12719 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12763 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13004 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13168 | 100.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13168 | 100.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13168 | 100.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13168 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13168 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13168 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13168 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13168 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13168 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13168 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13168 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13168 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13168 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13168 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13329 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13329 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13351 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13351 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13355 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1337 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1337 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13389 | 104.54 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13393 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13411 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13414 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13487 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13546 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1356 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13561 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13793 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.138 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13816 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13821 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13823 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14093 | 107.18 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.141 | 106.47 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.141 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14273 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14355 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14389 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14389 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14421 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15274 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16892 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22679 | 154.86 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2497 | 187.42 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25111 | 183.57 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25111 | 183.59 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25111 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25111 | 195.61 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25435 | 188.13 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.1167 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.14013 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22659 | 155.38 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24944 | 187.81 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25085 | 184.02 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25085 | 184.11 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25085 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25085 | 196.06 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25411 | 188.56 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10478 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10671 | 109.42 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10671 | 109.42 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1069 | 108.86 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1069 | 108.86 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10692 | 109.03 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10692 | 109.24 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.77 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.84 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.86 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.86 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.02 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.02 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.07 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.07 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.17 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.19 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.19 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.25 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.27 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.27 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.27 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.29 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.31 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.31 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.36 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.36 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.4 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.41 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.51 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.52 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.52 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.53 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.54 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.54 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.54 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.54 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.55 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.55 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.59 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.59 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.6 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.6 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.62 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.66 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.73 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.77 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.85 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.85 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.85 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.85 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.85 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.89 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.89 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.9 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.95 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.95 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 109.95 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 110.17 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 110.17 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 110.17 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 110.25 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 110.25 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 110.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 111.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 111.53 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 111.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 114.16 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10699 | 108.84 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10699 | 108.84 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10699 | 108.84 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10701 | 109.07 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10702 | 109.14 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10703 | 108.67 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10703 | 109.14 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10705 | 109.19 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10705 | 109.27 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10705 | 109.27 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10717 | 109.35 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10719 | 109.33 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10722 | 109.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10734 | 109.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10744 | 109.36 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10749 | 109.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10749 | 109.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10781 | 109.5 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10781 | 109.62 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10807 | 111.45 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10807 | 111.45 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10821 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10823 | 111.03 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10823 | 111.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10826 | 111.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10837 | 111 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10837 | 111 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10848 | 110.42 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10866 | 111.06 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10912 | 112.34 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10953 | 111.7 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10956 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10957 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11013 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11013 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11013 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11135 | 116 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1114 | 116.05 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11157 | 116.33 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11157 | 116.33 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11484 | 116.57 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11553 | 117.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11553 | 117.33 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1171 | 113.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11739 | 112.76 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11739 | 112.76 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12087 | 121.98 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12087 | 122.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12118 | 141.25 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12175 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12175 | 134.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12175 | 137.98 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12175 | 138.46 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12175 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12175 | 142.35 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12175 | 142.4 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12175 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1503 | 119.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17719 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09131 | 108.62 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09598 | 103.3 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09598 | 105.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09598 | 105.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09704 | 101.1 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09708 | 101.14 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09723 | 101.39 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09723 | 101.39 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10008 | 101.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10068 | 102.12 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10068 | 102.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10534 | 106.31 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10534 | 107.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10561 | 123.1 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1061 | 113.4 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1061 | 117.19 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1061 | 120.26 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1061 | 120.67 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1061 | 123.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1061 | 124.06 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1061 | 124.1 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1061 | 124.76 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13098 | 104.3 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17099 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05539 | 139.38 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05539 | 139.57 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05539 | 139.79 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05539 | 139.79 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05567 | 141.57 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05539 | 133.85 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05539 | 134.04 | POI 515800_22 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05539 | 134.04 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05539 | 134.12 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05539 | 134.12 | Potential P4 Event - POI 560078_2 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05539 | 137.92 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05539 | 138.2 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05539 | 138.5 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05539 | 138.5 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05567 | 140.52 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 1 | 159 | 159 | 0.05363 | 104.88 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing SPEARMAN3 to PRINGLE3 115 kV CKT1 line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | 353 | 353 | 0.16401 | 108.18 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing STLN-DEMARCO6 to G23-101-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.13077 | 108.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.13077 | 108.49 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09898 | 105.19 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09905 | 106.48 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09906 | 106.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09927 | 103.66 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09932 | 106.75 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09938 | 106.39 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09939 | 104.31 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09955 | 103.96 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0996 | 103.86 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09973 | 103.86 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09975 | 104.29 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09975 | 104.3 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09977 | 104.25 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09977 | 104.25 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0998 | 103.62 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09984 | 103.95 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09988 | 104.21 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09993 | 103.7 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 103.19 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 103.19 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 103.2 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 103.22 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 103.36 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 103.65 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 103.87 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 103.87 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 103.87 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 103.87 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 103.87 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 103.94 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 103.95 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 104.01 | P13:NBEC#1 GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 104.1 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 104.18 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 104.28 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 104.31 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 104.65 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 104.66 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 104.71 | 531504 CIMWD2 7 345 3WXFMR CIMRNWND2 MPT 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 104.71 | GEN-2010-009_POI_531501_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 104.74 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 104.75 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 104.75 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 104.75 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 104.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 104.87 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 104.87 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 105.04 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 105.14 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 105.15 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 105.37 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 105.37 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 105.49 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 105.49 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 105.51 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 105.53 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 105.63 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 105.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 105.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 105.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 105.74 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 105.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 105.91 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 111.31 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09998 | 103.33 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09999 | 103.48 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1 | 103.46 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1 | 103.48 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10001 | 103.3 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10001 | 103.41 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10001 | 103.62 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10001 | 103.92 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10001 | 103.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10001 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10002 | 103.26 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10003 | 104.56 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10004 | 103.43 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10007 | 103.51 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10007 | 103.92 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10007 | 104.02 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10008 | 104.19 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10009 | 103.93 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10009 | 104.29 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10011 | 104.28 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10013 | 103.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10014 | 103.53 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10014 | 103.72 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10014 | 103.77 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10014 | 104.21 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10014 | 104.21 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10018 | 103.96 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10018 | 104.04 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1002 | 105.27 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10022 | 105.48 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10023 | 104.43 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10024 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10045 | 104.27 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10047 | 103.64 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10049 | 104.71 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10049 | 104.71 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10051 | 104.3 | P12:345:WERE:VIOL-WICH-345:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10052 | 104.64 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10088 | 104.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10094 | 104.05 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10104 | 104.54 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10116 | 106 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10136 | 111.68 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1014 | 104.7 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1014 | 104.71 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10152 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10152 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10152 | 105.45 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10161 | 104.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10161 | 104.73 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10162 | 104.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10162 | 105.34 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10165 | 106.71 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10166 | 104.84 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10167 | 104.85 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10167 | 104.85 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10244 | 106.03 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10252 | 105.86 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10312 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10377 | 106.65 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10377 | 106.7 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1042 | 109.43 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10463 | 107.32 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10463 | 107.46 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10463 | 107.57 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10463 | 109.51 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10623 | 108.97 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10788 | 109.15 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10864 | 111.96 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11168 | 120.22 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11168 | 120.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11168 | 120.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11168 | 120.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11168 | 120.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12631 | 126.32 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12631 | 126.32 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12631 | 126.32 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12686 | 124.48 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12686 | 124.48 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12686 | 124.48 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12817 | 135.92 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12817 | 135.92 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11429 | 106.45 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11429 | 106.46 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11429 | 106.46 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11429 | 106.46 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11429 | 106.46 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12892 | 112.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12892 | 112.81 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12892 | 112.81 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12947 | 110.51 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12947 | 110.51 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12947 | 110.51 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.13077 | 122.53 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.13077 | 122.53 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.38875 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3888 | 139.38 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.38886 | 139.3 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.38981 | 137.63 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.38982 | 133.93 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39042 | 136.02 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39085 | 138.87 | Potential P4 Event - POI 773600_4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39087 | 138.88 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39087 | 138.88 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39089 | 132.94 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39089 | 133 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3909 | 133.01 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39092 | 132.62 | 514796 IODINE-4 138 515376 WWRDEHV4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39092 | 132.62 | 514796 IODINE-4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39092 | 132.82 | 532792 FR2EAST7 345 588364 G16-153-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39092 | 132.87 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39093 | 132.92 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39094 | 132.81 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39094 | 132.83 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39094 | 132.85 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39094 | 132.88 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39094 | 132.88 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39095 | 133.45 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39096 | 132.84 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.45 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.59 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.61 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.81 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.81 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.84 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.84 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.86 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.9 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.9 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.91 | P12:069:GLHP:COLE-TURPIN-BEARD-ADAMS-JEFFERSON:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.93 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.94 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.95 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.96 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.96 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.96 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.96 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.98 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.99 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.99 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.99 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.99 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133 | P12:EHV:EES::8ISES%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.01 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.01 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.04 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.04 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.04 | P23:500:EES-EAI:INDEP2:B6126 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.05 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.05 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.05 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.06 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.06 | P11:HV:EES::1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.06 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.06 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.06 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.07 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.09 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.09 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.09 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.09 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.09 | P23:345:MEC:CBEC 908 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.1 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.11 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.11 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.11 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.11 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.15 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.18 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.19 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.19 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.21 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.28 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.3 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.47 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.76 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.88 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.24 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.42 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.43 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.91 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.91 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 138.67 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 138.67 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39107 | 133.26 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39111 | 133.29 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3912 | 133.51 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39121 | 133.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39133 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39134 | 133.56 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39138 | 133.57 | P42:345:OKGE:SB_SEOL7385:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39139 | 133.33 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3914 | 133.2 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39157 | 133.61 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39161 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39161 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39242 | 135.99 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3926 | 136.22 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3926 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3926 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39345 | 134.9 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39345 | 134.91 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39345 | 135.3 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39345 | 135.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39399 | 137.34 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39555 | 138.51 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39626 | 138.61 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39769 | 140.79 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39772 | 163.83 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39799 | 163.21 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39799 | 163.21 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39801 | 161.82 | Potential P4 Event - POI 527656_9 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39816 | 161.31 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39816 | 161.31 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39816 | 164.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39816 | 164.87 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40009 | 137.06 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.43954 | 163.65 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.44102 | 157.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.44102 | 157.17 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.44102 | 157.17 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.38875 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3888 | 141.48 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.38886 | 142.25 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.38981 | 138.3 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.38982 | 135.66 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39042 | 137.76 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39061 | 134.6 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39085 | 142.83 | Potential P4 Event - POI 773600_1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39087 | 142.91 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39087 | 142.91 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39089 | 134.9 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39089 | 134.92 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3909 | 134.93 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39091 | 134.94 | P11:345:WERE:JECU3-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39092 | 134.63 | 514787 DEWEY 4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39092 | 134.63 | 514789 MENOTAP4 138 514790 IMO 4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39092 | 134.83 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39093 | 134.82 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39094 | 134.83 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39094 | 134.83 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39094 | 134.83 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39095 | 135.25 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39096 | 134.82 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.3 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.64 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.82 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.83 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.83 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.86 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.87 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.89 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.92 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.92 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.92 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.93 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.93 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.93 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.94 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.94 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.95 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.96 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.96 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.96 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.97 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.97 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.97 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.97 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.98 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.98 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.99 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.99 | P23:345:MEC:LOUISA 954 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.01 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.02 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.02 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.02 | P23:500:EES-EAI:WH_BLF:B7942 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.03 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.04 | P11:26:EES-EAI:INDEP2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.04 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.04 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.04 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.05 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.05 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.05 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.06 | ASGI-2021-001_POI_766031_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.06 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.06 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.06 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.07 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.1 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.11 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.11 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.14 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.14 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.14 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.21 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.23 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.27 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.34 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 137.63 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 137.79 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 137.99 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 138.62 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 138.62 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 139.4 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 139.4 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 142.7 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 142.7 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3912 | 135.31 | P42:345:OKGE:SB_BVTY7387:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3912 | 135.72 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39121 | 135.59 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39133 | 135.05 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39134 | 135.28 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39139 | 135.19 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3914 | 134.98 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39157 | 135.54 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39161 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39161 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39242 | 138.08 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3926 | 137.62 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3926 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3926 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39345 | 136.85 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39345 | 136.86 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39345 | 137.23 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39345 | 137.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39399 | 139.06 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39555 | 140.57 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39626 | 140.18 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39769 | 142.88 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39772 | 167.97 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39799 | 167.9 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39799 | 167.9 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39807 | 166.55 | Potential P4 Event - POI 527656_10 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39816 | 165.89 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39816 | 165.89 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39816 | 169.93 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39816 | 169.93 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40009 | 139.08 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.43954 | 165.72 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.44102 | 159.05 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.44102 | 159.06 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.44102 | 159.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05028 | 165.64 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05034 | 164.89 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05034 | 165.04 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05034 | 165.04 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05037 | 162.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05037 | 164.73 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05037 | 164.73 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05037 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05186 | 152.28 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05186 | 159.07 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05186 | 161.78 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05186 | 163.27 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0523 | 147.71 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0523 | 148.81 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11583 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11653 | 109.05 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11653 | 109.05 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11673 | 108.48 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11673 | 108.48 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11675 | 108.48 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11675 | 108.65 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11675 | 108.87 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.39 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.46 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.48 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.64 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.64 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.67 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.67 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.79 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.82 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.82 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.87 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.89 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.9 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.9 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.92 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.94 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.94 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.99 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.99 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.03 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.04 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.14 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.15 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.15 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.16 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.17 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.17 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.17 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.18 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.18 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.18 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.22 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.22 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.23 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.24 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.26 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.3 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.37 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.4 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.49 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.49 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.49 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.49 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.49 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.53 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.53 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.53 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.58 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.58 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.59 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.69 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.69 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.69 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.75 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.75 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.78 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 110.66 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 110.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 111.04 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 111.24 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 113.28 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11681 | 108.45 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11681 | 108.45 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11681 | 108.45 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11683 | 108.69 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11684 | 108.76 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11685 | 108.28 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11685 | 108.77 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11687 | 108.82 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11687 | 108.9 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11687 | 108.9 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11698 | 108.98 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11701 | 108.95 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11704 | 108.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11716 | 109.44 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11726 | 108.99 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1173 | 109.39 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1173 | 109.39 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11755 | 109.13 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11755 | 109.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11788 | 111.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11788 | 111.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11804 | 110.71 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11804 | 110.82 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11805 | 111.09 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11816 | 110.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11816 | 110.68 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11827 | 110.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11845 | 110.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11893 | 112.1 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11933 | 111.03 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11933 | 111.42 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11934 | 111.04 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1211 | 115.8 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12115 | 115.86 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12132 | 116.15 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12132 | 116.15 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12141 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12141 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12321 | 117.38 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12438 | 116.25 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12517 | 117.14 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12517 | 117.29 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12636 | 113.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12665 | 112.35 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12665 | 112.35 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13048 | 121.61 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13048 | 122.52 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13089 | 138.42 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1315 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1315 | 131.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1315 | 135.41 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1315 | 135.88 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1315 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1315 | 139.6 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1315 | 139.63 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1315 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15816 | 118.97 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19347 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10094 | 108.27 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10554 | 100.92 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10558 | 100.97 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10573 | 101.22 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10573 | 101.22 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10581 | 104.17 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10581 | 104.17 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10738 | 102.3 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10839 | 101.31 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10908 | 102.08 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10908 | 102.22 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11371 | 105.99 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11371 | 106.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11406 | 120.63 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11459 | 111.76 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11459 | 115 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11459 | 118.01 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11459 | 118.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11459 | 120.96 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11459 | 121.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11459 | 121.68 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11459 | 122.33 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13783 | 103.69 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18669 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13751 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1392 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1399 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14113 | 100.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14113 | 100.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14113 | 100.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14113 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14113 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14113 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14113 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14113 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14113 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14113 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14113 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14113 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14113 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14113 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14272 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14272 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14294 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14294 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14295 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1431 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1431 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14333 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14352 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14431 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14453 | 104.54 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14471 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14489 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14498 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14499 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14728 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14735 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14751 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14756 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14758 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15024 | 107.18 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1503 | 106.47 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1503 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15179 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15235 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15269 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15269 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1534 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16186 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17669 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24495 | 154.86 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26748 | 187.42 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26913 | 183.57 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26913 | 183.59 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26913 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26913 | 195.61 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27151 | 188.13 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.12772 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.14851 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24473 | 155.38 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.26721 | 187.81 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.26886 | 184.02 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.26886 | 184.11 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.26886 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.26886 | 196.06 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.27125 | 188.56 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11583 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11653 | 109.42 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11653 | 109.42 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11673 | 108.86 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11673 | 108.86 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11675 | 108.86 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11675 | 109.03 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11675 | 109.24 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.77 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.84 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.86 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.02 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.02 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.07 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.07 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.17 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.19 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.19 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.25 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.27 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.27 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.27 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.29 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.31 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.31 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.36 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.36 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.4 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.41 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.51 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.52 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.52 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.53 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.54 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.54 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.54 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.54 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.55 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.55 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.59 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.59 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.6 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.6 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.62 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.66 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.73 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.77 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.85 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.85 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.85 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.85 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.85 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.89 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.89 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.9 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.95 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.95 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 109.95 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 110.17 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 110.17 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 110.17 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 110.25 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 110.25 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 110.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 111.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 111.53 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 111.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 114.16 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11681 | 108.84 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11681 | 108.84 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11681 | 108.84 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11683 | 109.07 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11684 | 109.14 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11685 | 108.67 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11685 | 109.14 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11687 | 109.19 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11687 | 109.27 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11687 | 109.27 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11698 | 109.35 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11701 | 109.33 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11704 | 109.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11716 | 109.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11726 | 109.36 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1173 | 109.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1173 | 109.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11755 | 109.5 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11755 | 109.62 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11788 | 111.45 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11788 | 111.45 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11804 | 111.03 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11804 | 111.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11805 | 111.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11816 | 111 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11816 | 111 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11817 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11827 | 110.42 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11845 | 111.06 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11893 | 112.34 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11933 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11933 | 111.7 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11934 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1211 | 116 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12115 | 116.05 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12132 | 116.33 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12132 | 116.33 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12141 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12141 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12141 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12438 | 116.57 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12517 | 117.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12517 | 117.33 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12636 | 113.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12665 | 112.76 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12665 | 112.76 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13048 | 121.98 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13048 | 122.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13089 | 141.25 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1315 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1315 | 134.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1315 | 137.98 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1315 | 138.46 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1315 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1315 | 142.35 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1315 | 142.4 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1315 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15816 | 119.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19347 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10094 | 108.62 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10554 | 101.1 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10558 | 101.14 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10573 | 101.39 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10573 | 101.39 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10581 | 103.3 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10581 | 105.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10581 | 105.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10839 | 101.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10908 | 102.12 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10908 | 102.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11371 | 106.31 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11371 | 107.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11406 | 123.1 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11459 | 113.4 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11459 | 117.19 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11459 | 120.26 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11459 | 120.67 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11459 | 123.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11459 | 124.06 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11459 | 124.1 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11459 | 124.76 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13783 | 104.3 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18669 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08033 | 108.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08033 | 108.49 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05327 | 108.97 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05358 | 104.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05358 | 105.34 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05394 | 105.19 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05401 | 106.48 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05402 | 106.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0542 | 109.15 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05428 | 106.75 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05434 | 106.39 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05435 | 104.31 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05436 | 103.66 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05436 | 104.05 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05451 | 103.96 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05456 | 103.86 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05469 | 103.86 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05471 | 104.29 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05471 | 104.3 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05473 | 104.25 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05473 | 104.25 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05476 | 103.62 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0548 | 103.95 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05484 | 104.21 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05488 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05489 | 103.7 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 103.19 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 103.19 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 103.22 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 103.36 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 103.65 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 103.87 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 103.87 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 103.87 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 103.87 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 103.87 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 103.94 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 103.95 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 104.01 | P13:NBEC#1 GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 104.1 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 104.18 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 104.28 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 104.31 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 104.65 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 104.66 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 104.71 | 531504 CIMWD2 7 345 3WXFMR CIMRNWND2 MPT 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 104.71 | GEN-2010-009_POI_531501_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 104.75 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 104.75 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 104.75 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 104.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 104.87 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 104.87 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 105.04 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 105.37 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 105.49 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 105.49 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 105.51 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 105.53 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 105.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 105.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 105.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 105.74 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 105.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 105.91 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 111.31 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05493 | 103.2 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05493 | 104.74 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05493 | 105.14 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05493 | 105.15 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05493 | 105.37 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05494 | 103.33 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05494 | 105.63 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05495 | 103.48 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05497 | 103.41 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05498 | 103.3 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05498 | 103.46 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05499 | 103.26 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05499 | 103.48 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05499 | 103.92 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05499 | 103.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05499 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.055 | 103.43 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.055 | 106.65 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.055 | 106.7 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05501 | 103.62 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05501 | 104.56 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05506 | 103.51 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05507 | 103.92 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05507 | 104.02 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05508 | 103.93 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05509 | 104.19 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0551 | 103.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0551 | 104.29 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05512 | 104.21 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05512 | 104.21 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05512 | 104.28 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05514 | 104.04 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05515 | 104.7 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05515 | 104.71 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05517 | 103.53 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05517 | 103.72 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05519 | 103.77 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05525 | 103.96 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05527 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05527 | 104.43 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05527 | 105.27 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0553 | 105.48 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05544 | 124.48 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05544 | 124.48 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05544 | 124.48 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05554 | 103.64 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05564 | 104.27 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0557 | 104.71 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0557 | 104.71 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05573 | 104.64 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05587 | 111.68 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05588 | 104.3 | P12:345:WERE:VIOL-WICH-345:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05596 | 104.54 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05607 | 104.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05653 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05653 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05653 | 105.45 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05678 | 106 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05689 | 104.84 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05697 | 104.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05697 | 104.73 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05697 | 104.85 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05697 | 104.85 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05736 | 109.43 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05758 | 106.71 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05762 | 107.32 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05762 | 107.46 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05762 | 107.57 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05762 | 109.51 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05805 | 106.03 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05813 | 105.86 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06167 | 120.22 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06167 | 120.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06167 | 120.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06167 | 120.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06167 | 120.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06177 | 111.96 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07518 | 126.32 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07518 | 126.32 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07518 | 126.32 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07772 | 135.92 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07772 | 135.92 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.05805 | 110.51 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.05805 | 110.51 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.05805 | 110.51 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.06428 | 106.45 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.06428 | 106.46 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.06428 | 106.46 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.06428 | 106.46 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.06428 | 106.46 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.07779 | 112.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.07779 | 112.81 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.07779 | 112.81 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08033 | 122.53 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08033 | 122.53 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11836 | 108.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11836 | 108.49 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 105.19 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08727 | 106.48 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08727 | 106.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08752 | 103.66 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08753 | 106.75 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0876 | 104.31 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0876 | 106.39 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08777 | 103.96 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08781 | 103.86 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08794 | 103.86 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08796 | 104.29 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08796 | 104.3 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08798 | 104.25 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08798 | 104.25 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08801 | 103.62 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08805 | 103.95 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0881 | 104.21 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08814 | 103.7 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 103.19 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 103.19 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 103.2 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 103.22 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 103.36 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 103.65 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 103.87 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 103.87 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 103.87 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 103.87 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 103.87 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 103.94 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 103.95 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 104.01 | P13:NBEC#1 GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 104.1 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 104.18 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 104.28 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 104.31 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 104.65 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 104.66 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 104.71 | 531504 CIMWD2 7 345 3WXFMR CIMRNWND2 MPT 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 104.71 | GEN-2010-009_POI_531501_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 104.74 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 104.75 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 104.75 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 104.75 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 104.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 104.87 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 104.87 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 105.04 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 105.14 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 105.15 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 105.37 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 105.37 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 105.49 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 105.49 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 105.51 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 105.53 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 105.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 105.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 105.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 105.74 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 105.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 105.91 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 111.31 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08819 | 103.33 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08819 | 105.63 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0882 | 103.48 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08822 | 103.3 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08822 | 103.41 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08822 | 103.46 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08822 | 103.48 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08823 | 103.26 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08823 | 103.62 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08823 | 103.92 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08823 | 103.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08823 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08825 | 104.56 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08826 | 103.43 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08829 | 103.51 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08829 | 103.92 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08829 | 104.02 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08831 | 103.93 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08831 | 104.19 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08831 | 104.29 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08833 | 104.28 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08835 | 103.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08836 | 104.21 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08836 | 104.21 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08837 | 103.53 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08837 | 103.72 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08838 | 103.77 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08839 | 104.04 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08843 | 103.96 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08844 | 105.27 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08846 | 105.48 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08847 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08847 | 104.43 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0887 | 103.64 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08872 | 104.27 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08876 | 104.71 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08876 | 104.71 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08879 | 104.64 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0888 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08881 | 104.3 | P12:345:WERE:VIOL-WICH-345:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08915 | 104.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08933 | 104.7 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08933 | 104.71 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08937 | 104.54 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08946 | 111.68 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 106 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08954 | 104.05 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08989 | 104.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08989 | 104.73 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08999 | 104.85 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08999 | 104.85 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09002 | 104.84 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09005 | 106.71 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09007 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09007 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09007 | 105.45 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09076 | 106.03 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 105.86 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09086 | 106.65 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09086 | 106.7 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09194 | 109.43 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09233 | 107.32 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09233 | 107.46 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09233 | 107.57 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09233 | 109.51 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09389 | 108.97 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09458 | 104.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09458 | 105.34 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09663 | 111.96 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09742 | 109.15 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09859 | 120.22 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09859 | 120.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09859 | 120.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09859 | 120.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09859 | 120.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10716 | 124.48 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10716 | 124.48 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10716 | 124.48 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11378 | 126.32 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11378 | 126.32 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11378 | 126.32 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11575 | 135.92 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11575 | 135.92 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1012 | 106.45 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1012 | 106.46 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1012 | 106.46 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1012 | 106.46 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1012 | 106.46 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10977 | 110.51 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10977 | 110.51 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10977 | 110.51 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11639 | 112.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11639 | 112.81 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11639 | 112.81 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11836 | 122.53 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11836 | 122.53 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05931 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05931 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.05949 | 111.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.07641 | 115.99 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05571 | 143.07 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05934 | 139.19 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05953 | 138.87 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06173 | 135.64 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06173 | 135.64 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06176 | 135.15 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06179 | 135.16 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06182 | 135.07 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06183 | 135.48 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.02 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.07 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.14 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.15 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.17 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.44 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.47 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.47 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.49 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.52 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.52 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.52 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.52 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.55 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.55 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.57 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.59 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.62 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.62 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.7 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.7 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.7 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.7 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.72 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.72 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.72 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.73 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.73 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.73 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.75 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.75 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.76 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.77 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.78 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.83 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.95 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.95 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.95 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.95 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.95 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.98 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.98 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 136 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 136.02 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 136.02 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 136.02 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 136.24 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 136.24 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 136.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 136.47 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 136.47 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 136.47 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 137.36 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 139.3 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06185 | 135.15 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06187 | 135.16 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06188 | 135.15 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06188 | 135.15 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06188 | 135.15 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06188 | 135.39 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06188 | 135.44 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06189 | 135.02 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06189 | 135.45 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06189 | 135.49 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06189 | 135.56 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06189 | 135.56 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06196 | 135.61 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06196 | 135.63 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06196 | 135.65 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06196 | 135.73 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06199 | 135.62 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06205 | 136 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06209 | 135.63 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06211 | 135.96 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06211 | 135.96 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06239 | 137.43 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06239 | 137.43 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0624 | 137.34 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0624 | 137.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06245 | 137.04 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06245 | 137.04 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06247 | 137.06 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06247 | 137.16 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06249 | 137.41 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06249 | 137.41 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06255 | 137.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06261 | 136.61 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06272 | 139.39 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06304 | 138.33 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06324 | 137.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06348 | 137.58 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06349 | 137.59 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06386 | 141.34 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06389 | 141.38 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06398 | 141.62 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06398 | 141.62 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06463 | 141.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 142.78 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 142.94 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07143 | 147.71 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07143 | 148.81 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07463 | 149.61 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0919 | 152.28 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0919 | 159.07 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0919 | 161.78 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0919 | 163.27 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09877 | 163.49 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07912 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07912 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08884 | 118.97 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09223 | 109.05 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09223 | 109.05 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09243 | 108.48 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09243 | 108.48 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09245 | 108.48 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09245 | 108.65 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09245 | 108.87 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.39 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.46 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.48 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.64 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.64 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.67 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.67 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.79 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.82 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.82 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.87 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.89 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.9 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.9 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.92 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.94 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.94 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.99 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.99 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.03 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.04 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.14 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.15 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.15 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.16 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.17 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.17 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.17 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.18 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.18 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.18 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.22 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.22 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.23 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.24 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.26 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.3 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.37 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.4 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.49 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.49 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.49 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.49 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.49 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.53 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.53 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.53 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.58 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.58 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.59 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.69 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.69 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.69 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.75 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.75 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.78 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 110.66 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 110.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 111.04 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 111.24 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 113.28 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09252 | 108.45 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09252 | 108.45 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09252 | 108.45 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09253 | 108.69 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09254 | 108.76 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09255 | 108.28 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09255 | 108.77 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09256 | 108.82 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09256 | 108.9 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09256 | 108.9 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09268 | 108.98 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09269 | 108.95 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09274 | 108.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09275 | 109.13 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09275 | 109.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09285 | 109.44 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09293 | 108.99 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09296 | 109.39 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09296 | 109.39 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0935 | 111.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0935 | 111.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09352 | 111.09 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09363 | 110.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09363 | 110.68 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 110.71 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 110.82 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09382 | 110.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09384 | 110.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09412 | 113.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09441 | 112.35 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09441 | 112.35 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09459 | 112.1 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09497 | 111.42 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09525 | 111.03 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09526 | 111.04 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09628 | 115.8 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09634 | 115.86 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0965 | 116.15 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0965 | 116.15 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09784 | 116.25 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09818 | 117.38 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10013 | 117.14 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10013 | 117.29 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10848 | 121.61 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10848 | 122.52 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13148 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14872 | 138.42 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14942 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14942 | 131.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14942 | 135.41 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14942 | 135.88 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14942 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14942 | 139.6 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14942 | 139.63 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14942 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15321 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06895 | 104.17 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06895 | 104.17 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07742 | 103.69 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0839 | 100.92 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08396 | 100.97 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08409 | 101.22 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08409 | 101.22 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08526 | 101.31 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08556 | 102.3 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08726 | 102.08 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08726 | 102.22 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09454 | 105.99 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09454 | 106.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11458 | 108.27 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12961 | 120.63 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13021 | 111.76 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13021 | 115 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13021 | 118.01 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13021 | 118.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13021 | 120.96 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13021 | 121.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13021 | 121.68 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13021 | 122.33 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14784 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.08836 | 102.88 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.185 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18876 | 104.54 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19214 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19525 | 100.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19525 | 100.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19525 | 100.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19525 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19525 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19525 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19525 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19525 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19525 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19525 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19525 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19525 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19525 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19525 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19671 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19671 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19674 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19689 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19689 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19693 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19693 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19716 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19718 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19725 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19752 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19752 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19836 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1989 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19942 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19943 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20064 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20073 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20089 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20095 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20096 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20277 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20331 | 107.18 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20337 | 106.47 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20337 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20643 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21704 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21945 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27646 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27833 | 154.86 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28914 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36936 | 187.42 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37011 | 188.13 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37234 | 183.57 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37234 | 183.59 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37234 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37234 | 195.61 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.20134 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25365 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.27808 | 155.38 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36899 | 187.81 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36975 | 188.56 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37195 | 184.02 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37195 | 184.11 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37195 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37195 | 196.06 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07912 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07912 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07912 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08884 | 119.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08939 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09223 | 109.42 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09223 | 109.42 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09243 | 108.86 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09243 | 108.86 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09245 | 108.86 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09245 | 109.03 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09245 | 109.24 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.77 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.84 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.86 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.02 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.02 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.07 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.07 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.17 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.19 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.19 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.25 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.27 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.27 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.27 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.29 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.31 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.31 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.36 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.36 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.4 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.41 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.51 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.52 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.52 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.53 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.54 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.54 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.54 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.54 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.55 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.55 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.59 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.59 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.6 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.6 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.62 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.66 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.73 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.77 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.85 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.85 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.85 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.85 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.85 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.89 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.89 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.9 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.95 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.95 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 109.95 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 110.17 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 110.17 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 110.17 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 110.25 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 110.25 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 110.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 111.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 111.53 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 111.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 114.16 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09252 | 108.84 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09252 | 108.84 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09252 | 108.84 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09253 | 109.07 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09254 | 109.14 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09255 | 108.67 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09255 | 109.14 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09256 | 109.19 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09256 | 109.27 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09256 | 109.27 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09268 | 109.35 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09269 | 109.33 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09274 | 109.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09275 | 109.5 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09275 | 109.62 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09285 | 109.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09293 | 109.36 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09296 | 109.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09296 | 109.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0935 | 111.45 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0935 | 111.45 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09352 | 111.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09363 | 111 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09363 | 111 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 111.03 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 111.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09382 | 111.06 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09384 | 110.42 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09412 | 113.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09441 | 112.76 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09441 | 112.76 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09459 | 112.34 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09497 | 111.7 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09525 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09526 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09628 | 116 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09634 | 116.05 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0965 | 116.33 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0965 | 116.33 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09784 | 116.57 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10013 | 117.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10013 | 117.33 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10848 | 121.98 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10848 | 122.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13148 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14872 | 141.25 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14942 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14942 | 134.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14942 | 137.98 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14942 | 138.46 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14942 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14942 | 142.35 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14942 | 142.4 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14942 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15321 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06895 | 103.3 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06895 | 105.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06895 | 105.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07742 | 104.3 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0839 | 101.1 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08396 | 101.14 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08409 | 101.39 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08409 | 101.39 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08526 | 101.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08726 | 102.12 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08726 | 102.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09454 | 106.31 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09454 | 107.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11458 | 108.62 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12961 | 123.1 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13021 | 113.4 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13021 | 117.19 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13021 | 120.26 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13021 | 120.67 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13021 | 123.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13021 | 124.06 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13021 | 124.1 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13021 | 124.76 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14784 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.07941 | 112.72 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09853 | 111.33 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10353 | 119.45 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10382 | 106.79 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10382 | 109.48 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10382 | 114.6 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10382 | 115.27 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10382 | 119.86 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10382 | 120.54 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10382 | 120.55 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10382 | 121.12 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08798 | 108.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08798 | 108.49 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05951 | 104.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05951 | 105.34 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06083 | 105.19 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06085 | 104.05 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06091 | 106.48 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06092 | 106.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06118 | 106.75 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06124 | 103.66 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06124 | 106.39 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06125 | 104.31 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06141 | 103.96 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06145 | 103.86 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06159 | 103.86 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06161 | 104.29 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06161 | 104.3 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06163 | 104.25 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06163 | 104.25 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06165 | 103.62 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0617 | 103.95 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06174 | 104.21 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06178 | 103.7 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 103.19 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 103.19 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 103.22 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 103.36 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 103.65 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 103.87 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 103.87 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 103.87 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 103.87 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 103.87 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 103.94 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 103.95 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 104.01 | P13:NBEC#1 GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 104.1 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 104.18 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 104.28 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 104.31 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 104.65 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 104.66 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 104.71 | 531504 CIMWD2 7 345 3WXFMR CIMRNWND2 MPT 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 104.71 | GEN-2010-009_POI_531501_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 104.74 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 104.75 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 104.75 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 104.75 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 104.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 104.87 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 104.87 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 105.04 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 105.14 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 105.15 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 105.37 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 105.37 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 105.49 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 105.49 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 105.51 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 105.53 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 105.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 105.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 105.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 105.74 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 105.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 105.91 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 111.31 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06183 | 103.2 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06183 | 105.63 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06184 | 103.33 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06185 | 103.48 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06187 | 103.3 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06187 | 103.41 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06188 | 103.46 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06188 | 103.48 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06188 | 103.92 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06188 | 103.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06189 | 103.26 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06189 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0619 | 103.43 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0619 | 103.62 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0619 | 104.56 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06195 | 103.51 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06196 | 103.92 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06196 | 104.02 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06198 | 103.93 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06198 | 104.19 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06199 | 104.29 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.062 | 103.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06201 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06201 | 104.21 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06201 | 104.21 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06202 | 104.28 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06203 | 104.04 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06206 | 103.53 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06206 | 103.72 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06209 | 103.77 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06215 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06216 | 105.27 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06218 | 103.96 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06218 | 104.43 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06218 | 105.48 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06241 | 103.64 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06241 | 104.7 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06241 | 104.71 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06249 | 106.65 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06249 | 106.7 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06252 | 104.27 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06258 | 104.71 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06258 | 104.71 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06262 | 104.64 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06267 | 104.3 | P12:345:WERE:VIOL-WICH-345:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06283 | 109.15 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06284 | 111.68 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06292 | 104.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06338 | 104.54 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06353 | 106 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0637 | 104.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0637 | 104.73 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0637 | 108.97 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06399 | 104.85 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06399 | 104.85 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06415 | 104.84 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06422 | 106.71 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06453 | 109.43 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06465 | 106.03 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06473 | 105.86 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06482 | 107.32 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06482 | 107.46 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06482 | 107.57 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06482 | 109.51 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06487 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06487 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06487 | 105.45 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06652 | 124.48 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06652 | 124.48 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06652 | 124.48 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06894 | 111.96 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06933 | 120.22 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06933 | 120.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06933 | 120.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06933 | 120.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06933 | 120.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08305 | 126.32 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08305 | 126.32 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08305 | 126.32 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08538 | 135.92 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08538 | 135.92 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.06912 | 110.51 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.06912 | 110.51 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.06912 | 110.51 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.07194 | 106.45 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.07194 | 106.46 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.07194 | 106.46 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.07194 | 106.46 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.07194 | 106.46 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08565 | 112.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08565 | 112.81 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08565 | 112.81 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08798 | 122.53 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08798 | 122.53 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27L | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10132 | 100.21 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27L | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10132 | 100.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27L | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 1 | 145.27 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27L | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 1 | 144.13 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27L | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12282 | 100.21 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27L | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12282 | 100.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27L | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.24742 | 100.21 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27L | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.24742 | 100.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05104 | 138.19 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05104 | 130.1 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05104 | 137.17 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12255 | 107.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12255 | 107.29 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09147 | 104.57 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0915 | 106.59 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09151 | 106.62 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09174 | 103.97 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09174 | 106.9 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09181 | 106.53 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09187 | 103.66 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09203 | 103.29 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09209 | 103.13 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0922 | 103.65 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0922 | 103.65 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09221 | 102.88 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09221 | 103.12 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09228 | 102.89 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09234 | 103.45 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09236 | 102.64 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 102.47 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 102.47 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 102.48 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 102.5 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 102.65 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 102.91 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 103.1 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 103.11 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 103.18 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 103.18 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 103.18 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 103.19 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 103.2 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 103.35 | GEN-2023-116_POI_640252_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 103.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 103.44 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 103.51 | P15:230:UMZB:# 2982 #:: DHC IN NE. STEGALL DC CONVERTER STATION AND SHUNT DEVICE:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 103.54 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 103.63 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 103.93 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 103.98 | P23:345:XEL:8P2 KING | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 104 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 104.01 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 104.02 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 104.06 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 104.12 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 104.12 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 104.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 104.3 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 105.07 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 105.12 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 105.13 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 105.2 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 105.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 105.26 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 105.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 105.43 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 105.44 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 105.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 105.53 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 105.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 105.64 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 105.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 105.79 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 105.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 111.13 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09245 | 105.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09246 | 102.76 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09247 | 102.54 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09247 | 102.66 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09248 | 102.73 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09248 | 102.76 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09248 | 102.91 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09249 | 103.18 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09249 | 103.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09249 | 103.18 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09249 | 103.23 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0925 | 102.54 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0925 | 102.61 | P12:345:AMMO::MAYWOOD:SUBT:77 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09251 | 103.82 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09253 | 102.76 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09254 | 103.18 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09254 | 103.28 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09255 | 102.79 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09256 | 103.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09257 | 103.23 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09257 | 103.58 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09259 | 103.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09261 | 102.61 | 300143 4VALLEY 138 514830 FITZGRD4 138 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09262 | 102.86 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09262 | 103.04 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09263 | 103.52 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09263 | 103.52 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09264 | 104.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09266 | 103.26 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09267 | 103.02 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09267 | 103.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 104.57 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09271 | 104.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09273 | 102.79 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09274 | 103.74 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09274 | 103.74 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09294 | 103.57 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09297 | 102.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09302 | 103.37 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09308 | 103.24 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09308 | 103.75 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09308 | 103.75 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09337 | 103.64 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09351 | 104.88 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09354 | 103.64 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09368 | 103.95 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09368 | 103.95 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0938 | 111.11 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09383 | 103.35 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09414 | 105.73 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09414 | 105.73 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09415 | 103.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09416 | 104.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09416 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09416 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09419 | 103.92 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09419 | 103.92 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0942 | 104.13 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0942 | 104.13 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09503 | 105.39 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09511 | 105.24 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09539 | 105.91 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09539 | 105.96 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09638 | 108.66 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09681 | 106.49 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09681 | 106.62 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09681 | 106.74 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09681 | 108.72 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0972 | 103.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0972 | 104.57 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09871 | 108.81 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10102 | 111.24 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10288 | 108.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10337 | 119.41 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10337 | 119.41 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10337 | 119.41 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10337 | 119.41 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10337 | 119.41 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1133 | 124.17 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1133 | 124.17 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1133 | 124.17 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11679 | 124.55 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11679 | 124.55 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11679 | 124.55 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12 | 134.94 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12 | 134.94 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10592 | 104.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10592 | 104.23 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10592 | 104.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10592 | 104.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10592 | 104.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11585 | 109.24 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11585 | 109.24 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11585 | 109.24 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11933 | 109.9 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11933 | 109.9 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11933 | 109.9 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12255 | 121.32 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12255 | 121.32 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.06078 | 111.5 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.07972 | 114.4 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05976 | 138.53 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05981 | 142.55 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06 | 138.2 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06275 | 134.27 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06275 | 134.32 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06276 | 134.67 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.02 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.07 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.08 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.08 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.09 | P23:345:XEL:8N17 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.09 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.1 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.62 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.65 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.65 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.67 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.7 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.7 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.71 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.71 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.74 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.74 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.75 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.77 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.8 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.81 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.87 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.88 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.88 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.88 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.89 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.89 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.9 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.91 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.91 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.91 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.93 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.93 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.94 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.95 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 135 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 135.03 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 135.05 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 135.11 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 135.11 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 135.12 | P11:21:EES:RVB:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 135.12 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 135.12 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 135.14 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 135.14 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 135.17 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 135.19 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 135.19 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 135.19 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 135.44 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 135.44 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 135.5 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 135.67 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 135.67 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 135.67 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 136.51 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 138.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06279 | 134.33 | 539784 ENSNGW 3 115 3WXFMR ENSIGN WIND 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0628 | 134.35 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0628 | 134.36 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0628 | 134.36 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0628 | 134.36 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0628 | 134.58 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06281 | 134.58 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06281 | 134.62 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06282 | 133.94 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06282 | 134.68 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06282 | 134.68 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06282 | 134.74 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06282 | 134.74 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06287 | 134.64 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06288 | 134.22 | 560022 CRAWFISH_DR 345 774180 G23-110-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06289 | 134.89 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0629 | 134.82 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06292 | 134.81 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06292 | 134.81 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06292 | 134.81 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06292 | 134.81 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06297 | 134.86 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06305 | 135.18 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06305 | 135.18 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06333 | 136.26 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06333 | 136.26 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06333 | 136.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06335 | 136.3 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06341 | 135.85 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06341 | 135.9 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06341 | 136.03 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06341 | 136.03 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06342 | 136.42 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06342 | 136.42 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06352 | 136.2 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06356 | 138.37 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06361 | 135.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06397 | 137.2 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0642 | 136.64 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06463 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06463 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06489 | 140.07 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06493 | 140.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06501 | 140.41 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06501 | 140.41 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06583 | 140.35 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06745 | 141.43 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06745 | 141.57 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07346 | 148.33 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07366 | 146.73 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07366 | 147.76 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08502 | 150.42 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08502 | 154 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08502 | 156.76 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08502 | 157.19 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08502 | 159.91 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08502 | 161.9 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.10753 | 159.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07352 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07352 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07352 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08757 | 110.39 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08895 | 108.23 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08895 | 108.23 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08913 | 107.69 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08913 | 107.69 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08915 | 107.69 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08915 | 108.08 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.35 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.38 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.39 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.4 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.4 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.4 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.6 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.69 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.84 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.85 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.86 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.88 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.88 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.02 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.02 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.08 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.1 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.1 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.1 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.12 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.15 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.15 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.19 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.2 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.23 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.34 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.35 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.36 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.36 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.37 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.37 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.37 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.38 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.39 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.39 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.42 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.42 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.43 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.44 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.45 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.5 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.55 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.59 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.67 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.67 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.69 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.69 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.69 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.71 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.71 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.73 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.78 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.78 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.78 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.91 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.91 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.91 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.96 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.97 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.99 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 109.92 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 109.95 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 110.21 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 110.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 112.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08921 | 107.69 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08921 | 107.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08921 | 107.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08923 | 107.91 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08923 | 107.91 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08925 | 107.18 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08925 | 107.96 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08925 | 108.02 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08925 | 108.03 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08927 | 108.11 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08927 | 108.11 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08935 | 107.98 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0894 | 108.21 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.21 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.41 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08954 | 108.27 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08968 | 108.64 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08968 | 108.64 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09022 | 109.95 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09022 | 109.95 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09028 | 110.01 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09037 | 109.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09037 | 109.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09038 | 109.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09038 | 109.68 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0906 | 109.91 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09068 | 109.29 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09078 | 112.06 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09104 | 111.18 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09104 | 111.18 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09131 | 111 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09176 | 110.36 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09238 | 110.26 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09239 | 110.27 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09317 | 114.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09324 | 114.62 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0934 | 114.95 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0934 | 114.95 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09505 | 115.01 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09761 | 115.82 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09761 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10767 | 120.81 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10767 | 121.59 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13076 | 136.58 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13137 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13137 | 130.57 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13137 | 133.59 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13137 | 134.05 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13137 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13137 | 137.75 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13137 | 137.78 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13137 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13528 | 121.87 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14765 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06407 | 101.8 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06407 | 103.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06407 | 103.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0814 | 100.18 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0814 | 100.18 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08283 | 100.23 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08507 | 100.94 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08507 | 101.06 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09383 | 105.29 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09383 | 105.97 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11395 | 119.03 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11448 | 110.17 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11448 | 113.79 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11448 | 116.43 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11448 | 116.82 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11448 | 119.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11448 | 120.05 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11448 | 120.08 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11448 | 121.11 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11789 | 106.21 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14245 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.05737 | 100.95 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14362 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15277 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16477 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16669 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1679 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17044 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17054 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1707 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17075 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17077 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17081 | 101.44 | Potential P4 Event - POI 523823_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17302 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17325 | 104.75 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17331 | 104.09 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17331 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17703 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19245 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24471 | 152.61 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26251 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31198 | 183.79 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3142 | 179.87 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3142 | 179.92 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3142 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3142 | 191.94 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31486 | 184.51 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.17657 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24085 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24449 | 153.1 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31167 | 184.16 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31388 | 180.34 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31388 | 180.35 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31388 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31388 | 192.34 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31456 | 184.91 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07352 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07352 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07352 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08757 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08757 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08769 | 110.28 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08895 | 108.46 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08895 | 108.46 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08913 | 107.93 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08913 | 107.93 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08915 | 107.93 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08915 | 108.31 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.6 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.64 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.64 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.65 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.65 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.84 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.91 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.93 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.93 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.93 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.08 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.09 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.1 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.14 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.14 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.24 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.26 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.26 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.31 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.33 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.34 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.34 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.36 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.38 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.38 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.43 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.43 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.47 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.48 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.57 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.58 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.59 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.59 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.6 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.6 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.6 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.61 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.62 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.62 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.65 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.65 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.66 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.67 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.69 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.73 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.78 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.82 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.9 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.9 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.94 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.94 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.96 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 109 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 109 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 109.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 109.26 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 109.26 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 109.26 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 109.33 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 109.33 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 109.38 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 110.13 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 110.7 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 113.2 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08923 | 108.15 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08923 | 108.15 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08925 | 107.43 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08925 | 107.43 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08925 | 108.2 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08925 | 108.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08925 | 108.27 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08927 | 108.34 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08927 | 108.34 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08935 | 108.22 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0894 | 108.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.38 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.38 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.64 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08954 | 108.5 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08968 | 108.87 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08968 | 108.87 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09022 | 110.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09022 | 110.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09028 | 110.2 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09037 | 109.68 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09037 | 109.73 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09038 | 109.88 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09038 | 109.88 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0906 | 110.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09068 | 109.48 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09078 | 112.33 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09104 | 111.45 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09104 | 111.45 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09131 | 111.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09176 | 110.52 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09238 | 110.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09239 | 110.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09317 | 114.65 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09324 | 114.7 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0934 | 115.03 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0934 | 115.03 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09505 | 115.2 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09761 | 115.8 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09761 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10767 | 121.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10767 | 121.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13076 | 139.23 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13137 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13137 | 132.76 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13137 | 135.94 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13137 | 136.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13137 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13137 | 140.37 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13137 | 140.41 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13137 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13528 | 122.24 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14765 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06407 | 102.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06407 | 104.7 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06407 | 104.7 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0814 | 100.26 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0814 | 100.26 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08283 | 100.4 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08507 | 100.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08507 | 101.05 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09383 | 105.57 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09383 | 106.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11395 | 121.34 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11448 | 111.55 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11448 | 115.7 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11448 | 118.48 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11448 | 118.89 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11448 | 121.6 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11448 | 122.33 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11448 | 122.37 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11448 | 123.4 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11789 | 106.54 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14245 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.06849 | 111.48 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08306 | 116.16 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08332 | 104.1 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08332 | 107.2 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08332 | 111.56 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08332 | 112.2 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08332 | 116.48 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08332 | 117.09 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08332 | 117.11 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08332 | 118.06 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09423 | 106.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11708 | 107.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11708 | 107.29 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08675 | 104.57 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08679 | 106.59 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0868 | 106.62 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08702 | 103.97 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08702 | 106.9 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08709 | 106.53 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08715 | 103.66 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08732 | 103.29 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08737 | 103.13 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08748 | 103.65 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08748 | 103.65 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08749 | 102.88 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08749 | 103.12 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08756 | 102.89 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08763 | 103.45 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08764 | 102.64 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 102.47 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 102.47 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 102.5 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 102.65 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 102.91 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 103.1 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 103.11 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 103.18 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 103.18 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 103.18 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 103.19 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 103.2 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 103.35 | GEN-2023-116_POI_640252_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 103.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 103.44 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 103.51 | P15:230:UMZB:# 2982 #:: DHC IN NE. STEGALL DC CONVERTER STATION AND SHUNT DEVICE:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 103.54 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 103.63 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 103.93 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 103.98 | P23:345:XEL:8P2 KING | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 104 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 104.01 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 104.02 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 104.06 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 104.12 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 104.12 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 104.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 104.3 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 105.07 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 105.12 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 105.13 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 105.2 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 105.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 105.26 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 105.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 105.43 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 105.44 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 105.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 105.53 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 105.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 105.64 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 105.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 105.79 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 105.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 111.13 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08773 | 102.48 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08773 | 105.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08775 | 102.66 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08775 | 102.76 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08776 | 102.54 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08776 | 102.73 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08776 | 102.76 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08777 | 102.91 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08777 | 103.18 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08777 | 103.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08777 | 103.18 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08777 | 103.23 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08778 | 102.54 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08778 | 102.61 | P12:345:AMMO::MAYWOOD:SUBT:77 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08779 | 103.82 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08781 | 102.76 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08783 | 103.18 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08783 | 103.28 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08784 | 102.79 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08785 | 103.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08786 | 103.23 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08786 | 103.58 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08788 | 103.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08789 | 102.61 | 300143 4VALLEY 138 514830 FITZGRD4 138 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08791 | 102.86 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08791 | 103.04 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08791 | 103.52 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08791 | 103.52 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08792 | 104.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08795 | 103.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08796 | 103.26 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08797 | 103.02 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08798 | 104.57 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.088 | 104.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08802 | 102.79 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08803 | 103.74 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08803 | 103.74 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08824 | 103.57 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08826 | 102.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08833 | 103.37 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08836 | 103.24 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08839 | 103.75 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08839 | 103.75 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08868 | 103.64 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08885 | 104.88 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08887 | 103.95 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08887 | 103.95 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08889 | 103.64 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08903 | 111.11 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08908 | 103.35 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 104.13 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 104.13 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08951 | 105.73 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08951 | 105.73 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08952 | 103.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08954 | 103.92 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08954 | 103.92 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08966 | 104.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08966 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08966 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09032 | 105.91 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09032 | 105.96 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09035 | 105.39 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09043 | 105.24 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09148 | 108.66 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 106.49 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 106.62 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 106.74 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 108.72 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09326 | 108.81 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.094 | 103.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.094 | 104.57 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09604 | 111.24 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09649 | 108.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09813 | 119.41 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09813 | 119.41 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09813 | 119.41 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09813 | 119.41 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09813 | 119.41 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1061 | 124.17 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1061 | 124.17 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1061 | 124.17 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11126 | 124.55 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11126 | 124.55 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11126 | 124.55 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11453 | 134.94 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11453 | 134.94 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10068 | 104.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10068 | 104.23 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10068 | 104.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10068 | 104.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10068 | 104.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10865 | 109.24 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10865 | 109.24 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10865 | 109.24 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11381 | 109.9 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11381 | 109.9 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11381 | 109.9 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11708 | 121.32 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11708 | 121.32 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.06131 | 111.5 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.07747 | 114.4 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05075 | 165.4 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05289 | 142.55 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05975 | 138.53 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05988 | 138.2 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06076 | 134.22 | 560022 CRAWFISH_DR 345 774180 G23-110-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06138 | 134.27 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06139 | 134.32 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06139 | 134.67 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.02 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.07 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.08 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.08 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.09 | P23:345:XEL:8N17 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.09 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.1 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.62 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.65 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.65 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.67 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.7 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.7 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.71 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.71 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.74 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.74 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.75 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.77 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.8 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.81 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.87 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.88 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.88 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.88 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.89 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.89 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.9 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.91 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.91 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.91 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.93 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.93 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.94 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.95 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 135 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 135.03 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 135.05 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 135.11 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 135.11 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 135.12 | P11:21:EES:RVB:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 135.12 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 135.12 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 135.14 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 135.14 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 135.17 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 135.19 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 135.19 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 135.19 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 135.44 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 135.44 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 135.5 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 135.67 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 135.67 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 135.67 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 136.51 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 138.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06143 | 134.33 | 539784 ENSNGW 3 115 3WXFMR ENSIGN WIND 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06143 | 134.35 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06143 | 134.58 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06144 | 134.36 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06144 | 134.36 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06144 | 134.36 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06144 | 134.58 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06144 | 134.62 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 133.94 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 134.68 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 134.68 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 134.74 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 134.74 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06149 | 134.64 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06151 | 134.89 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06152 | 134.82 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06155 | 134.81 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06155 | 134.81 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06155 | 134.81 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06155 | 134.81 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0616 | 134.86 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06167 | 135.18 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06167 | 135.18 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06194 | 136.26 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06194 | 136.26 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06194 | 136.3 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06196 | 136.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.062 | 136.03 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.062 | 136.03 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06202 | 135.85 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06202 | 135.9 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06206 | 136.42 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06206 | 136.42 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06209 | 136.2 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06214 | 135.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06223 | 138.37 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06257 | 137.2 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06279 | 136.64 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06297 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06298 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06341 | 140.07 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06345 | 140.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06353 | 140.41 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06353 | 140.41 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0641 | 140.35 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06554 | 141.43 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06554 | 141.57 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07054 | 146.73 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07054 | 147.76 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07597 | 148.33 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09075 | 150.42 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09075 | 154 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09075 | 156.76 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09075 | 157.19 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09075 | 159.91 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09075 | 161.9 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09609 | 159.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09384 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09384 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09384 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10176 | 110.39 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10221 | 108.23 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10221 | 108.23 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10239 | 107.69 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10239 | 107.69 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10241 | 108.08 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10242 | 107.39 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10242 | 107.4 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10242 | 107.69 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 107.35 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 107.38 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 107.4 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 107.4 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 107.6 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 107.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 107.69 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 107.84 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 107.85 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 107.86 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 107.88 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 107.88 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.02 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.02 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.08 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.1 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.1 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.1 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.12 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.15 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.15 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.19 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.2 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.23 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.34 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.35 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.36 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.36 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.37 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.37 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.37 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.38 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.39 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.39 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.42 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.42 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.43 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.44 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.45 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.5 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.55 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.59 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.67 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.67 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.69 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.69 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.69 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.71 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.71 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.73 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.78 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.78 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.78 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.91 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.91 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.91 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.96 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.97 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.99 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 109.92 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 109.95 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 110.21 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 110.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 112.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10248 | 107.69 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10248 | 107.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10248 | 107.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10249 | 107.91 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1025 | 107.91 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10251 | 107.96 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10251 | 108.02 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10251 | 108.03 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10252 | 107.18 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10253 | 108.11 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10253 | 108.11 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10261 | 107.98 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10265 | 108.21 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1027 | 108.21 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1027 | 108.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1027 | 108.41 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1028 | 108.27 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10292 | 108.64 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10292 | 108.64 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10345 | 109.95 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10345 | 109.95 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10345 | 110.01 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10356 | 109.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10356 | 109.68 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10359 | 109.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10359 | 109.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10375 | 109.91 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10377 | 109.29 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10404 | 112.06 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10431 | 111.18 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10431 | 111.18 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10452 | 111 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10494 | 110.36 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10515 | 110.26 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10515 | 110.27 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10622 | 114.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1063 | 114.62 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10645 | 114.95 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10645 | 114.95 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10761 | 115.01 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10989 | 115.82 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10989 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11797 | 120.81 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11797 | 121.59 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13816 | 121.87 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15736 | 136.58 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1581 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1581 | 130.57 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1581 | 133.59 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1581 | 134.05 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1581 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1581 | 137.75 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1581 | 137.78 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1581 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16962 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08178 | 101.8 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08178 | 103.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08178 | 103.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09277 | 100.18 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09277 | 100.18 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09378 | 100.23 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09576 | 100.94 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09576 | 101.06 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10281 | 105.29 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10281 | 105.97 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1204 | 106.21 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13713 | 119.03 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13778 | 110.17 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13778 | 113.79 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13778 | 116.43 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13778 | 116.82 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13778 | 119.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13778 | 120.05 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13778 | 120.08 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13778 | 121.11 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16365 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09511 | 100.95 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19143 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19593 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20251 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20444 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20556 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20789 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20799 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20815 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2082 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20821 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20825 | 101.44 | Potential P4 Event - POI 523823_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20978 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21058 | 104.75 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21064 | 104.09 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21064 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21334 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22576 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27825 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.29449 | 152.61 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.383 | 183.79 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38309 | 184.51 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38618 | 179.87 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38618 | 179.92 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38618 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38618 | 191.94 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.20713 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25529 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.29424 | 153.1 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38261 | 184.16 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38271 | 184.91 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38578 | 180.34 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38578 | 180.35 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38578 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38578 | 192.34 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09384 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09384 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09384 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09821 | 110.28 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10176 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10176 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10221 | 108.46 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10221 | 108.46 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10239 | 107.93 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10239 | 107.93 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10241 | 108.31 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10242 | 107.64 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10242 | 107.65 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10242 | 107.93 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 107.6 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 107.64 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 107.65 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 107.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 107.84 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 107.91 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 107.93 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 107.93 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 107.93 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.08 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.09 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.1 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.14 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.14 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.24 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.26 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.26 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.31 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.33 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.34 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.34 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.36 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.38 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.38 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.43 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.43 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.47 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.48 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.57 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.58 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.59 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.59 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.6 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.6 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.6 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.61 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.62 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.62 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.65 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.65 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.66 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.67 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.69 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.73 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.78 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.82 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.9 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.9 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.94 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.94 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.96 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 109 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 109 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 109.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 109.26 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 109.26 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 109.26 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 109.33 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 109.33 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 109.38 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 110.13 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 110.7 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 113.2 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10249 | 108.15 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1025 | 108.15 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10251 | 108.2 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10251 | 108.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10251 | 108.27 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10252 | 107.43 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10252 | 107.43 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10253 | 108.34 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10253 | 108.34 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10261 | 108.22 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10265 | 108.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1027 | 108.38 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1027 | 108.38 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1027 | 108.64 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1028 | 108.5 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10292 | 108.87 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10292 | 108.87 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10345 | 110.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10345 | 110.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10345 | 110.2 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10356 | 109.88 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10356 | 109.88 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10359 | 109.68 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10359 | 109.73 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10375 | 110.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10377 | 109.48 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10404 | 112.33 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10431 | 111.45 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10431 | 111.45 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10452 | 111.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10494 | 110.52 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10515 | 110.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10515 | 110.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10622 | 114.65 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1063 | 114.7 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10645 | 115.03 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10645 | 115.03 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10761 | 115.2 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10989 | 115.8 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10989 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11797 | 121.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11797 | 121.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13816 | 122.24 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15736 | 139.23 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1581 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1581 | 132.76 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1581 | 135.94 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1581 | 136.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1581 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1581 | 140.37 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1581 | 140.41 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1581 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16962 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08178 | 102.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08178 | 104.7 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08178 | 104.7 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09277 | 100.26 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09277 | 100.26 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09378 | 100.4 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09576 | 100.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09576 | 101.05 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10281 | 105.57 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10281 | 106.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1204 | 106.54 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13713 | 121.34 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13778 | 111.55 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13778 | 115.7 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13778 | 118.48 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13778 | 118.89 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13778 | 121.6 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13778 | 122.33 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13778 | 122.37 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13778 | 123.4 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16365 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08873 | 111.48 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10624 | 106.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11205 | 116.16 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11235 | 104.1 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11235 | 107.2 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11235 | 111.56 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11235 | 112.2 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11235 | 116.48 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11235 | 117.09 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11235 | 117.11 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11235 | 118.06 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 528413 TAYLOR 3 115 528449 W_BENDER 3 115 1 | 143 | 157 | 1 | 136.32 | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1 | Cumulative Impact | Rebuild the existing TAYLOR3 to W_BENDER3 115 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1153 | 107.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1153 | 107.29 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0854 | 104.57 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08544 | 106.59 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08545 | 106.62 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08567 | 103.97 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08568 | 106.9 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08575 | 106.53 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08581 | 103.66 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 103.29 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08603 | 103.13 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08614 | 103.65 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08614 | 103.65 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08615 | 102.88 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08615 | 103.12 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08621 | 102.89 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08628 | 103.45 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0863 | 102.64 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.47 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.47 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.48 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.5 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.65 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.91 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.1 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.11 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.18 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.18 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.18 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.19 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.2 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.35 | GEN-2023-116_POI_640252_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.44 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.51 | P15:230:UMZB:# 2982 #:: DHC IN NE. STEGALL DC CONVERTER STATION AND SHUNT DEVICE:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.54 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.63 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.93 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.98 | P23:345:XEL:8P2 KING | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.01 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.02 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.06 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.12 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.12 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.3 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.07 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.12 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.13 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.2 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.26 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.43 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.44 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.53 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.64 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.79 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 111.13 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0864 | 102.76 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08641 | 102.54 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08641 | 102.66 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08642 | 102.73 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08642 | 102.76 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08643 | 102.91 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08643 | 103.18 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08643 | 103.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08643 | 103.18 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08643 | 103.23 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08644 | 102.54 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08644 | 102.61 | P12:345:AMMO::MAYWOOD:SUBT:77 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08645 | 103.82 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 102.76 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 102.79 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 103.18 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 103.28 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08651 | 103.23 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08651 | 103.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08651 | 103.58 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08653 | 103.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08655 | 102.61 | 300143 4VALLEY 138 514830 FITZGRD4 138 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08656 | 102.86 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08657 | 103.04 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08657 | 103.52 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08657 | 103.52 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08658 | 104.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08661 | 103.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08662 | 103.26 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08663 | 103.02 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08664 | 104.57 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08666 | 104.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08668 | 102.79 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08669 | 103.74 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08669 | 103.74 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0869 | 103.57 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08692 | 102.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.087 | 103.37 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08706 | 103.75 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08706 | 103.75 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08734 | 103.64 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08738 | 103.24 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08749 | 103.95 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08749 | 103.95 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08753 | 104.88 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08758 | 103.64 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08768 | 111.11 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08816 | 104.13 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08816 | 104.13 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0882 | 105.73 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0882 | 105.73 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08822 | 103.92 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08822 | 103.92 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08822 | 103.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08841 | 104.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08841 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08841 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08892 | 105.91 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08892 | 105.96 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08902 | 105.39 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0891 | 105.24 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08929 | 103.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08929 | 104.57 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08973 | 103.35 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09008 | 108.66 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09048 | 106.49 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09048 | 106.62 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09048 | 106.74 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09048 | 108.72 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09148 | 108.81 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09376 | 108.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09455 | 111.24 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09664 | 119.41 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09664 | 119.41 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09664 | 119.41 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09664 | 119.41 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09664 | 119.41 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10434 | 124.17 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10434 | 124.17 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10434 | 124.17 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10946 | 124.55 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10946 | 124.55 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10946 | 124.55 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11275 | 134.94 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11275 | 134.94 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09919 | 104.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09919 | 104.23 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09919 | 104.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09919 | 104.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09919 | 104.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10689 | 109.24 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10689 | 109.24 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10689 | 109.24 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11201 | 109.9 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11201 | 109.9 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11201 | 109.9 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1153 | 121.32 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1153 | 121.32 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13 | 111.5 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13888 | 102.83 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13888 | 102.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13888 | 102.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13915 | 103.68 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13915 | 103.68 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.1395 | 104.16 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17344 | 114.4 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17719 | 107.58 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18762 | 107.83 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18762 | 108.41 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18762 | 108.41 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18788 | 109.17 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18788 | 109.17 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18824 | 109.67 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.11 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.11 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.11 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.12 | ASGI-2011-004_POI_525915_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.17 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.33 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.59 | GEN-2011-025_POI_525803_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.64 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 101.04 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 101.04 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 101.04 | GEN-2023-086_POI_773700_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 103.21 | 774381 GEN-2023-120 115 774382 G23-120XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 103.21 | GEN-2023-120_POI_525192_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 105.36 | 524757 BETHEL_COL 3 115 524755 BETHEL_COL11 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 106.65 | GEN-2014-040_POI_524746_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07656 | 100.11 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07656 | 100.11 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0766 | 100.13 | 515375 WWRDEHV7 345 516059 BECKHAM7 345 2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07661 | 100.84 | Potential P4 Event - POI 776000_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07662 | 100.19 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07662 | 100.25 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07662 | 100.29 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07662 | 100.29 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07662 | 100.31 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07663 | 100.19 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07665 | 100.32 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07665 | 100.32 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07678 | 100.67 | POI 515800_22 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07678 | 100.69 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07682 | 102.94 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07725 | 101.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07725 | 102.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 103.85 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 104.28 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 105.13 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 105.26 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07843 | 102.17 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07935 | 103.83 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08031 | 105.78 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08139 | 118.93 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09004 | 115.77 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09004 | 116.09 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 116.35 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 116.35 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09015 | 116.49 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09265 | 117.56 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09265 | 120.95 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.10347 | 127.17 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.66 | 524757 BETHEL_COL 3 115 524756 BETHEL_COL21 34.5 2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 101.52 | 774381 GEN-2023-120 115 774382 G23-120XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 101.52 | GEN-2023-120_POI_525192_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 103.4 | 524757 BETHEL_COL 3 115 524755 BETHEL_COL11 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 105.44 | GEN-2014-040_POI_524746_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07682 | 101.12 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07725 | 100.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07725 | 100.64 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 102.3 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 102.76 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 103.7 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 103.84 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07935 | 102.14 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08031 | 104.12 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08139 | 118.92 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09004 | 114.41 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09004 | 114.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 115.06 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 115.06 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09015 | 115.22 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09265 | 115.67 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09265 | 119.13 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.10347 | 125.32 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.11102 | 138.46 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1502 | 134.22 | 560022 CRAWFISH_DR 345 774180 G23-110-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15121 | 134.27 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15121 | 134.32 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15122 | 134.67 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.02 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.07 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.08 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.08 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.09 | P23:345:XEL:8N17 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.09 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.1 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.62 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.65 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.65 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.67 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.7 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.7 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.71 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.71 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.74 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.74 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.75 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.77 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.8 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.81 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.87 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.88 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.88 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.88 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.89 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.89 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.9 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.91 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.91 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.91 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.93 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.93 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.94 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.95 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.03 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.05 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.11 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.11 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.12 | P11:21:EES:RVB:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.12 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.12 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.14 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.14 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.17 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.19 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.19 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.19 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.44 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.44 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.5 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.67 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.67 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.67 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 136.51 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 138.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15125 | 134.33 | 539784 ENSNGW 3 115 3WXFMR ENSIGN WIND 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.35 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.36 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.36 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.36 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.58 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.58 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15127 | 134.62 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15127 | 134.68 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15127 | 134.68 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15128 | 133.94 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15128 | 134.74 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15128 | 134.74 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15132 | 134.64 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15135 | 134.82 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15136 | 134.89 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15138 | 134.81 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15138 | 134.81 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15138 | 134.81 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15138 | 134.81 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15142 | 134.86 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15149 | 135.18 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15149 | 135.18 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15175 | 136.3 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15176 | 136.26 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15176 | 136.26 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15181 | 136.03 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15181 | 136.03 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15184 | 135.85 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15184 | 135.9 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1519 | 136.2 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15191 | 135.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15216 | 136.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15225 | 136.42 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15225 | 136.42 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15237 | 137.2 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15258 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15259 | 136.64 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15259 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15321 | 140.07 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15324 | 140.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15333 | 140.41 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15333 | 140.41 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15386 | 140.35 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15504 | 141.43 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15504 | 141.57 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15736 | 138.37 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15747 | 138.2 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15801 | 138.53 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15893 | 146.73 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15893 | 147.76 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16243 | 142.55 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 150.42 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 154 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 156.76 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 157.19 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 159.91 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 161.9 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16762 | 148.33 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17038 | 159.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1998 | 162.73 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1998 | 164.74 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1998 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19991 | 165.01 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19991 | 165.01 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20014 | 165.4 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.2073 | 114.05 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.2073 | 114.9 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10203 | 112.47 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17709 | 108.23 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17709 | 108.23 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17726 | 107.69 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17726 | 107.69 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17729 | 107.69 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17729 | 108.08 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.35 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.38 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.39 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.4 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.4 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.4 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.6 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.69 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.84 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.85 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.86 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.88 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.88 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.02 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.02 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.08 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.1 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.1 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.1 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.12 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.15 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.15 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.19 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.2 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.23 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.34 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.35 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.36 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.36 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.37 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.37 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.37 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.38 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.39 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.39 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.42 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.42 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.43 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.44 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.45 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.5 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.55 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.59 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.67 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.67 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.69 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.69 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.69 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.71 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.71 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.73 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.78 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.78 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.78 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.91 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.91 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.91 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.96 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.97 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.99 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.92 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.95 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 110.21 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 110.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 112.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17735 | 107.69 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17735 | 107.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17735 | 107.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17736 | 107.91 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17737 | 107.91 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 107.96 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 108.02 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 108.03 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17739 | 107.18 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1774 | 108.11 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1774 | 108.11 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17748 | 107.98 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17752 | 108.21 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17757 | 108.21 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17757 | 108.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 108.41 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17767 | 108.27 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17778 | 108.64 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17778 | 108.64 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1783 | 110.01 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17831 | 109.95 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17831 | 109.95 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17841 | 109.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17841 | 109.68 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17845 | 109.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17845 | 109.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17853 | 109.29 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17858 | 109.91 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 111 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 110.26 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 110.27 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17976 | 110.36 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17997 | 112.06 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17999 | 110.39 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18023 | 111.18 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18023 | 111.18 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18104 | 114.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18111 | 114.62 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18127 | 114.95 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18127 | 114.95 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18237 | 115.01 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18418 | 115.82 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18418 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19039 | 120.81 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19039 | 121.59 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19703 | 121.87 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20217 | 136.58 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 130.57 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 133.59 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 134.05 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 137.75 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 137.78 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2936 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15797 | 100.18 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15797 | 100.18 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15893 | 100.23 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1605 | 100.94 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1605 | 101.06 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16592 | 105.29 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16592 | 105.97 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17171 | 106.21 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17618 | 119.03 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 110.17 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 113.79 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 116.43 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 116.82 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 119.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 120.05 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 120.08 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 121.11 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 101.8 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 103.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 103.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28327 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1132 | 100.95 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2206 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22083 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2236 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22378 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22589 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.226 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22616 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22621 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22622 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22626 | 101.44 | Potential P4 Event - POI 523823_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22771 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22855 | 104.75 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22861 | 104.09 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22861 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23058 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24019 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24771 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26243 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37835 | 152.61 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41566 | 184.51 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41702 | 183.79 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 179.87 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 179.92 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 191.94 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22037 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24078 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37802 | 153.1 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41526 | 184.91 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4166 | 184.16 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 180.34 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 180.35 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 192.34 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10203 | 113.2 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17709 | 108.46 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17709 | 108.46 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17726 | 107.93 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17726 | 107.93 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17729 | 107.93 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17729 | 108.31 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.6 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.64 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.64 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.65 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.65 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.84 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.91 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.93 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.93 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.93 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.08 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.09 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.1 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.14 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.14 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.24 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.26 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.26 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.31 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.33 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.34 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.34 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.36 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.38 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.38 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.43 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.43 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.47 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.48 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.57 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.58 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.59 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.59 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.6 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.6 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.6 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.61 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.62 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.62 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.65 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.65 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.66 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.67 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.69 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.73 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.78 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.82 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.9 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.9 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.94 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.94 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.96 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.26 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.26 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.26 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.33 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.33 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.38 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 110.13 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 110.7 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 113.2 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17736 | 108.15 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17737 | 108.15 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 108.2 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 108.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 108.27 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17739 | 107.43 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17739 | 107.43 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1774 | 108.34 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1774 | 108.34 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17748 | 108.22 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17752 | 108.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17757 | 108.38 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17757 | 108.38 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 108.64 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17767 | 108.5 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17778 | 108.87 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17778 | 108.87 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1783 | 110.2 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17831 | 110.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17831 | 110.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17841 | 109.88 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17841 | 109.88 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17845 | 109.68 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17845 | 109.73 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17853 | 109.48 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17858 | 110.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 111.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 110.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 110.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17976 | 110.52 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17997 | 112.33 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17999 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17999 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18023 | 111.45 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18023 | 111.45 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18104 | 114.65 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18111 | 114.7 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18127 | 115.03 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18127 | 115.03 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18237 | 115.2 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18285 | 110.28 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18418 | 115.8 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18418 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19039 | 121.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19039 | 121.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19703 | 122.24 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20217 | 139.23 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 132.76 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 135.94 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 136.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 140.37 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 140.41 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2936 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15797 | 100.26 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15797 | 100.26 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15893 | 100.4 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1605 | 100.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1605 | 101.05 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16592 | 105.57 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16592 | 106.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17171 | 106.54 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17618 | 121.34 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 111.55 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 115.7 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 118.48 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 118.89 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 121.6 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 122.33 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 122.37 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 123.4 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 102.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 104.7 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 104.7 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28327 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10263 | 116.16 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10278 | 106.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 104.1 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 107.2 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 111.56 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 112.2 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 116.48 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 117.09 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 117.11 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 118.06 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11545 | 111.48 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09684 | 107.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09684 | 107.29 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06831 | 103.35 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06919 | 104.57 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06923 | 106.59 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06923 | 106.62 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06946 | 103.97 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06946 | 106.9 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06953 | 106.53 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06959 | 103.66 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0696 | 103.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0696 | 104.57 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06976 | 103.29 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06981 | 103.13 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06992 | 103.65 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06992 | 103.65 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06993 | 102.88 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06993 | 103.12 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07 | 102.89 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07006 | 103.45 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07008 | 102.64 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 102.47 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 102.47 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 102.5 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 102.65 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 102.91 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 103.1 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 103.11 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 103.18 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 103.18 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 103.18 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 103.19 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 103.2 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 103.35 | GEN-2023-116_POI_640252_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 103.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 103.44 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 103.51 | P15:230:UMZB:# 2982 #:: DHC IN NE. STEGALL DC CONVERTER STATION AND SHUNT DEVICE:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 103.54 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 103.63 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 103.93 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 103.98 | P23:345:XEL:8P2 KING | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 104 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 104.01 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 104.02 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 104.06 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 104.12 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 104.12 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 104.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 104.3 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 105.07 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 105.12 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 105.13 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 105.2 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 105.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 105.26 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 105.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 105.43 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 105.44 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 105.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 105.53 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 105.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 105.64 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 105.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 105.79 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 105.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 111.13 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07017 | 102.48 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07017 | 105.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07019 | 102.76 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0702 | 102.54 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0702 | 102.66 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07021 | 102.73 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07021 | 102.76 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07022 | 102.91 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07022 | 103.18 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07022 | 103.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07022 | 103.18 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07022 | 103.23 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07023 | 102.54 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07023 | 102.61 | P12:345:AMMO::MAYWOOD:SUBT:77 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07024 | 103.82 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07025 | 102.76 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07028 | 102.79 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07029 | 103.18 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07029 | 103.28 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07031 | 103.23 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07031 | 103.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07032 | 103.58 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07033 | 102.61 | 300143 4VALLEY 138 514830 FITZGRD4 138 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07034 | 103.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07036 | 103.52 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07036 | 103.52 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07036 | 104.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07038 | 102.86 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07038 | 103.04 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0704 | 103.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07047 | 103.02 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07047 | 103.26 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07047 | 104.57 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07048 | 102.79 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07049 | 104.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07052 | 103.74 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07052 | 103.74 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07064 | 103.24 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07074 | 102.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07075 | 103.57 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07088 | 103.37 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07093 | 103.95 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07093 | 103.95 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07095 | 103.75 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07095 | 103.75 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0712 | 103.64 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0713 | 111.11 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07143 | 105.91 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07143 | 105.96 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07153 | 104.88 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07157 | 103.64 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07203 | 104.13 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07203 | 104.13 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07222 | 103.92 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07222 | 103.92 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07227 | 105.73 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07227 | 105.73 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07229 | 103.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07289 | 104.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07289 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07289 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07294 | 105.39 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07301 | 105.24 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07307 | 108.81 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07319 | 108.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07322 | 108.66 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07355 | 106.49 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07355 | 106.62 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07355 | 106.74 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07355 | 108.72 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07756 | 111.24 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07864 | 119.41 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07864 | 119.41 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07864 | 119.41 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07864 | 119.41 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07864 | 119.41 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07914 | 124.17 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07914 | 124.17 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07914 | 124.17 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09081 | 124.55 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09081 | 124.55 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09081 | 124.55 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09429 | 134.94 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09429 | 134.94 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08118 | 104.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08118 | 104.23 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08118 | 104.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08118 | 104.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08118 | 104.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08169 | 109.24 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08169 | 109.24 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08169 | 109.24 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09335 | 109.9 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09335 | 109.9 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09335 | 109.9 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09684 | 121.32 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09684 | 121.32 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.06118 | 114.05 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.06118 | 114.9 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.28139 | 112.47 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35005 | 136.58 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 130.57 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 133.59 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 134.05 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 137.75 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 137.78 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35645 | 108.23 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35645 | 108.23 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35662 | 107.69 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35662 | 107.69 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35664 | 108.08 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35665 | 107.69 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.35 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.38 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.39 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.4 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.4 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.4 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.6 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.69 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.84 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.85 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.86 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.88 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.88 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.02 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.02 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.08 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.1 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.1 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.1 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.12 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.15 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.15 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.19 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.2 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.23 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.34 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.35 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.36 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.36 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.37 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.37 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.37 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.38 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.39 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.39 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.42 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.42 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.43 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.44 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.45 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.5 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.55 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.59 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.67 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.67 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.69 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.69 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.69 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.71 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.71 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.73 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.78 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.78 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.78 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.91 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.91 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.91 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.96 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.97 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.99 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 109.92 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 109.95 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 110.21 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 110.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 112.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35671 | 107.69 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35671 | 107.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35671 | 107.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35671 | 107.91 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35672 | 107.91 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35672 | 108.02 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35672 | 108.03 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35673 | 107.96 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35674 | 108.11 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35674 | 108.11 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35675 | 107.18 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35679 | 107.98 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35683 | 108.21 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35683 | 108.41 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35692 | 108.21 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35692 | 108.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.357 | 108.27 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35706 | 108.64 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35706 | 108.64 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35735 | 110.01 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35736 | 109.29 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35746 | 109.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35746 | 109.68 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35754 | 109.95 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35754 | 109.95 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35755 | 109.91 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3576 | 110.26 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3576 | 110.27 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35768 | 109.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35768 | 109.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35781 | 112.06 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.358 | 110.39 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35808 | 111.18 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35808 | 111.18 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35854 | 111 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35886 | 110.36 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35919 | 115.01 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35967 | 114.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35975 | 114.62 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3599 | 114.95 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3599 | 114.95 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36059 | 115.82 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36059 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36203 | 120.81 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36203 | 121.59 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36709 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36709 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36709 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36725 | 121.87 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.59062 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30506 | 119.03 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 110.17 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 113.79 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 116.43 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 116.82 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 119.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 120.05 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 120.08 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 121.11 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31302 | 100.23 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31364 | 100.18 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31364 | 100.18 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31424 | 100.94 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31424 | 101.06 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31549 | 105.29 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31549 | 105.97 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3199 | 101.8 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3199 | 103.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3199 | 103.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.32004 | 106.21 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.56984 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23155 | 100.95 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33895 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34033 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34169 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34251 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34321 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34333 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34349 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34354 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34354 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34358 | 101.44 | Potential P4 Event - POI 523823_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34465 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34537 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34547 | 104.75 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34551 | 104.09 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34551 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34695 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34698 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3614 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.62977 | 184.51 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.6397 | 183.79 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.64637 | 179.87 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.64637 | 179.92 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.64637 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.64637 | 191.94 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.65511 | 152.61 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31835 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.33158 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.62915 | 184.91 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.63905 | 184.16 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.6457 | 180.34 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.6457 | 180.35 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.6457 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.6457 | 192.34 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.65453 | 153.1 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.28139 | 113.2 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35005 | 139.23 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 132.76 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 135.94 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 136.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 140.37 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 140.41 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35645 | 108.46 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35645 | 108.46 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35662 | 107.93 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35662 | 107.93 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35664 | 108.31 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35665 | 107.93 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.6 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.64 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.64 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.65 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.65 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.84 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.91 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.93 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.93 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.93 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.08 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.09 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.1 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.14 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.14 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.24 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.26 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.26 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.31 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.33 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.34 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.34 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.36 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.38 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.38 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.43 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.43 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.47 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.48 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.57 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.58 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.59 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.59 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.6 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.6 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.6 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.61 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.62 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.62 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.65 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.65 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.66 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.67 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.69 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.73 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.78 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.82 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.9 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.9 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.94 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.94 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.96 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 109 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 109 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 109.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 109.26 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 109.26 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 109.26 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 109.33 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 109.33 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 109.38 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 110.13 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 110.7 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 113.2 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35671 | 108.15 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35672 | 108.15 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35672 | 108.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35672 | 108.27 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35673 | 108.2 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35674 | 108.34 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35674 | 108.34 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35675 | 107.43 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35675 | 107.43 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35679 | 108.22 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35683 | 108.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35683 | 108.64 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35692 | 108.38 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35692 | 108.38 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35698 | 110.28 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.357 | 108.5 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35706 | 108.87 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35706 | 108.87 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35735 | 110.2 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35736 | 109.48 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35746 | 109.88 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35746 | 109.88 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35754 | 110.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35754 | 110.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35755 | 110.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3576 | 110.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3576 | 110.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35768 | 109.68 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35768 | 109.73 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35781 | 112.33 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.358 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.358 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35808 | 111.45 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35808 | 111.45 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35854 | 111.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35886 | 110.52 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35919 | 115.2 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35967 | 114.65 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35975 | 114.7 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3599 | 115.03 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3599 | 115.03 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36059 | 115.8 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36059 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36203 | 121.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36203 | 121.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36709 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36709 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36709 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36725 | 122.24 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.59062 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30506 | 121.34 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 111.55 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 115.7 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 118.48 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 118.89 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 121.6 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 122.33 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 122.37 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 123.4 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31302 | 100.4 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31364 | 100.26 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31364 | 100.26 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31424 | 100.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31424 | 101.05 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31549 | 105.57 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31549 | 106.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3199 | 102.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3199 | 104.7 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3199 | 104.7 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.32004 | 106.54 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.56984 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05045 | 135.01 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05045 | 135.02 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05045 | 135.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05045 | 135.18 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05045 | 128.95 | POI 515800_22 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05045 | 129.04 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05045 | 129.06 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05045 | 129.06 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05045 | 133.67 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05045 | 133.68 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05045 | 133.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05045 | 133.92 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.15565 | 107.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.15565 | 107.29 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12471 | 104.57 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12475 | 106.59 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12476 | 106.62 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12498 | 103.97 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12498 | 106.9 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12505 | 106.53 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12511 | 103.66 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12528 | 103.29 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12533 | 103.13 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12544 | 103.65 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12544 | 103.65 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12545 | 102.88 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12545 | 103.12 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12552 | 102.89 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12559 | 103.45 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1256 | 102.64 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 102.47 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 102.47 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 102.5 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 102.65 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 102.91 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 103.1 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 103.11 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 103.18 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 103.18 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 103.18 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 103.19 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 103.2 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 103.35 | GEN-2023-116_POI_640252_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 103.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 103.44 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 103.51 | P15:230:UMZB:# 2982 #:: DHC IN NE. STEGALL DC CONVERTER STATION AND SHUNT DEVICE:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 103.54 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 103.63 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 103.93 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 103.98 | P23:345:XEL:8P2 KING | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 104 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 104.01 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 104.02 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 104.06 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 104.12 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 104.12 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 104.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 104.3 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 105.07 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 105.12 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 105.13 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 105.2 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 105.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 105.26 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 105.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 105.43 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 105.44 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 105.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 105.53 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 105.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 105.64 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 105.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 105.79 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 105.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 111.13 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12569 | 102.48 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12569 | 105.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1257 | 102.66 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1257 | 102.76 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12571 | 102.54 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12571 | 102.73 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12571 | 102.76 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12571 | 102.91 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12572 | 103.18 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12572 | 103.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12572 | 103.18 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12572 | 103.23 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12573 | 102.54 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12574 | 102.61 | P12:345:AMMO::MAYWOOD:SUBT:77 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12574 | 103.82 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12577 | 102.76 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12577 | 103.18 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12577 | 103.28 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12578 | 102.79 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12578 | 103.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12579 | 103.23 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12579 | 103.58 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1258 | 103.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12582 | 102.86 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12583 | 103.04 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12584 | 102.61 | 300143 4VALLEY 138 514830 FITZGRD4 138 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12584 | 103.26 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12585 | 103.02 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12586 | 103.52 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12586 | 103.52 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12587 | 104.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12588 | 104.57 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12589 | 104.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1259 | 103.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12593 | 103.74 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12593 | 103.74 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12595 | 102.79 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12609 | 103.57 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12614 | 103.37 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12617 | 102.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12619 | 103.75 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12619 | 103.75 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12645 | 103.64 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12646 | 104.88 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12649 | 103.35 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12662 | 103.64 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12694 | 104.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12694 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12694 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12695 | 105.73 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12695 | 105.73 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12697 | 103.95 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12697 | 103.95 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12715 | 103.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12724 | 103.92 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12724 | 103.92 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12725 | 103.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12725 | 104.57 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12729 | 104.13 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12729 | 104.13 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12738 | 111.11 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12749 | 103.24 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12802 | 105.39 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12809 | 105.24 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.13096 | 108.66 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1315 | 106.49 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1315 | 106.62 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1315 | 106.74 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1315 | 108.72 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.13201 | 108.81 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.13211 | 105.96 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.13212 | 105.91 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.13382 | 108.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.13433 | 111.24 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.14028 | 119.41 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.14028 | 119.41 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.14028 | 119.41 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.14028 | 119.41 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.14028 | 119.41 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1506 | 124.55 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1506 | 124.55 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1506 | 124.55 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1531 | 134.94 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1531 | 134.94 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.17115 | 124.17 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.17115 | 124.17 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.17115 | 124.17 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.14283 | 104.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.14283 | 104.23 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.14283 | 104.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.14283 | 104.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.14283 | 104.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.15315 | 109.9 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.15315 | 109.9 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.15315 | 109.9 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.15565 | 121.32 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.15565 | 121.32 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1737 | 109.24 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1737 | 109.24 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1737 | 109.24 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.06958 | 121.87 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07371 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07371 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07371 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0749 | 108.23 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0749 | 108.23 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07508 | 107.69 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07508 | 107.69 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.35 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.38 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.39 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.4 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.4 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.4 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.6 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.69 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.69 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.84 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.85 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.86 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.88 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.88 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.02 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.02 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.08 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.08 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.1 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.1 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.1 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.12 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.15 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.15 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.19 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.2 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.23 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.34 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.35 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.36 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.36 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.37 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.37 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.37 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.38 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.39 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.39 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.42 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.42 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.43 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.44 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.45 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.5 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.55 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.59 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.67 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.67 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.69 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.69 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.69 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.71 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.71 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.73 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.78 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.78 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.78 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.91 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.91 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.91 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.96 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.97 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.99 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 109.92 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 109.95 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 110.21 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 110.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 112.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07516 | 107.69 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07516 | 107.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07516 | 107.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07518 | 107.91 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07519 | 107.91 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0752 | 107.18 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07521 | 107.96 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07521 | 108.02 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07521 | 108.03 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07524 | 108.11 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07524 | 108.11 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07538 | 108.21 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07538 | 108.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0754 | 107.98 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0754 | 108.21 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07553 | 108.27 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07562 | 108.41 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07571 | 108.64 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07571 | 108.64 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07639 | 109.95 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07639 | 109.95 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07655 | 109.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07655 | 109.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07659 | 109.91 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07664 | 109.29 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07691 | 110.01 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07701 | 109.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07701 | 109.68 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07725 | 111 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07776 | 110.36 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07784 | 110.26 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07785 | 110.27 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08016 | 112.06 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08043 | 111.18 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08043 | 111.18 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08063 | 114.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08065 | 114.62 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08083 | 114.95 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08083 | 114.95 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0834 | 110.39 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08363 | 115.82 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08363 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08795 | 115.01 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08855 | 136.58 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08896 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08896 | 130.57 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08896 | 133.59 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08896 | 134.05 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08896 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08896 | 137.75 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08896 | 137.78 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08896 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08954 | 120.81 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08954 | 121.59 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12437 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06064 | 106.21 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06423 | 101.8 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06423 | 103.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06423 | 103.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07044 | 100.18 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07044 | 100.18 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07288 | 100.94 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07288 | 101.06 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07664 | 100.23 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07717 | 119.03 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07753 | 110.17 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07753 | 113.79 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07753 | 116.43 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07753 | 116.82 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07753 | 119.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07753 | 120.05 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07753 | 120.08 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07753 | 121.11 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07803 | 105.29 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07803 | 105.97 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.08713 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09386 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09776 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09883 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10194 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10484 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10664 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10668 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10684 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10689 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10693 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10699 | 101.44 | Potential P4 Event - POI 523823_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11026 | 104.75 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11035 | 104.09 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11035 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11119 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11682 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12041 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16572 | 152.61 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18773 | 183.79 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18846 | 179.87 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18846 | 179.92 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18846 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18846 | 191.94 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19367 | 184.51 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.07994 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.11048 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.16557 | 153.1 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.18754 | 184.16 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.18827 | 180.34 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.18827 | 180.35 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.18827 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.18827 | 192.34 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.19349 | 184.91 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.06958 | 122.24 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07371 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07371 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07371 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0749 | 108.46 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0749 | 108.46 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07508 | 107.93 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07508 | 107.93 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.6 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.64 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.64 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.65 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.65 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.84 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.91 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.93 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.93 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.93 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.93 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.08 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.09 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.1 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.14 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.14 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.24 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.26 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.26 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.31 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.31 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.33 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.34 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.34 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.36 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.38 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.38 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.43 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.43 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.47 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.48 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.57 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.58 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.59 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.59 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.6 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.6 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.6 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.61 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.62 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.62 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.65 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.65 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.66 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.67 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.69 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.73 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.78 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.82 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.9 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.9 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.94 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.94 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.96 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 109 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 109 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 109.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 109.26 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 109.26 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 109.26 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 109.33 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 109.33 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 109.38 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 110.13 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 110.7 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 113.2 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07518 | 108.15 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07519 | 108.15 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0752 | 107.43 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0752 | 107.43 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07521 | 108.2 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07521 | 108.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07521 | 108.27 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07524 | 108.34 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07524 | 108.34 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07538 | 108.38 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07538 | 108.38 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0754 | 108.22 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0754 | 108.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07553 | 108.5 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07562 | 108.64 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07571 | 108.87 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07571 | 108.87 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07585 | 110.28 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07639 | 110.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07639 | 110.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07655 | 109.68 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07655 | 109.73 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07659 | 110.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07664 | 109.48 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07691 | 110.2 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07701 | 109.88 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07701 | 109.88 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07725 | 111.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07776 | 110.52 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07784 | 110.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07785 | 110.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08016 | 112.33 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08043 | 111.45 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08043 | 111.45 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08063 | 114.65 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08065 | 114.7 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08083 | 115.03 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08083 | 115.03 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0834 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0834 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08363 | 115.8 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08363 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08795 | 115.2 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08855 | 139.23 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08896 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08896 | 132.76 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08896 | 135.94 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08896 | 136.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08896 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08896 | 140.37 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08896 | 140.41 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08896 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08954 | 121.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08954 | 121.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12437 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06064 | 106.54 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06423 | 102.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06423 | 104.7 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06423 | 104.7 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07044 | 100.26 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07044 | 100.26 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07288 | 100.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07288 | 101.05 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07664 | 100.4 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07717 | 121.34 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07753 | 111.55 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07753 | 115.7 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07753 | 118.48 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07753 | 118.89 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07753 | 121.6 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07753 | 122.33 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07753 | 122.37 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07753 | 123.4 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07803 | 105.57 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07803 | 106.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1153 | 107.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1153 | 107.29 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0854 | 104.57 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08544 | 106.59 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08545 | 106.62 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08567 | 103.97 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08568 | 106.9 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08575 | 106.53 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08581 | 103.66 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 103.29 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08603 | 103.13 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08614 | 103.65 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08614 | 103.65 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08615 | 102.88 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08615 | 103.12 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08621 | 102.89 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08628 | 103.45 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0863 | 102.64 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.47 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.47 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.48 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.5 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.65 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.91 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.1 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.11 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.18 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.18 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.18 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.19 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.2 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.35 | GEN-2023-116_POI_640252_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.44 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.51 | P15:230:UMZB:# 2982 #:: DHC IN NE. STEGALL DC CONVERTER STATION AND SHUNT DEVICE:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.54 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.63 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.93 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.98 | P23:345:XEL:8P2 KING | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.01 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.02 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.06 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.12 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.12 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.3 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.07 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.12 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.13 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.2 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.26 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.43 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.44 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.53 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.64 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.79 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 111.13 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0864 | 102.76 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08641 | 102.54 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08641 | 102.66 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08642 | 102.73 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08642 | 102.76 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08643 | 102.91 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08643 | 103.18 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08643 | 103.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08643 | 103.18 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08643 | 103.23 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08644 | 102.54 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08644 | 102.61 | P12:345:AMMO::MAYWOOD:SUBT:77 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08645 | 103.82 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 102.76 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 102.79 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 103.18 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 103.28 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08651 | 103.23 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08651 | 103.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08651 | 103.58 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08653 | 103.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08655 | 102.61 | 300143 4VALLEY 138 514830 FITZGRD4 138 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08656 | 102.86 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08657 | 103.04 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08657 | 103.52 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08657 | 103.52 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08658 | 104.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08661 | 103.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08662 | 103.26 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08663 | 103.02 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08664 | 104.57 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08666 | 104.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08668 | 102.79 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08669 | 103.74 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08669 | 103.74 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0869 | 103.57 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08692 | 102.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.087 | 103.37 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08706 | 103.75 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08706 | 103.75 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08734 | 103.64 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08738 | 103.24 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08749 | 103.95 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08749 | 103.95 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08753 | 104.88 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08758 | 103.64 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08768 | 111.11 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08816 | 104.13 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08816 | 104.13 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0882 | 105.73 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0882 | 105.73 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08822 | 103.92 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08822 | 103.92 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08822 | 103.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08841 | 104.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08841 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08841 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08892 | 105.91 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08892 | 105.96 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08902 | 105.39 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0891 | 105.24 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08929 | 103.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08929 | 104.57 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08973 | 103.35 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09008 | 108.66 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09048 | 106.49 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09048 | 106.62 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09048 | 106.74 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09048 | 108.72 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09148 | 108.81 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09376 | 108.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09455 | 111.24 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09664 | 119.41 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09664 | 119.41 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09664 | 119.41 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09664 | 119.41 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09664 | 119.41 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10434 | 124.17 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10434 | 124.17 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10434 | 124.17 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10946 | 124.55 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10946 | 124.55 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10946 | 124.55 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11275 | 134.94 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11275 | 134.94 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09919 | 104.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09919 | 104.23 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09919 | 104.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09919 | 104.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09919 | 104.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10689 | 109.24 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10689 | 109.24 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10689 | 109.24 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11201 | 109.9 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11201 | 109.9 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11201 | 109.9 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1153 | 121.32 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1153 | 121.32 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13 | 111.5 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13888 | 102.83 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13888 | 102.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13888 | 102.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13915 | 103.68 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13915 | 103.68 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.1395 | 104.16 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17344 | 114.4 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17719 | 107.58 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18762 | 107.83 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18762 | 108.41 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18762 | 108.41 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18788 | 109.17 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18788 | 109.17 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18824 | 109.67 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.11 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.11 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.11 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.12 | ASGI-2011-004_POI_525915_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.17 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.33 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.59 | GEN-2011-025_POI_525803_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.64 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 101.04 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 101.04 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 101.04 | GEN-2023-086_POI_773700_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 103.21 | 774381 GEN-2023-120 115 774382 G23-120XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 103.21 | GEN-2023-120_POI_525192_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 105.36 | 524757 BETHEL_COL 3 115 524755 BETHEL_COL11 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 106.65 | GEN-2014-040_POI_524746_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07656 | 100.11 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07656 | 100.11 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0766 | 100.13 | 515375 WWRDEHV7 345 516059 BECKHAM7 345 2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07661 | 100.84 | Potential P4 Event - POI 776000_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07662 | 100.19 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07662 | 100.25 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07662 | 100.29 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07662 | 100.29 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07662 | 100.31 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07663 | 100.19 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07665 | 100.32 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07665 | 100.32 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07678 | 100.67 | POI 515800_22 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07678 | 100.69 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07682 | 102.94 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07725 | 101.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07725 | 102.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 103.85 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 104.28 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 105.13 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 105.26 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07843 | 102.17 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07935 | 103.83 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08031 | 105.78 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08139 | 118.93 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09004 | 115.77 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09004 | 116.09 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 116.35 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 116.35 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09015 | 116.49 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09265 | 117.56 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09265 | 120.95 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.10347 | 127.17 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.66 | 524757 BETHEL_COL 3 115 524756 BETHEL_COL21 34.5 2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 101.52 | 774381 GEN-2023-120 115 774382 G23-120XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 101.52 | GEN-2023-120_POI_525192_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 103.4 | 524757 BETHEL_COL 3 115 524755 BETHEL_COL11 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 105.44 | GEN-2014-040_POI_524746_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07682 | 101.12 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07725 | 100.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07725 | 100.64 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 102.3 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 102.76 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 103.7 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 103.84 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07935 | 102.14 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08031 | 104.12 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08139 | 118.92 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09004 | 114.41 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09004 | 114.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 115.06 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 115.06 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09015 | 115.22 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09265 | 115.67 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09265 | 119.13 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.10347 | 125.32 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.11102 | 138.46 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1502 | 134.22 | 560022 CRAWFISH_DR 345 774180 G23-110-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15121 | 134.27 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15121 | 134.32 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15122 | 134.67 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.02 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.07 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.08 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.08 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.09 | P23:345:XEL:8N17 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.09 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.1 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.62 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.65 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.65 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.67 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.7 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.7 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.71 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.71 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.74 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.74 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.75 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.77 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.8 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.81 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.87 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.88 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.88 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.88 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.89 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.89 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.9 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.91 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.91 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.91 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.93 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.93 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.94 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.95 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.03 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.05 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.11 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.11 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.12 | P11:21:EES:RVB:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.12 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.12 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.14 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.14 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.17 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.19 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.19 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.19 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.44 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.44 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.5 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.67 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.67 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.67 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 136.51 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 138.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15125 | 134.33 | 539784 ENSNGW 3 115 3WXFMR ENSIGN WIND 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.35 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.36 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.36 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.36 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.58 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.58 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15127 | 134.62 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15127 | 134.68 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15127 | 134.68 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15128 | 133.94 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15128 | 134.74 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15128 | 134.74 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15132 | 134.64 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15135 | 134.82 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15136 | 134.89 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15138 | 134.81 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15138 | 134.81 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15138 | 134.81 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15138 | 134.81 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15142 | 134.86 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15149 | 135.18 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15149 | 135.18 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15175 | 136.3 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15176 | 136.26 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15176 | 136.26 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15181 | 136.03 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15181 | 136.03 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15184 | 135.85 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15184 | 135.9 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1519 | 136.2 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15191 | 135.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15216 | 136.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15225 | 136.42 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15225 | 136.42 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15237 | 137.2 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15258 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15259 | 136.64 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15259 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15321 | 140.07 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15324 | 140.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15333 | 140.41 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15333 | 140.41 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15386 | 140.35 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15504 | 141.43 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15504 | 141.57 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15736 | 138.37 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15747 | 138.2 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15801 | 138.53 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15893 | 146.73 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15893 | 147.76 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16243 | 142.55 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 150.42 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 154 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 156.76 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 157.19 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 159.91 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 161.9 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16762 | 148.33 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17038 | 159.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1998 | 162.73 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1998 | 164.74 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1998 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19991 | 165.01 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19991 | 165.01 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20014 | 165.4 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.2073 | 114.05 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.2073 | 114.9 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10203 | 112.47 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17709 | 108.23 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17709 | 108.23 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17726 | 107.69 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17726 | 107.69 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17729 | 107.69 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17729 | 108.08 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.35 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.38 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.39 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.4 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.4 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.4 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.6 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.69 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.84 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.85 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.86 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.88 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.88 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.02 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.02 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.08 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.1 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.1 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.1 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.12 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.15 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.15 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.19 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.2 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.23 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.34 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.35 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.36 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.36 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.37 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.37 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.37 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.38 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.39 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.39 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.42 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.42 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.43 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.44 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.45 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.5 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.55 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.59 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.67 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.67 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.69 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.69 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.69 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.71 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.71 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.73 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.78 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.78 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.78 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.91 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.91 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.91 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.96 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.97 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.99 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.92 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.95 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 110.21 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 110.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 112.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17735 | 107.69 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17735 | 107.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17735 | 107.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17736 | 107.91 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17737 | 107.91 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 107.96 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 108.02 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 108.03 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17739 | 107.18 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1774 | 108.11 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1774 | 108.11 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17748 | 107.98 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17752 | 108.21 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17757 | 108.21 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17757 | 108.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 108.41 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17767 | 108.27 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17778 | 108.64 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17778 | 108.64 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1783 | 110.01 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17831 | 109.95 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17831 | 109.95 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17841 | 109.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17841 | 109.68 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17845 | 109.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17845 | 109.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17853 | 109.29 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17858 | 109.91 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 111 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 110.26 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 110.27 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17976 | 110.36 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17997 | 112.06 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17999 | 110.39 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18023 | 111.18 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18023 | 111.18 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18104 | 114.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18111 | 114.62 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18127 | 114.95 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18127 | 114.95 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18237 | 115.01 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18418 | 115.82 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18418 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19039 | 120.81 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19039 | 121.59 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19703 | 121.87 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20217 | 136.58 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 130.57 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 133.59 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 134.05 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 137.75 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 137.78 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2936 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15797 | 100.18 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15797 | 100.18 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15893 | 100.23 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1605 | 100.94 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1605 | 101.06 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16592 | 105.29 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16592 | 105.97 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17171 | 106.21 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17618 | 119.03 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 110.17 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 113.79 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 116.43 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 116.82 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 119.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 120.05 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 120.08 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 121.11 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 101.8 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 103.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 103.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28327 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1132 | 100.95 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2206 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22083 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2236 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22378 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22589 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.226 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22616 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22621 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22622 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22626 | 101.44 | Potential P4 Event - POI 523823_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22771 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22855 | 104.75 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22861 | 104.09 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22861 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23058 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24019 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24771 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26243 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37835 | 152.61 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41566 | 184.51 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41702 | 183.79 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 179.87 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 179.92 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 191.94 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22037 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24078 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37802 | 153.1 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41526 | 184.91 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4166 | 184.16 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 180.34 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 180.35 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 192.34 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10203 | 113.2 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17709 | 108.46 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17709 | 108.46 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17726 | 107.93 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17726 | 107.93 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17729 | 107.93 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17729 | 108.31 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.6 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.64 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.64 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.65 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.65 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.84 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.91 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.93 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.93 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.93 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.08 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.09 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.1 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.14 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.14 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.24 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.26 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.26 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.31 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.33 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.34 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.34 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.36 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.38 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.38 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.43 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.43 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.47 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.48 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.57 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.58 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.59 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.59 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.6 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.6 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.6 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.61 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.62 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.62 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.65 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.65 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.66 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.67 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.69 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.73 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.78 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.82 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.9 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.9 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.94 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.94 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.96 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.26 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.26 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.26 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.33 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.33 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.38 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 110.13 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 110.7 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 113.2 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17736 | 108.15 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17737 | 108.15 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 108.2 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 108.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 108.27 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17739 | 107.43 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17739 | 107.43 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1774 | 108.34 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1774 | 108.34 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17748 | 108.22 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17752 | 108.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17757 | 108.38 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17757 | 108.38 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 108.64 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17767 | 108.5 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17778 | 108.87 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17778 | 108.87 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1783 | 110.2 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17831 | 110.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17831 | 110.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17841 | 109.88 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17841 | 109.88 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17845 | 109.68 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17845 | 109.73 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17853 | 109.48 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17858 | 110.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 111.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 110.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 110.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17976 | 110.52 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17997 | 112.33 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17999 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17999 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18023 | 111.45 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18023 | 111.45 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18104 | 114.65 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18111 | 114.7 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18127 | 115.03 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18127 | 115.03 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18237 | 115.2 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18285 | 110.28 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18418 | 115.8 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18418 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19039 | 121.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19039 | 121.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19703 | 122.24 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20217 | 139.23 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 132.76 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 135.94 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 136.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 140.37 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 140.41 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2936 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15797 | 100.26 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15797 | 100.26 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15893 | 100.4 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1605 | 100.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1605 | 101.05 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16592 | 105.57 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16592 | 106.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17171 | 106.54 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17618 | 121.34 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 111.55 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 115.7 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 118.48 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 118.89 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 121.6 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 122.33 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 122.37 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 123.4 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 102.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 104.7 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 104.7 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28327 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10263 | 116.16 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10278 | 106.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 104.1 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 107.2 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 111.56 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 112.2 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 116.48 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 117.09 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 117.11 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 118.06 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11545 | 111.48 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05018 | 138.19 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05018 | 130.1 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05018 | 137.17 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12133 | 107.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12133 | 107.29 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09043 | 104.57 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09047 | 106.59 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09048 | 106.62 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0907 | 103.97 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0907 | 106.9 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09077 | 106.53 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09083 | 103.66 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.091 | 103.29 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09105 | 103.13 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09116 | 103.65 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09116 | 103.65 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09117 | 102.88 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09117 | 103.12 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09124 | 102.89 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09131 | 103.45 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09132 | 102.64 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 102.47 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 102.47 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 102.5 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 102.65 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 102.91 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 103.1 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 103.11 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 103.18 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 103.18 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 103.18 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 103.19 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 103.2 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 103.35 | GEN-2023-116_POI_640252_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 103.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 103.44 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 103.51 | P15:230:UMZB:# 2982 #:: DHC IN NE. STEGALL DC CONVERTER STATION AND SHUNT DEVICE:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 103.54 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 103.63 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 103.93 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 103.98 | P23:345:XEL:8P2 KING | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 104 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 104.01 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 104.02 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 104.06 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 104.12 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 104.12 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 104.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 104.3 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 105.07 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 105.12 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 105.13 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 105.2 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 105.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 105.26 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 105.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 105.43 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 105.44 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 105.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 105.53 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 105.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 105.64 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 105.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 105.79 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 105.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 111.13 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09141 | 102.48 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09141 | 105.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09143 | 102.66 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09143 | 102.76 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09144 | 102.54 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09144 | 102.73 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09144 | 102.76 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09145 | 102.91 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09145 | 103.18 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09145 | 103.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09145 | 103.18 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09145 | 103.23 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09146 | 102.54 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09146 | 102.61 | P12:345:AMMO::MAYWOOD:SUBT:77 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09147 | 103.82 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09149 | 102.76 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09151 | 102.79 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09151 | 103.18 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09151 | 103.28 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09152 | 103.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09153 | 103.23 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09153 | 103.58 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09155 | 103.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09157 | 102.61 | 300143 4VALLEY 138 514830 FITZGRD4 138 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09158 | 102.86 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09158 | 103.04 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09159 | 103.52 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09159 | 103.52 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0916 | 104.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09162 | 103.26 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09163 | 103.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09164 | 103.02 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09165 | 104.57 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09167 | 104.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0917 | 102.79 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0917 | 103.74 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0917 | 103.74 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0919 | 103.57 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09194 | 102.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09199 | 103.37 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09205 | 103.75 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09205 | 103.75 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09206 | 103.24 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09234 | 103.64 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09248 | 104.88 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09252 | 103.64 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09262 | 103.95 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09262 | 103.95 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09275 | 111.11 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09297 | 103.35 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09312 | 105.73 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09312 | 105.73 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09314 | 103.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09316 | 104.13 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09316 | 104.13 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09317 | 103.92 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09317 | 103.92 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09318 | 104.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09318 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09318 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.094 | 105.39 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09408 | 105.24 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09428 | 105.91 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09428 | 105.96 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0953 | 108.66 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09572 | 106.49 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09572 | 106.62 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09572 | 106.74 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09572 | 108.72 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09635 | 103.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09635 | 104.57 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09749 | 108.81 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09991 | 111.24 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10139 | 108.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10222 | 119.41 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10222 | 119.41 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10222 | 119.41 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10222 | 119.41 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10222 | 119.41 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11174 | 124.17 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11174 | 124.17 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11174 | 124.17 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11555 | 124.55 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11555 | 124.55 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11555 | 124.55 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11878 | 134.94 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11878 | 134.94 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10476 | 104.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10476 | 104.23 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10476 | 104.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10476 | 104.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10476 | 104.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11429 | 109.24 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11429 | 109.24 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11429 | 109.24 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1181 | 109.9 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1181 | 109.9 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1181 | 109.9 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12133 | 121.32 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12133 | 121.32 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.06064 | 111.5 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.07984 | 114.4 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06648 | 138.53 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06682 | 138.2 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06842 | 142.55 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07067 | 134.22 | 560022 CRAWFISH_DR 345 774180 G23-110-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07072 | 134.27 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07072 | 134.32 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.02 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.07 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.08 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.08 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.09 | P23:345:XEL:8N17 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.09 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.1 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.62 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.65 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.65 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.67 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.67 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.7 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.7 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.71 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.71 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.74 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.74 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.75 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.77 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.8 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.81 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.87 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.88 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.88 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.88 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.89 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.89 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.9 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.91 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.91 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.91 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.93 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.93 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.94 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.95 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 135 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 135.03 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 135.05 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 135.11 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 135.11 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 135.12 | P11:21:EES:RVB:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 135.12 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 135.12 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 135.14 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 135.14 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 135.17 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 135.19 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 135.19 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 135.19 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 135.44 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 135.44 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 135.5 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 135.67 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 135.67 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 135.67 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 136.51 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 138.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07076 | 134.33 | 539784 ENSNGW 3 115 3WXFMR ENSIGN WIND 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07076 | 134.35 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07077 | 134.36 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07077 | 134.36 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07077 | 134.36 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07077 | 134.58 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07077 | 134.58 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07078 | 133.94 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07078 | 134.62 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07078 | 134.68 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07078 | 134.68 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07079 | 134.74 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07079 | 134.74 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07083 | 134.64 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07085 | 134.89 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07086 | 134.82 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07089 | 134.81 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07089 | 134.81 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07089 | 134.81 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07089 | 134.81 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07094 | 134.86 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07101 | 135.18 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07101 | 135.18 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07129 | 136.26 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07129 | 136.26 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07131 | 136.3 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07131 | 136.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07136 | 136.03 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07136 | 136.03 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07137 | 135.85 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07137 | 135.9 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07141 | 136.42 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07141 | 136.42 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07147 | 136.2 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07155 | 135.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07174 | 138.37 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07192 | 137.2 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07216 | 136.64 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07253 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07253 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07283 | 140.07 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07287 | 140.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07295 | 140.41 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07295 | 140.41 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07372 | 140.35 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07528 | 141.43 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07528 | 141.57 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08115 | 146.73 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08115 | 147.76 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08196 | 148.33 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09386 | 150.42 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09386 | 154 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09386 | 156.76 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09386 | 157.19 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09386 | 159.91 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09386 | 161.9 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.10945 | 159.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07306 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07306 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07306 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09393 | 110.39 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09497 | 108.23 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09497 | 108.23 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09515 | 107.69 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09515 | 107.69 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09517 | 107.69 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09517 | 108.08 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.35 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.38 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.39 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.4 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.4 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.4 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.6 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.69 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.84 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.85 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.86 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.88 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.88 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.02 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.02 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.08 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.1 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.1 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.1 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.12 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.15 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.15 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.19 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.2 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.23 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.34 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.35 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.36 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.36 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.37 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.37 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.37 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.38 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.39 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.39 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.42 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.42 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.43 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.44 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.45 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.5 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.55 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.59 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.67 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.67 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.69 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.69 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.69 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.71 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.71 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.73 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.78 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.78 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.78 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.91 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.91 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.91 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.96 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.97 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.99 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 109.92 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 109.95 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 110.21 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 110.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 112.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09523 | 107.69 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09523 | 107.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09523 | 107.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09525 | 107.91 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09525 | 107.91 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09527 | 107.18 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09527 | 107.96 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09527 | 108.02 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09527 | 108.03 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09528 | 108.11 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09528 | 108.11 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09537 | 107.98 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09542 | 108.21 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09546 | 108.21 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09546 | 108.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09547 | 108.41 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09556 | 108.27 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0957 | 108.64 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0957 | 108.64 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09623 | 109.95 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09623 | 109.95 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09628 | 110.01 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09638 | 109.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09638 | 109.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09638 | 109.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09638 | 109.68 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09659 | 109.91 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09665 | 109.29 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09685 | 112.06 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09711 | 111.18 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09711 | 111.18 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09732 | 111 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09775 | 110.36 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09829 | 110.26 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0983 | 110.27 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09914 | 114.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09921 | 114.62 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09937 | 114.95 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09937 | 114.95 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10092 | 115.01 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10339 | 115.82 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10339 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1129 | 120.81 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1129 | 121.59 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13507 | 121.87 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13841 | 136.58 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13906 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13906 | 130.57 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13906 | 133.59 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13906 | 134.05 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13906 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13906 | 137.75 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13906 | 137.78 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13906 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15762 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06367 | 101.8 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06367 | 103.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06367 | 103.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0866 | 100.18 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0866 | 100.18 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08795 | 100.23 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0901 | 100.94 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0901 | 101.06 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09839 | 105.29 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09839 | 105.97 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11771 | 106.21 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12062 | 119.03 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12119 | 110.17 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12119 | 113.79 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12119 | 116.43 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12119 | 116.82 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12119 | 119.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12119 | 120.05 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12119 | 120.08 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12119 | 121.11 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15207 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.06632 | 100.95 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15056 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15675 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17372 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17571 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17683 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17933 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17943 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17959 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17964 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17965 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1797 | 101.44 | Potential P4 Event - POI 523823_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18177 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18211 | 104.75 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18217 | 104.09 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18217 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18563 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20021 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25825 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25903 | 152.61 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.32883 | 183.79 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33104 | 184.51 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33128 | 179.87 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33128 | 179.92 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33128 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33128 | 191.94 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.18369 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23694 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2588 | 153.1 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.32849 | 184.16 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.33071 | 184.91 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.33093 | 180.34 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.33093 | 180.35 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.33093 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.33093 | 192.34 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07306 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07306 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07306 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09393 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09393 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09404 | 110.28 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09497 | 108.46 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09497 | 108.46 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09515 | 107.93 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09515 | 107.93 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09517 | 107.93 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09517 | 108.31 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.6 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.64 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.64 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.65 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.65 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.84 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.91 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.93 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.93 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.93 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.08 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.09 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.1 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.14 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.14 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.24 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.26 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.26 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.31 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.33 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.34 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.34 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.36 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.38 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.38 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.43 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.43 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.47 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.48 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.57 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.58 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.59 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.59 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.6 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.6 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.6 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.61 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.62 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.62 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.65 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.65 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.66 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.67 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.69 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.73 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.78 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.82 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.9 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.9 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.94 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.94 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.96 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 109 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 109 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 109.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 109.26 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 109.26 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 109.26 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 109.33 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 109.33 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 109.38 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 110.13 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 110.7 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 113.2 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09525 | 108.15 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09525 | 108.15 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09527 | 107.43 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09527 | 107.43 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09527 | 108.2 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09527 | 108.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09527 | 108.27 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09528 | 108.34 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09528 | 108.34 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09537 | 108.22 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09542 | 108.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09546 | 108.38 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09546 | 108.38 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09547 | 108.64 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09556 | 108.5 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0957 | 108.87 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0957 | 108.87 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09623 | 110.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09623 | 110.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09628 | 110.2 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09638 | 109.68 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09638 | 109.73 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09638 | 109.88 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09638 | 109.88 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09659 | 110.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09665 | 109.48 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09685 | 112.33 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09711 | 111.45 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09711 | 111.45 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09732 | 111.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09775 | 110.52 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09829 | 110.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0983 | 110.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09914 | 114.65 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09921 | 114.7 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09937 | 115.03 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09937 | 115.03 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10092 | 115.2 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10339 | 115.8 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10339 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1129 | 121.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1129 | 121.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13507 | 122.24 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13841 | 139.23 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13906 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13906 | 132.76 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13906 | 135.94 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13906 | 136.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13906 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13906 | 140.37 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13906 | 140.41 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13906 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15762 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06367 | 102.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06367 | 104.7 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06367 | 104.7 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0866 | 100.26 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0866 | 100.26 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08795 | 100.4 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0901 | 100.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0901 | 101.05 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09839 | 105.57 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09839 | 106.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11771 | 106.54 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12062 | 121.34 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12119 | 111.55 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12119 | 115.7 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12119 | 118.48 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12119 | 118.89 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12119 | 121.6 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12119 | 122.33 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12119 | 122.37 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12119 | 123.4 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15207 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.07282 | 111.48 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08692 | 116.16 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08719 | 104.1 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08719 | 107.2 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08719 | 111.56 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08719 | 112.2 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08719 | 116.48 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08719 | 117.09 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08719 | 117.11 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08719 | 118.06 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09195 | 106.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05207 | 135.01 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05207 | 135.02 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05207 | 135.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05207 | 135.18 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05296 | 138.19 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05207 | 128.95 | POI 515800_22 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05207 | 129.04 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05207 | 129.06 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05207 | 129.06 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05296 | 130.1 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05207 | 133.67 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05207 | 133.68 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05207 | 133.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05207 | 133.92 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05296 | 137.17 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12837 | 107.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12837 | 107.29 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0973 | 104.57 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09734 | 106.59 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09735 | 106.62 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09757 | 103.97 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09758 | 106.9 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09765 | 106.53 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09771 | 103.66 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09787 | 103.29 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09792 | 103.13 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09804 | 103.65 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09804 | 103.65 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09805 | 102.88 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09805 | 103.12 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09811 | 102.89 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09818 | 103.45 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09819 | 102.64 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 102.47 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 102.47 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 102.5 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 102.65 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 102.91 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 103.1 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 103.11 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 103.18 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 103.18 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 103.18 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 103.19 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 103.2 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 103.35 | GEN-2023-116_POI_640252_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 103.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 103.44 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 103.51 | P15:230:UMZB:# 2982 #:: DHC IN NE. STEGALL DC CONVERTER STATION AND SHUNT DEVICE:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 103.54 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 103.63 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 103.93 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 103.98 | P23:345:XEL:8P2 KING | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 104 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 104.01 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 104.02 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 104.06 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 104.12 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 104.12 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 104.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 104.3 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 105.2 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 105.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 105.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 105.43 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 105.44 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 105.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 105.53 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 105.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 105.64 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 105.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 105.79 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 105.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 111.13 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09828 | 102.48 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09828 | 105.07 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09828 | 105.12 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09828 | 105.13 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09828 | 105.26 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09828 | 105.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0983 | 102.66 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0983 | 102.76 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09831 | 102.54 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09831 | 102.73 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09831 | 102.76 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09832 | 102.91 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09832 | 103.18 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09832 | 103.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09832 | 103.18 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09832 | 103.23 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09833 | 102.54 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09833 | 102.61 | P12:345:AMMO::MAYWOOD:SUBT:77 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09834 | 103.82 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09837 | 102.76 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09838 | 102.79 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09838 | 103.18 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09838 | 103.28 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09839 | 103.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0984 | 103.23 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0984 | 103.58 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09842 | 103.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09844 | 102.61 | 300143 4VALLEY 138 514830 FITZGRD4 138 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09844 | 102.86 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09845 | 103.04 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09846 | 103.52 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09846 | 103.52 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09847 | 104.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09848 | 103.26 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0985 | 103.02 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0985 | 103.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09851 | 104.57 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09853 | 104.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09856 | 102.79 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09856 | 103.74 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09856 | 103.74 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09876 | 103.57 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0988 | 102.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09883 | 103.37 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09889 | 103.75 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09889 | 103.75 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09918 | 103.64 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09929 | 104.88 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09934 | 103.64 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09936 | 103.35 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09962 | 103.95 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09962 | 103.95 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09969 | 111.11 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09989 | 104.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09989 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09989 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0999 | 105.73 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0999 | 105.73 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09994 | 103.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09999 | 103.92 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09999 | 103.92 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10001 | 104.13 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10001 | 104.13 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10006 | 103.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10006 | 104.57 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1002 | 103.24 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10082 | 105.39 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1009 | 105.24 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10183 | 105.96 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10184 | 105.91 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10245 | 108.66 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1029 | 106.49 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1029 | 106.62 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1029 | 106.74 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1029 | 108.72 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10452 | 108.81 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10686 | 111.24 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10714 | 108.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10985 | 119.41 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10985 | 119.41 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10985 | 119.41 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10985 | 119.41 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10985 | 119.41 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12269 | 124.55 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12269 | 124.55 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12269 | 124.55 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12346 | 124.17 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12346 | 124.17 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12346 | 124.17 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12583 | 134.94 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12583 | 134.94 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1124 | 104.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1124 | 104.23 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1124 | 104.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1124 | 104.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1124 | 104.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12524 | 109.9 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12524 | 109.9 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12524 | 109.9 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12601 | 109.24 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12601 | 109.24 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12601 | 109.24 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12837 | 121.32 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12837 | 121.32 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05008 | 137.2 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05033 | 136.64 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05059 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0506 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05076 | 136.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05085 | 136.42 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05085 | 136.42 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05115 | 140.07 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05118 | 140.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05127 | 140.41 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05127 | 140.41 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05203 | 142.55 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05258 | 140.35 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05355 | 141.43 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05355 | 141.57 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05414 | 148.33 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05632 | 165.4 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05637 | 165.01 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05637 | 165.01 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0564 | 162.73 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0564 | 164.74 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0564 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05722 | 150.42 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05722 | 154 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05722 | 156.76 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05722 | 157.19 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05722 | 159.91 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05722 | 161.9 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05813 | 146.73 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05813 | 147.76 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12334 | 121.87 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12357 | 108.23 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12357 | 108.23 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12375 | 107.69 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12375 | 107.69 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12377 | 107.69 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12377 | 108.08 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.35 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.38 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.39 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.4 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.4 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.4 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.6 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.69 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.84 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.85 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.86 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.88 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.88 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.02 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.02 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.08 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.1 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.1 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.1 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.12 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.15 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.15 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.19 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.2 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.23 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.34 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.35 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.36 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.36 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.37 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.37 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.37 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.38 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.39 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.39 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.42 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.42 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.43 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.44 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.45 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.5 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.55 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.59 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.67 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.67 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.69 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.69 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.69 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.71 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.71 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.73 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.78 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.78 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.78 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.91 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.91 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.91 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.96 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.97 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.99 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 109.92 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 109.95 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 110.21 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 110.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 112.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12383 | 107.69 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12383 | 107.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12383 | 107.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12385 | 107.91 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12385 | 107.91 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12387 | 107.18 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12387 | 107.96 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12388 | 108.02 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12388 | 108.03 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12389 | 108.11 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12389 | 108.11 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12399 | 107.98 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12403 | 108.21 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12407 | 108.21 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12407 | 108.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12417 | 108.27 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1243 | 108.41 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12432 | 108.64 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12432 | 108.64 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12488 | 109.95 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12488 | 109.95 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12502 | 110.01 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12503 | 109.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12503 | 109.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12512 | 109.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12512 | 109.68 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12529 | 109.29 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12534 | 109.91 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12593 | 111 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12638 | 110.36 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12674 | 110.26 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12675 | 110.27 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12806 | 114.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12812 | 114.62 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12828 | 114.95 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12828 | 114.95 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12916 | 112.06 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12925 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12925 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12925 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12943 | 111.18 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12943 | 111.18 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13089 | 115.01 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1322 | 115.82 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1322 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13464 | 110.39 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13895 | 136.58 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1395 | 120.81 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1395 | 121.59 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1396 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1396 | 130.57 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1396 | 133.59 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1396 | 134.05 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1396 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1396 | 137.75 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1396 | 137.78 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1396 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20498 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10749 | 106.21 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11179 | 100.18 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11179 | 100.18 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11263 | 101.8 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11263 | 103.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11263 | 103.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11407 | 100.23 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11521 | 100.94 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11521 | 101.06 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12109 | 119.03 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12157 | 105.29 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12157 | 105.97 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12165 | 110.17 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12165 | 113.79 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12165 | 116.43 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12165 | 116.82 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12165 | 119.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12165 | 120.05 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12165 | 120.08 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12165 | 121.11 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19777 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14627 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14902 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14994 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15307 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15414 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.156 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15608 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15624 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15629 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15631 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15635 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15636 | 101.44 | Potential P4 Event - POI 523823_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15895 | 104.75 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15901 | 104.09 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15901 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15991 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16216 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17345 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26003 | 152.61 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28405 | 183.79 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28594 | 179.87 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28594 | 179.92 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28594 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28594 | 191.94 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28758 | 184.51 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.13672 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.15914 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2598 | 153.1 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.28377 | 184.16 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.28564 | 180.34 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.28564 | 180.35 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.28564 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.28564 | 192.34 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2873 | 184.91 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12334 | 122.24 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12357 | 108.46 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12357 | 108.46 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12375 | 107.93 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12375 | 107.93 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12377 | 107.93 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12377 | 108.31 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.6 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.64 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.64 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.65 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.65 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.84 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.91 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.93 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.93 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.93 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.08 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.09 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.1 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.14 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.14 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.24 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.26 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.26 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.31 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.33 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.34 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.34 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.36 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.38 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.38 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.43 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.43 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.47 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.48 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.57 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.58 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.59 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.59 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.6 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.6 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.6 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.61 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.62 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.62 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.65 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.65 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.66 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.67 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.69 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.73 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.78 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.82 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.9 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.9 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.94 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.94 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.96 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 109 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 109 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 109.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 109.26 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 109.26 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 109.26 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 109.33 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 109.33 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 109.38 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 110.13 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 110.7 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 113.2 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12385 | 108.15 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12385 | 108.15 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12387 | 107.43 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12387 | 107.43 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12387 | 108.2 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12388 | 108.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12388 | 108.27 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12389 | 108.34 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12389 | 108.34 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12399 | 108.22 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12403 | 108.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12407 | 108.38 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12407 | 108.38 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12417 | 108.5 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1243 | 108.64 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12432 | 108.87 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12432 | 108.87 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12488 | 110.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12488 | 110.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12502 | 110.2 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12503 | 109.68 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12503 | 109.73 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12512 | 109.88 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12512 | 109.88 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12529 | 109.48 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12534 | 110.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12534 | 110.28 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12593 | 111.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12638 | 110.52 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12674 | 110.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12675 | 110.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12806 | 114.65 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12812 | 114.7 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12828 | 115.03 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12828 | 115.03 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12916 | 112.33 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12925 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12925 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12925 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12943 | 111.45 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12943 | 111.45 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13089 | 115.2 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1322 | 115.8 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1322 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13464 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13464 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13895 | 139.23 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1395 | 121.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1395 | 121.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1396 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1396 | 132.76 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1396 | 135.94 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1396 | 136.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1396 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1396 | 140.37 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1396 | 140.41 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1396 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20498 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10749 | 106.54 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11179 | 100.26 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11179 | 100.26 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11263 | 102.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11263 | 104.7 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11263 | 104.7 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11407 | 100.4 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11521 | 100.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11521 | 101.05 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12109 | 121.34 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12157 | 105.57 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12157 | 106.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12165 | 111.55 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12165 | 115.7 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12165 | 118.48 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12165 | 118.89 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12165 | 121.6 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12165 | 122.33 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12165 | 122.37 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12165 | 123.4 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19777 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0518 | 135.01 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0518 | 135.02 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0518 | 135.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0518 | 135.18 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05795 | 138.19 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0518 | 128.95 | POI 515800_22 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0518 | 129.04 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0518 | 129.06 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0518 | 129.06 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05795 | 130.1 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0518 | 133.67 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0518 | 133.68 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0518 | 133.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0518 | 133.92 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05795 | 137.17 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10062 | 107.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10062 | 107.29 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06605 | 108.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06857 | 104.57 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06861 | 106.59 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06862 | 106.62 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06884 | 103.97 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06885 | 106.9 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06891 | 106.53 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06893 | 103.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06893 | 104.57 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06898 | 103.66 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06914 | 103.29 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06919 | 103.13 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06923 | 103.24 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06929 | 103.35 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0693 | 103.65 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06931 | 103.65 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06932 | 102.88 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06932 | 103.12 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06938 | 102.89 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06945 | 103.45 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06946 | 102.64 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 102.47 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 102.47 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 102.5 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 102.65 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 102.91 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 103.1 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 103.11 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 103.18 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 103.18 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 103.18 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 103.19 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 103.2 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 103.35 | GEN-2023-116_POI_640252_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 103.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 103.44 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 103.51 | P15:230:UMZB:# 2982 #:: DHC IN NE. STEGALL DC CONVERTER STATION AND SHUNT DEVICE:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 103.54 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 103.63 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 103.93 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 103.98 | P23:345:XEL:8P2 KING | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 104 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 104.01 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 104.02 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 104.06 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 104.12 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 104.12 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 104.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 104.3 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 105.12 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 105.2 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 105.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 105.26 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 105.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 105.43 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 105.44 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 105.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 105.53 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 105.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 105.64 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 105.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 105.79 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 105.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 111.13 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06955 | 102.48 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06955 | 105.07 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06955 | 105.13 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06955 | 105.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06957 | 102.76 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06958 | 102.54 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06958 | 102.66 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06959 | 102.73 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06959 | 102.76 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0696 | 102.91 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0696 | 103.18 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0696 | 103.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0696 | 103.18 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0696 | 103.23 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06961 | 102.54 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06961 | 102.61 | P12:345:AMMO::MAYWOOD:SUBT:77 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06962 | 103.82 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06964 | 102.76 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06966 | 102.79 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06966 | 103.18 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06966 | 103.28 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06968 | 103.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06969 | 103.23 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06969 | 103.58 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06971 | 103.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06972 | 102.61 | 300143 4VALLEY 138 514830 FITZGRD4 138 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06974 | 102.86 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06974 | 103.52 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06974 | 103.52 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06975 | 103.04 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06975 | 104.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06978 | 103.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06979 | 103.26 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06981 | 103.02 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06982 | 104.57 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06984 | 104.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06985 | 102.79 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06987 | 103.74 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06987 | 103.74 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06994 | 105.91 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06994 | 105.96 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07009 | 103.57 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0701 | 102.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07019 | 103.37 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07026 | 103.75 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07026 | 103.75 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07058 | 103.64 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07067 | 111.11 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07071 | 103.64 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07078 | 104.88 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07084 | 103.95 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07084 | 103.95 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07137 | 103.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0714 | 103.92 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0714 | 103.92 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0714 | 104.13 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0714 | 104.13 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07142 | 104.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07142 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07142 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07151 | 105.73 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07151 | 105.73 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07231 | 105.39 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07231 | 124.17 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07231 | 124.17 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07231 | 124.17 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07239 | 105.24 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07256 | 108.66 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07292 | 106.49 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07292 | 106.62 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07292 | 106.74 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07292 | 108.72 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0764 | 108.81 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07794 | 119.41 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07794 | 119.41 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07794 | 119.41 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07794 | 119.41 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07794 | 119.41 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07835 | 111.24 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09432 | 124.55 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09432 | 124.55 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09432 | 124.55 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09807 | 134.94 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09807 | 134.94 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.07486 | 109.24 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.07486 | 109.24 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.07486 | 109.24 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08049 | 104.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08049 | 104.23 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08049 | 104.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08049 | 104.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08049 | 104.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09687 | 109.9 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09687 | 109.9 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09687 | 109.9 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10062 | 121.32 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10062 | 121.32 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11417 | 107.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11417 | 107.29 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08459 | 104.57 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08462 | 106.59 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08463 | 106.62 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08486 | 103.97 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08486 | 106.9 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08493 | 106.53 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08499 | 103.66 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08515 | 103.29 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08521 | 103.13 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08532 | 103.65 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08532 | 103.65 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08533 | 102.88 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08533 | 103.12 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0854 | 102.89 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08546 | 103.45 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08548 | 102.64 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 102.47 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 102.47 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 102.48 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 102.5 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 102.65 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 102.91 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 103.1 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 103.11 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 103.18 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 103.18 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 103.18 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 103.19 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 103.2 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 103.35 | GEN-2023-116_POI_640252_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 103.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 103.44 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 103.51 | P15:230:UMZB:# 2982 #:: DHC IN NE. STEGALL DC CONVERTER STATION AND SHUNT DEVICE:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 103.54 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 103.63 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 103.93 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 103.98 | P23:345:XEL:8P2 KING | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 104 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 104.01 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 104.02 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 104.06 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 104.12 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 104.12 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 104.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 104.3 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 105.07 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 105.12 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 105.13 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 105.2 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 105.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 105.26 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 105.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 105.43 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 105.44 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 105.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 105.53 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 105.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 105.64 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 105.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 105.79 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 105.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 111.13 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08557 | 105.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08558 | 102.76 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08559 | 102.54 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08559 | 102.66 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0856 | 102.73 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0856 | 102.76 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08561 | 102.91 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08561 | 103.18 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08561 | 103.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08561 | 103.18 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08561 | 103.23 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08562 | 102.54 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08562 | 102.61 | P12:345:AMMO::MAYWOOD:SUBT:77 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08563 | 103.82 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08565 | 102.76 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08567 | 103.18 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08567 | 103.28 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08568 | 102.79 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08569 | 103.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0857 | 103.23 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0857 | 103.58 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08572 | 103.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 102.61 | 300143 4VALLEY 138 514830 FITZGRD4 138 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08575 | 102.86 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08575 | 103.04 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08575 | 103.52 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08575 | 103.52 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08576 | 104.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08579 | 103.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08581 | 103.26 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08582 | 103.02 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08583 | 104.57 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08585 | 104.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08586 | 102.79 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.74 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.74 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08609 | 103.57 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08611 | 102.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08618 | 103.35 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08619 | 103.37 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08625 | 103.75 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08625 | 103.75 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08653 | 103.64 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08667 | 103.95 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08667 | 103.95 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08673 | 104.88 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08678 | 103.64 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08683 | 103.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08683 | 104.57 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08685 | 111.11 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08695 | 103.24 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08735 | 104.13 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08735 | 104.13 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0874 | 105.73 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0874 | 105.73 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08743 | 103.92 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08743 | 103.92 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08743 | 103.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08766 | 104.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08766 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08766 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08807 | 105.91 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08807 | 105.96 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08821 | 105.39 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08829 | 105.24 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08923 | 108.66 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08962 | 106.49 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08962 | 106.62 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08962 | 106.74 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08962 | 108.72 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09035 | 108.81 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09184 | 108.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09363 | 111.24 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09573 | 119.41 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09573 | 119.41 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09573 | 119.41 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09573 | 119.41 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09573 | 119.41 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10334 | 124.17 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10334 | 124.17 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10334 | 124.17 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10832 | 124.55 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10832 | 124.55 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10832 | 124.55 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11162 | 134.94 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11162 | 134.94 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09828 | 104.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09828 | 104.23 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09828 | 104.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09828 | 104.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09828 | 104.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10588 | 109.24 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10588 | 109.24 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10588 | 109.24 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11087 | 109.9 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11087 | 109.9 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11087 | 109.9 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11417 | 121.32 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11417 | 121.32 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.08566 | 114.05 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.08566 | 114.9 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14192 | 112.47 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21697 | 108.23 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21697 | 108.23 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21715 | 107.69 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21715 | 107.69 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21717 | 107.69 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21717 | 108.08 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.35 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.38 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.39 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.4 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.4 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.4 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.6 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.69 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.84 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.85 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.86 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.88 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.88 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.02 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.02 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.08 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.1 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.1 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.1 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.12 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.15 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.15 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.19 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.2 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.23 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.34 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.35 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.36 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.36 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.37 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.37 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.37 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.38 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.39 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.39 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.42 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.42 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.43 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.44 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.45 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.5 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.55 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.59 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.67 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.67 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.69 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.69 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.69 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.71 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.71 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.73 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.78 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.78 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.78 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.91 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.91 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.91 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.96 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.97 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.99 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 109.92 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 109.95 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 110.21 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 110.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 112.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21723 | 107.69 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21723 | 107.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21723 | 107.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21724 | 107.91 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21725 | 107.91 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21726 | 107.96 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21726 | 108.02 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21726 | 108.03 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21727 | 107.18 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21728 | 108.11 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21728 | 108.11 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21736 | 107.98 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2174 | 108.21 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21745 | 108.21 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21745 | 108.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21755 | 108.27 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21757 | 108.41 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21766 | 108.64 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21766 | 108.64 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21817 | 110.01 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21818 | 109.95 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21818 | 109.95 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21828 | 109.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21828 | 109.68 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21833 | 109.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21833 | 109.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21834 | 109.29 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21846 | 109.91 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21922 | 110.26 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21922 | 111 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21923 | 110.27 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21961 | 110.36 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22088 | 114.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22096 | 114.62 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22101 | 112.06 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22111 | 114.95 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22111 | 114.95 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22128 | 111.18 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22128 | 111.18 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2222 | 115.01 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22235 | 110.39 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22364 | 115.82 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22364 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22589 | 121.87 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2274 | 136.58 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22832 | 120.81 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22832 | 121.59 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 130.57 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 133.59 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 134.05 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 137.75 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 137.78 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23178 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23178 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23178 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35965 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19269 | 100.18 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19269 | 100.18 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19364 | 100.23 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1949 | 100.94 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1949 | 101.06 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19686 | 106.21 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19817 | 119.03 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19897 | 105.29 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19897 | 105.97 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1991 | 110.17 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1991 | 113.79 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1991 | 116.43 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1991 | 116.82 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1991 | 119.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1991 | 120.05 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1991 | 120.08 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1991 | 121.11 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20199 | 101.8 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20199 | 103.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20199 | 103.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.347 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12536 | 100.95 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23276 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23373 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23572 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23731 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.238 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2381 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23826 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23831 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23832 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23836 | 101.44 | Potential P4 Event - POI 523823_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23979 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24064 | 104.75 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24069 | 104.09 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24069 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24213 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24396 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24941 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25122 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42557 | 152.61 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.43752 | 184.51 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.43988 | 183.79 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.44386 | 179.87 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.44386 | 179.92 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.44386 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.44386 | 191.94 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22883 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23049 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4252 | 153.1 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.43709 | 184.91 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.43943 | 184.16 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4434 | 180.34 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4434 | 180.35 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4434 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4434 | 192.34 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14192 | 113.2 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21697 | 108.46 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21697 | 108.46 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21715 | 107.93 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21715 | 107.93 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21717 | 107.93 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21717 | 108.31 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.6 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.64 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.64 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.65 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.65 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.84 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.91 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.93 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.93 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.93 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.08 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.09 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.1 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.14 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.14 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.24 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.26 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.26 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.31 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.33 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.34 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.34 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.36 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.38 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.38 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.43 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.43 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.47 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.48 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.57 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.58 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.59 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.59 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.6 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.6 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.6 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.61 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.62 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.62 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.65 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.65 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.66 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.67 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.69 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.73 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.78 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.82 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.9 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.9 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.94 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.94 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.96 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 109 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 109 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 109.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 109.26 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 109.26 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 109.26 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 109.33 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 109.33 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 109.38 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 110.13 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 110.7 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 113.2 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21724 | 108.15 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21725 | 108.15 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21726 | 108.2 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21726 | 108.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21726 | 108.27 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21727 | 107.43 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21727 | 107.43 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21728 | 108.34 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21728 | 108.34 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21736 | 108.22 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2174 | 108.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21745 | 108.38 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21745 | 108.38 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21755 | 108.5 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21757 | 108.64 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21766 | 108.87 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21766 | 108.87 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21817 | 110.2 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21818 | 110.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21818 | 110.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21828 | 109.88 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21828 | 109.88 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21833 | 109.68 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21833 | 109.73 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21834 | 109.48 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21846 | 110.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21922 | 110.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21922 | 111.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21923 | 110.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21924 | 110.28 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21961 | 110.52 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22088 | 114.65 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22096 | 114.7 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22101 | 112.33 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22111 | 115.03 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22111 | 115.03 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22128 | 111.45 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22128 | 111.45 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2222 | 115.2 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22235 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22235 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22364 | 115.8 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22364 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22589 | 122.24 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2274 | 139.23 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22832 | 121.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22832 | 121.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 132.76 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 135.94 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 136.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 140.37 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 140.41 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23178 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23178 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23178 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35965 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19269 | 100.26 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19269 | 100.26 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19364 | 100.4 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1949 | 100.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1949 | 101.05 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19686 | 106.54 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19817 | 121.34 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19897 | 105.57 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19897 | 106.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1991 | 111.55 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1991 | 115.7 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1991 | 118.48 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1991 | 118.89 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1991 | 121.6 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1991 | 122.33 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1991 | 122.37 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1991 | 123.4 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20199 | 102.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20199 | 104.7 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20199 | 104.7 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.347 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0531 | 138.19 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0547 | 135.01 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0547 | 135.02 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0547 | 135.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0547 | 135.18 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0531 | 130.1 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0547 | 128.95 | POI 515800_22 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0547 | 129.04 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0547 | 129.06 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0547 | 129.06 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0531 | 137.17 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0547 | 133.67 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0547 | 133.68 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0547 | 133.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0547 | 133.92 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 1 | 159 | 159 | 0.11966 | 101.24 | Potential P4 Event - POI 523097_33 | Cumulative Impact | Rebuild the existing SPEARMAN3 to PRINGLE3 115 kV CKT1 line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 1 | 159 | 159 | 0.11966 | 101.24 | Potential P4 Event - POI 523961_4 | Cumulative Impact | Rebuild the existing SPEARMAN3 to PRINGLE3 115 kV CKT1 line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 1 | 159 | 159 | 0.17552 | 116.46 | P12:115:SPS:T08_2_SPRMN_PRNGLE:::: | Cumulative Impact | Rebuild the existing SPEARMAN3 to PRINGLE3 115 kV CKT1 line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 2 | 159 | 159 | 0.15759 | 104.93 | P12:115:SPS:T06_1_SPRMN_PRNGLE:::: | Cumulative Impact | Rebuild the existing SPEARMAN3 to PRINGLE3 115 kV CKT2 line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.39526 | 105.96 | P12:115:SPS:T49_1_PRNGLE_BLKHK:::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.39526 | 107.15 | 523214 WRB_REF 115 523396 WRB_SW 115 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.39526 | 110.11 | 523214 WRB_REF 115 523346 BLKHAWK_E 3 115 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41342 | 104.88 | P12:230:SPS:K98::1_CHANN_XIT:: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41357 | 102.85 | P12:345:OKGE:BKRBKR604_2 :::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41362 | 102.34 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41362 | 102.41 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41362 | 102.62 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41362 | 102.63 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41363 | 101.93 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41363 | 101.94 | 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41363 | 102.18 | 539783 CRKCK 3 115 539784 ENSNGW 3 115 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41363 | 102.22 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41363 | 102.25 | P13:115:SUNC:FORTDODGE_GSU:::HV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41363 | 102.64 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41364 | 102.17 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41364 | 102.17 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41364 | 102.23 | P11:345:WERE:JECU2-GEN:::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41364 | 102.23 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 101.79 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 101.91 | P12:EHV:EES::8PERRYVILLE%:1(1) | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 101.92 | P11:230-22:CLEC::RODEMR 6:1(1) | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 101.93 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 101.93 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 101.93 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 101.93 | P11:HV:EES::1CARVLE_C1!:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 101.93 | P12:LV-EHV:EES::7GRIMES%:1FRNTR 1!:1FRNTR 2!:1FRNTR 3!:1FRNTR 4!:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 101.94 | P12:LV-HV:EES::6GYPSY%:1GYP U3!:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.15 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.15 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.15 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.15 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.16 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.16 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.16 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.18 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.19 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.2 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.2 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.21 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.22 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.22 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.22 | P23:345:XEL:8P2 KING | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.25 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.25 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.25 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.26 | 531451 MINGO 7 345 531632 SLMNFRK7 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.27 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.28 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.29 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.3 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.48 | 772281 GEN-2023-015 345 772282 G23-015XFMR1 34.5 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.52 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.54 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.54 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.54 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.54 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.54 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.55 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.55 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.56 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.56 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.56 | P23:345:MEC:CBEC 908 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.57 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.57 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.58 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.59 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.59 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.59 | P23:345:MEC:CBEC 905 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.61 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.61 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.62 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.62 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.63 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.78 | 522941 LOBO-T 3 115 522957 POWELL CNR 3 115 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.78 | 772181 GEN-2023-010 230 772182 G23-010XFMR1 34.5 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.78 | 772181 GEN-2023-010 230 772185 G23-010XFMR2 34.5 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.78 | P12:115:GLHP:POWELL-LOBO-DRYTRAILS:::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.9 | 522941 LOBO-T 3 115 523099 TC-DRYTRLS 3 115 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 103.15 | GEN-2006-044_POI_523097_Generator_outage | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 103.19 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 103.2 | ASGI-2016-010_POI_523090_Generator_outage | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 103.32 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 103.32 | GEN-2017-100_POI_523090_Generator_outage | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 103.54 | GEN-2023-010_POI_523309_Generator_outage | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 103.58 | GEN-2002-009_POI_523195_Generator_outage | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 103.73 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 103.73 | GEN-2017-047_POI_523120_Generator_outage | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 108.01 | 523344 BLKHAWK_W 3 115 523461 BLACKHAWK1 1 13.8 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 108.58 | 523346 BLKHAWK_E 3 115 523462 BLACKHAWK2 1 13.8 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41366 | 102.27 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41366 | 102.27 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41366 | 102.29 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41366 | 102.35 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41366 | 102.38 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41368 | 102.43 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41369 | 102.41 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41369 | 102.42 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.4137 | 102.45 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41371 | 102.24 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41372 | 102.38 | P23:345:AEPW:PITTSBURG CB 3445A NBTB:::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41372 | 102.38 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT:::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41375 | 102.45 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41375 | 102.56 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41376 | 103.13 | Potential P4 Event - POI 560022_9 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41376 | 103.13 | Potential P4 Event - POI 762216_5 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.4138 | 102.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41382 | 102.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41384 | 103.41 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41384 | 103.56 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41384 | 103.56 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41386 | 103.09 | Potential P4 Event - POI 762216_14 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41386 | 103.09 | Potential P4 Event - POI 762467_7 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41396 | 103.21 | POI 515800_22 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41396 | 103.24 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41415 | 104.24 | P42:345:OKGE:SB_BOER7384:::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41417 | 104 | 515375 WWRDEHV7 345 516059 BECKHAM7 345 2 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41417 | 104 | P12:345:OKGE:BKRBKR489:::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41441 | 107.6 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41447 | 104.47 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41447 | 105.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41516 | 102.53 | 523977 HARRNG_WST 6 230 523978 HARRNG_MID 6 230 @1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41535 | 108.4 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41538 | 105.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41544 | 104.58 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41544 | 104.58 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41605 | 117.31 | Potential P4 Event - POI 523097_33 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41605 | 117.31 | Potential P4 Event - POI 523961_4 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41773 | 106.3 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.44502 | 105.66 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 1 | 145.55 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.39526 | 109.01 | P12:115:SPS:T49_1_PRNGLE_BLKHK:::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.39526 | 113.84 | 523214 WRB_REF 115 523346 BLKHAWK_E 3 115 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41342 | 108.42 | P12:230:SPS:K98::1_CHANN_XIT:: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41351 | 105.29 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41357 | 106.28 | P12:345:OKGE:BKRBKR604_2 :::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41362 | 105.74 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41362 | 105.83 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41362 | 106.04 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41362 | 106.04 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41363 | 105.57 | 539783 CRKCK 3 115 539784 ENSNGW 3 115 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41363 | 105.61 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41363 | 105.64 | P13:115:SUNC:FORTDODGE_GSU:::HV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41363 | 106.06 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41364 | 105.31 | 640183 GENTLMN3 345 640500 THEDFRD3 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41364 | 105.57 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41364 | 105.57 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41364 | 105.62 | P11:345:WERE:JECU2-GEN:::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41364 | 105.62 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.13 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.28 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.29 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.3 | P12:LV-HV:EES::6GYPSY%:1GYP U3!:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.31 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.31 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.31 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.31 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.31 | P12:HV:EES::4LEWIS%:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.31 | P12:HV:EES::4LEWIS%:1(1) | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.31 | P12:LV-HV:EES::3GYPSY%:1GYP U2!:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.52 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.52 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.54 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.54 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.54 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.54 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.55 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.55 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.55 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.57 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.58 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.59 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.59 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.61 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.61 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.62 | 531451 MINGO 7 345 531632 SLMNFRK7 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.62 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.62 | P23:345:XEL:8P2 KING | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.65 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.65 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.66 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.67 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.67 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.69 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.69 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.89 | 772281 GEN-2023-015 345 772282 G23-015XFMR1 34.5 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.92 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.93 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.93 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.93 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.93 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.94 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.95 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.96 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.96 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.96 | P23:345:MEC:CBEC 908 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.97 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.97 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.98 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.99 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.99 | P23:345:MEC:CBEC 905 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.02 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.02 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.03 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.03 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.04 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.11 | 772181 GEN-2023-010 230 772182 G23-010XFMR1 34.5 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.11 | 772181 GEN-2023-010 230 772185 G23-010XFMR2 34.5 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.18 | 522941 LOBO-T 3 115 522957 POWELL CNR 3 115 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.18 | P12:115:GLHP:POWELL-LOBO-DRYTRAILS:::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.3 | 522941 LOBO-T 3 115 523099 TC-DRYTRLS 3 115 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.52 | ASGI-2011-002_POI_523266_Generator_outage | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.61 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.61 | ASGI-2016-010_POI_523090_Generator_outage | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.73 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.73 | GEN-2017-100_POI_523090_Generator_outage | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.87 | GEN-2023-010_POI_523309_Generator_outage | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 107.03 | GEN-2002-009_POI_523195_Generator_outage | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 107.15 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 107.16 | GEN-2017-047_POI_523120_Generator_outage | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 111.28 | 523344 BLKHAWK_W 3 115 523461 BLACKHAWK1 1 13.8 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 111.84 | 523346 BLKHAWK_E 3 115 523462 BLACKHAWK2 1 13.8 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41366 | 105.52 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41366 | 105.67 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41366 | 105.68 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41366 | 105.68 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41366 | 105.76 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41366 | 105.79 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41368 | 105.86 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41369 | 105.82 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41369 | 105.84 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.4137 | 105.88 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41371 | 105.64 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41372 | 105.79 | P23:345:AEPW:PITTSBURG CB 3445A NBTB:::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41372 | 105.79 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT:::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41375 | 105.87 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41375 | 105.99 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41376 | 106.6 | Potential P4 Event - POI 560022_9 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41376 | 106.6 | Potential P4 Event - POI 762216_5 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.4138 | 106.12 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41382 | 106.23 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41384 | 106.93 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41384 | 107.1 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41384 | 107.1 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41386 | 106.57 | Potential P4 Event - POI 762216_14 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41386 | 106.57 | Potential P4 Event - POI 762467_7 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41396 | 106.73 | POI 515800_22 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41396 | 106.78 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41415 | 107.79 | P42:345:OKGE:SB_BOER7384:::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41417 | 107.54 | 515375 WWRDEHV7 345 516059 BECKHAM7 345 2 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41417 | 107.54 | P12:345:OKGE:BKRBKR489:::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41441 | 110.65 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41441 | 111.36 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41447 | 108.12 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41447 | 109.03 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41516 | 105.96 | 523977 HARRNG_WST 6 230 523978 HARRNG_MID 6 230 @1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41535 | 112.38 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41538 | 108.97 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41544 | 108.19 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41544 | 108.2 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41605 | 121.81 | Potential P4 Event - POI 523097_33 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41605 | 121.81 | Potential P4 Event - POI 523961_4 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41773 | 109.93 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.44502 | 109.13 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 1 | 143.52 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.14292 | 107.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.14292 | 107.29 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1117 | 104.57 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11174 | 106.59 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11175 | 106.62 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11197 | 103.97 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11198 | 106.9 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11205 | 106.53 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11211 | 103.66 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11227 | 103.29 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11233 | 103.13 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11244 | 103.65 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11244 | 103.65 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11245 | 102.88 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11245 | 103.12 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11251 | 102.89 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11258 | 103.45 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11259 | 102.64 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11267 | 103.98 | P23:345:XEL:8P2 KING | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 102.47 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 102.47 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 102.48 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 102.5 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 102.65 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 102.91 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 103.1 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 103.11 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 103.18 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 103.18 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 103.18 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 103.19 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 103.2 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 103.35 | GEN-2023-116_POI_640252_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 103.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 103.44 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 103.51 | P15:230:UMZB:# 2982 #:: DHC IN NE. STEGALL DC CONVERTER STATION AND SHUNT DEVICE:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 103.54 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 103.63 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 103.93 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 104 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 104.01 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 104.02 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 104.06 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 104.12 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 104.12 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 104.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 104.3 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 105.07 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 105.12 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 105.13 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 105.2 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 105.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 105.26 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 105.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 105.43 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 105.44 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 105.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 105.53 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 105.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 105.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 105.64 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 105.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 105.79 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 105.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 111.13 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1127 | 102.66 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1127 | 102.76 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11271 | 102.54 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11271 | 102.73 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11271 | 102.76 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11271 | 102.91 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11271 | 103.18 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11271 | 103.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11271 | 103.18 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11272 | 103.23 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11273 | 102.54 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11273 | 102.61 | P12:345:AMMO::MAYWOOD:SUBT:77 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11274 | 103.82 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11277 | 102.76 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11277 | 103.18 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11277 | 103.28 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11278 | 102.79 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11278 | 103.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11279 | 103.23 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11279 | 103.58 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1128 | 103.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11283 | 102.86 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11283 | 103.04 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11284 | 102.61 | 300143 4VALLEY 138 514830 FITZGRD4 138 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11285 | 103.26 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11286 | 103.52 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11286 | 103.52 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11287 | 103.02 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11287 | 104.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11289 | 104.57 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1129 | 103.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11291 | 104.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11294 | 103.74 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11294 | 103.74 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11295 | 102.79 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11312 | 103.57 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11318 | 102.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11318 | 103.37 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11323 | 103.75 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11323 | 103.75 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11351 | 103.64 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11353 | 103.35 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11356 | 104.88 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11366 | 103.64 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11404 | 104.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11404 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11404 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1141 | 103.95 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1141 | 103.95 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11411 | 105.73 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11411 | 105.73 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11421 | 103.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11424 | 111.11 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11428 | 103.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11428 | 104.57 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11429 | 103.92 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11429 | 103.92 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11434 | 104.13 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11434 | 104.13 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11511 | 105.39 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11519 | 105.24 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11544 | 103.24 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11743 | 108.66 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11771 | 105.91 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11771 | 105.96 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11792 | 106.49 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11792 | 106.62 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11792 | 106.74 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11792 | 108.72 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11912 | 108.81 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12081 | 108.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12136 | 111.24 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12584 | 119.41 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12584 | 119.41 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12584 | 119.41 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12584 | 119.41 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12584 | 119.41 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.13752 | 124.55 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.13752 | 124.55 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.13752 | 124.55 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.14037 | 134.94 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.14037 | 134.94 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.14826 | 124.17 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.14826 | 124.17 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.14826 | 124.17 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12839 | 104.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12839 | 104.23 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12839 | 104.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12839 | 104.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12839 | 104.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.14006 | 109.9 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.14006 | 109.9 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.14006 | 109.9 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.14292 | 121.32 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.14292 | 121.32 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.15081 | 109.24 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.15081 | 109.24 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.15081 | 109.24 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08444 | 121.87 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08853 | 108.23 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08853 | 108.23 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08871 | 107.69 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08871 | 107.69 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08873 | 107.69 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08873 | 108.08 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.35 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.38 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.39 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.4 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.4 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.4 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.6 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.69 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.84 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.85 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.86 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.88 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.88 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.02 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.02 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.08 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.1 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.1 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.1 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.12 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.15 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.15 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.19 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.2 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.23 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.34 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.35 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.36 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.36 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.37 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.37 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.37 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.38 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.39 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.39 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.42 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.42 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.43 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.44 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.45 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.5 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.55 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.59 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.67 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.67 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.69 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.69 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.69 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.71 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.71 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.73 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.78 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.78 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.78 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.91 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.91 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.91 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.96 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.97 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.99 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 109.92 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 109.95 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 110.21 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 110.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 112.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08879 | 107.69 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08879 | 107.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08879 | 107.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08882 | 107.91 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08882 | 107.91 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08883 | 107.18 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08884 | 107.96 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08885 | 108.02 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08885 | 108.03 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08886 | 108.11 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08886 | 108.11 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08893 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08893 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08893 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08899 | 107.98 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08902 | 108.21 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08903 | 108.21 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08903 | 108.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08915 | 108.27 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08932 | 108.64 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08932 | 108.64 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08942 | 108.41 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08994 | 109.95 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08994 | 109.95 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0901 | 109.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0901 | 109.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09028 | 110.01 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0903 | 109.29 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09038 | 109.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09038 | 109.68 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09039 | 109.91 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0909 | 111 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09139 | 110.36 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09148 | 110.26 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09149 | 110.27 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09367 | 114.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09371 | 114.62 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09388 | 114.95 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09388 | 114.95 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09661 | 112.06 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09687 | 111.18 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09687 | 111.18 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09743 | 115.82 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09743 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09834 | 110.39 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09879 | 115.01 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10251 | 136.58 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10299 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10299 | 130.57 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10299 | 133.59 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10299 | 134.05 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10299 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10299 | 137.75 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10299 | 137.78 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10299 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10317 | 120.81 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10317 | 121.59 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14695 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07358 | 106.21 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0775 | 101.8 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0775 | 103.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0775 | 103.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08182 | 100.18 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08182 | 100.18 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08491 | 100.94 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08491 | 101.06 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08609 | 100.23 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08933 | 119.03 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08975 | 110.17 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08975 | 113.79 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08975 | 116.43 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08975 | 116.82 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08975 | 119.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08975 | 120.05 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08975 | 120.08 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08975 | 121.11 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08991 | 105.29 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08991 | 105.97 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14178 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10372 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10822 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11285 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11299 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11599 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11982 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11988 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12004 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12009 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12013 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12018 | 101.44 | Potential P4 Event - POI 523823_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12221 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12313 | 104.75 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12321 | 104.09 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12321 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12546 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12693 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13442 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19184 | 152.61 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21418 | 183.79 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2152 | 179.87 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2152 | 179.92 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2152 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2152 | 191.94 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21969 | 184.51 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.09517 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.12333 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.19167 | 153.1 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21396 | 184.16 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21498 | 180.34 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21498 | 180.35 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21498 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21498 | 192.34 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21947 | 184.91 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08444 | 122.24 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08853 | 108.46 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08853 | 108.46 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08871 | 107.93 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08871 | 107.93 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08873 | 107.93 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08873 | 108.31 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.6 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.64 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.64 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.65 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.65 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.84 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.91 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.93 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.93 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.93 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.08 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.09 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.1 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.14 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.14 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.24 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.26 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.26 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.31 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.33 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.34 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.34 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.36 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.38 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.38 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.43 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.43 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.47 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.48 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.57 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.58 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.59 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.59 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.6 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.6 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.6 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.61 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.62 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.62 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.65 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.65 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.66 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.67 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.69 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.73 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.78 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.82 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.9 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.9 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.94 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.94 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.96 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 109 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 109 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 109.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 109.26 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 109.26 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 109.26 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 109.33 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 109.33 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 109.38 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 110.13 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 110.7 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 113.2 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08882 | 108.15 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08882 | 108.15 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08883 | 107.43 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08883 | 107.43 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08884 | 108.2 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08885 | 108.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08885 | 108.27 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08886 | 108.34 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08886 | 108.34 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08893 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08893 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08893 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08899 | 108.22 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08902 | 108.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08903 | 108.38 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08903 | 108.38 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08915 | 108.5 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08932 | 108.87 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08932 | 108.87 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08942 | 108.64 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08966 | 110.28 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08994 | 110.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08994 | 110.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0901 | 109.68 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0901 | 109.73 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09028 | 110.2 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0903 | 109.48 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09038 | 109.88 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09038 | 109.88 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09039 | 110.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0909 | 111.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09139 | 110.52 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09148 | 110.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09149 | 110.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09367 | 114.65 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09371 | 114.7 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09388 | 115.03 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09388 | 115.03 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09661 | 112.33 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09687 | 111.45 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09687 | 111.45 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09743 | 115.8 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09743 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09834 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09834 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09879 | 115.2 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10251 | 139.23 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10299 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10299 | 132.76 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10299 | 135.94 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10299 | 136.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10299 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10299 | 140.37 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10299 | 140.41 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10299 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10317 | 121.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10317 | 121.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14695 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07358 | 106.54 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0775 | 102.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0775 | 104.7 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0775 | 104.7 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08182 | 100.26 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08182 | 100.26 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08491 | 100.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08491 | 101.05 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08609 | 100.4 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08933 | 121.34 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08975 | 111.55 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08975 | 115.7 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08975 | 118.48 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08975 | 118.89 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08975 | 121.6 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08975 | 122.33 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08975 | 122.37 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08975 | 123.4 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08991 | 105.57 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08991 | 106.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14178 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1153 | 107.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1153 | 107.29 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0854 | 104.57 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08544 | 106.59 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08545 | 106.62 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08567 | 103.97 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08568 | 106.9 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08575 | 106.53 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08581 | 103.66 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 103.29 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08603 | 103.13 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08614 | 103.65 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08614 | 103.65 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08615 | 102.88 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08615 | 103.12 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08621 | 102.89 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08628 | 103.45 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0863 | 102.64 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.47 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.47 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.48 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.5 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.65 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.91 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.1 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.11 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.18 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.18 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.18 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.19 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.2 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.35 | GEN-2023-116_POI_640252_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.44 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.51 | P15:230:UMZB:# 2982 #:: DHC IN NE. STEGALL DC CONVERTER STATION AND SHUNT DEVICE:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.54 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.63 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.93 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.98 | P23:345:XEL:8P2 KING | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.01 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.02 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.06 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.12 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.12 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.3 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.07 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.12 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.13 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.2 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.26 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.43 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.44 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.53 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.64 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.79 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 111.13 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0864 | 102.76 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08641 | 102.54 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08641 | 102.66 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08642 | 102.73 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08642 | 102.76 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08643 | 102.91 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08643 | 103.18 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08643 | 103.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08643 | 103.18 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08643 | 103.23 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08644 | 102.54 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08644 | 102.61 | P12:345:AMMO::MAYWOOD:SUBT:77 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08645 | 103.82 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 102.76 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 102.79 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 103.18 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 103.28 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08651 | 103.23 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08651 | 103.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08651 | 103.58 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08653 | 103.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08655 | 102.61 | 300143 4VALLEY 138 514830 FITZGRD4 138 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08656 | 102.86 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08657 | 103.04 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08657 | 103.52 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08657 | 103.52 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08658 | 104.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08661 | 103.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08662 | 103.26 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08663 | 103.02 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08664 | 104.57 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08666 | 104.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08668 | 102.79 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08669 | 103.74 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08669 | 103.74 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0869 | 103.57 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08692 | 102.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.087 | 103.37 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08706 | 103.75 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08706 | 103.75 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08734 | 103.64 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08738 | 103.24 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08749 | 103.95 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08749 | 103.95 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08753 | 104.88 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08758 | 103.64 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08768 | 111.11 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08816 | 104.13 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08816 | 104.13 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0882 | 105.73 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0882 | 105.73 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08822 | 103.92 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08822 | 103.92 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08822 | 103.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08841 | 104.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08841 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08841 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08892 | 105.91 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08892 | 105.96 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08902 | 105.39 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0891 | 105.24 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08929 | 103.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08929 | 104.57 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08973 | 103.35 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09008 | 108.66 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09048 | 106.49 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09048 | 106.62 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09048 | 106.74 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09048 | 108.72 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09148 | 108.81 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09376 | 108.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09455 | 111.24 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09664 | 119.41 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09664 | 119.41 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09664 | 119.41 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09664 | 119.41 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09664 | 119.41 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10434 | 124.17 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10434 | 124.17 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10434 | 124.17 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10946 | 124.55 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10946 | 124.55 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10946 | 124.55 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11275 | 134.94 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11275 | 134.94 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09919 | 104.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09919 | 104.23 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09919 | 104.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09919 | 104.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09919 | 104.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10689 | 109.24 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10689 | 109.24 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10689 | 109.24 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11201 | 109.9 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11201 | 109.9 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11201 | 109.9 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1153 | 121.32 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1153 | 121.32 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13 | 111.5 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13888 | 102.83 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13888 | 102.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13888 | 102.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13915 | 103.68 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13915 | 103.68 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.1395 | 104.16 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17344 | 114.4 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17719 | 107.58 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18762 | 107.83 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18762 | 108.41 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18762 | 108.41 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18788 | 109.17 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18788 | 109.17 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18824 | 109.67 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.11 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.11 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.11 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.12 | ASGI-2011-004_POI_525915_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.17 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.33 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.59 | GEN-2011-025_POI_525803_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.64 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 101.04 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 101.04 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 101.04 | GEN-2023-086_POI_773700_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 103.21 | 774381 GEN-2023-120 115 774382 G23-120XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 103.21 | GEN-2023-120_POI_525192_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 105.36 | 524757 BETHEL_COL 3 115 524755 BETHEL_COL11 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 106.65 | GEN-2014-040_POI_524746_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07656 | 100.11 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07656 | 100.11 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0766 | 100.13 | 515375 WWRDEHV7 345 516059 BECKHAM7 345 2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07661 | 100.84 | Potential P4 Event - POI 776000_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07662 | 100.19 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07662 | 100.25 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07662 | 100.29 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07662 | 100.29 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07662 | 100.31 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07663 | 100.19 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07665 | 100.32 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07665 | 100.32 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07678 | 100.67 | POI 515800_22 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07678 | 100.69 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07682 | 102.94 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07725 | 101.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07725 | 102.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 103.85 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 104.28 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 105.13 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 105.26 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07843 | 102.17 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07935 | 103.83 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08031 | 105.78 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08139 | 118.93 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09004 | 115.77 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09004 | 116.09 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 116.35 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 116.35 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09015 | 116.49 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09265 | 117.56 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09265 | 120.95 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.10347 | 127.17 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.66 | 524757 BETHEL_COL 3 115 524756 BETHEL_COL21 34.5 2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 101.52 | 774381 GEN-2023-120 115 774382 G23-120XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 101.52 | GEN-2023-120_POI_525192_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 103.4 | 524757 BETHEL_COL 3 115 524755 BETHEL_COL11 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 105.44 | GEN-2014-040_POI_524746_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07682 | 101.12 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07725 | 100.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07725 | 100.64 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 102.3 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 102.76 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 103.7 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 103.84 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07935 | 102.14 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08031 | 104.12 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08139 | 118.92 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09004 | 114.41 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09004 | 114.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 115.06 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 115.06 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09015 | 115.22 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09265 | 115.67 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09265 | 119.13 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.10347 | 125.32 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.11102 | 138.46 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1502 | 134.22 | 560022 CRAWFISH_DR 345 774180 G23-110-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15121 | 134.27 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15121 | 134.32 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15122 | 134.67 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.02 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.07 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.08 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.08 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.09 | P23:345:XEL:8N17 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.09 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.1 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.62 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.65 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.65 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.67 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.7 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.7 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.71 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.71 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.74 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.74 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.75 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.77 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.8 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.81 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.87 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.88 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.88 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.88 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.89 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.89 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.9 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.91 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.91 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.91 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.93 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.93 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.94 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.95 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.03 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.05 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.11 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.11 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.12 | P11:21:EES:RVB:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.12 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.12 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.14 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.14 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.17 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.19 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.19 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.19 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.44 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.44 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.5 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.67 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.67 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.67 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 136.51 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 138.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15125 | 134.33 | 539784 ENSNGW 3 115 3WXFMR ENSIGN WIND 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.35 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.36 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.36 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.36 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.58 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.58 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15127 | 134.62 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15127 | 134.68 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15127 | 134.68 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15128 | 133.94 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15128 | 134.74 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15128 | 134.74 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15132 | 134.64 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15135 | 134.82 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15136 | 134.89 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15138 | 134.81 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15138 | 134.81 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15138 | 134.81 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15138 | 134.81 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15142 | 134.86 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15149 | 135.18 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15149 | 135.18 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15175 | 136.3 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15176 | 136.26 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15176 | 136.26 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15181 | 136.03 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15181 | 136.03 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15184 | 135.85 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15184 | 135.9 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1519 | 136.2 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15191 | 135.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15216 | 136.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15225 | 136.42 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15225 | 136.42 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15237 | 137.2 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15258 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15259 | 136.64 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15259 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15321 | 140.07 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15324 | 140.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15333 | 140.41 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15333 | 140.41 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15386 | 140.35 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15504 | 141.43 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15504 | 141.57 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15736 | 138.37 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15747 | 138.2 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15801 | 138.53 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15893 | 146.73 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15893 | 147.76 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16243 | 142.55 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 150.42 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 154 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 156.76 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 157.19 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 159.91 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 161.9 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16762 | 148.33 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17038 | 159.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1998 | 162.73 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1998 | 164.74 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1998 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19991 | 165.01 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19991 | 165.01 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20014 | 165.4 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.2073 | 114.05 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.2073 | 114.9 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10203 | 112.47 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17709 | 108.23 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17709 | 108.23 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17726 | 107.69 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17726 | 107.69 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17729 | 107.69 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17729 | 108.08 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.35 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.38 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.39 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.4 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.4 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.4 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.6 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.69 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.84 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.85 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.86 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.88 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.88 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.02 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.02 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.08 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.1 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.1 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.1 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.12 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.15 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.15 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.19 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.2 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.23 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.34 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.35 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.36 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.36 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.37 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.37 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.37 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.38 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.39 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.39 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.42 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.42 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.43 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.44 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.45 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.5 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.55 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.59 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.67 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.67 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.69 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.69 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.69 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.71 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.71 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.73 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.78 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.78 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.78 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.91 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.91 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.91 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.96 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.97 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.99 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.92 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.95 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 110.21 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 110.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 112.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17735 | 107.69 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17735 | 107.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17735 | 107.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17736 | 107.91 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17737 | 107.91 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 107.96 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 108.02 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 108.03 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17739 | 107.18 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1774 | 108.11 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1774 | 108.11 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17748 | 107.98 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17752 | 108.21 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17757 | 108.21 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17757 | 108.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 108.41 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17767 | 108.27 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17778 | 108.64 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17778 | 108.64 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1783 | 110.01 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17831 | 109.95 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17831 | 109.95 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17841 | 109.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17841 | 109.68 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17845 | 109.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17845 | 109.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17853 | 109.29 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17858 | 109.91 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 111 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 110.26 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 110.27 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17976 | 110.36 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17997 | 112.06 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17999 | 110.39 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18023 | 111.18 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18023 | 111.18 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18104 | 114.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18111 | 114.62 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18127 | 114.95 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18127 | 114.95 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18237 | 115.01 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18418 | 115.82 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18418 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19039 | 120.81 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19039 | 121.59 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19703 | 121.87 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20217 | 136.58 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 130.57 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 133.59 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 134.05 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 137.75 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 137.78 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2936 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15797 | 100.18 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15797 | 100.18 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15893 | 100.23 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1605 | 100.94 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1605 | 101.06 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16592 | 105.29 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16592 | 105.97 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17171 | 106.21 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17618 | 119.03 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 110.17 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 113.79 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 116.43 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 116.82 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 119.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 120.05 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 120.08 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 121.11 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 101.8 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 103.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 103.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28327 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1132 | 100.95 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2206 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22083 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2236 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22378 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22589 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.226 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22616 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22621 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22622 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22626 | 101.44 | Potential P4 Event - POI 523823_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22771 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22855 | 104.75 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22861 | 104.09 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22861 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23058 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24019 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24771 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26243 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37835 | 152.61 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41566 | 184.51 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41702 | 183.79 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 179.87 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 179.92 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 191.94 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22037 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24078 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37802 | 153.1 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41526 | 184.91 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4166 | 184.16 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 180.34 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 180.35 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 192.34 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10203 | 113.2 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17709 | 108.46 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17709 | 108.46 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17726 | 107.93 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17726 | 107.93 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17729 | 107.93 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17729 | 108.31 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.6 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.64 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.64 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.65 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.65 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.84 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.91 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.93 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.93 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.93 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.08 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.09 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.1 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.14 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.14 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.24 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.26 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.26 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.31 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.33 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.34 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.34 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.36 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.38 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.38 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.43 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.43 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.47 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.48 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.57 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.58 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.59 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.59 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.6 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.6 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.6 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.61 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.62 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.62 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.65 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.65 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.66 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.67 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.69 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.73 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.78 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.82 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.9 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.9 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.94 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.94 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.96 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.26 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.26 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.26 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.33 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.33 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.38 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 110.13 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 110.7 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 113.2 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17736 | 108.15 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17737 | 108.15 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 108.2 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 108.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 108.27 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17739 | 107.43 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17739 | 107.43 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1774 | 108.34 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1774 | 108.34 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17748 | 108.22 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17752 | 108.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17757 | 108.38 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17757 | 108.38 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 108.64 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17767 | 108.5 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17778 | 108.87 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17778 | 108.87 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1783 | 110.2 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17831 | 110.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17831 | 110.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17841 | 109.88 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17841 | 109.88 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17845 | 109.68 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17845 | 109.73 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17853 | 109.48 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17858 | 110.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 111.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 110.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 110.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17976 | 110.52 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17997 | 112.33 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17999 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17999 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18023 | 111.45 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18023 | 111.45 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18104 | 114.65 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18111 | 114.7 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18127 | 115.03 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18127 | 115.03 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18237 | 115.2 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18285 | 110.28 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18418 | 115.8 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18418 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19039 | 121.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19039 | 121.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19703 | 122.24 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20217 | 139.23 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 132.76 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 135.94 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 136.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 140.37 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 140.41 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2936 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15797 | 100.26 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15797 | 100.26 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15893 | 100.4 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1605 | 100.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1605 | 101.05 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16592 | 105.57 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16592 | 106.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17171 | 106.54 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17618 | 121.34 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 111.55 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 115.7 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 118.48 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 118.89 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 121.6 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 122.33 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 122.37 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 123.4 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 102.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 104.7 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 104.7 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28327 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10263 | 116.16 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10278 | 106.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 104.1 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 107.2 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 111.56 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 112.2 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 116.48 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 117.09 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 117.11 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 118.06 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11545 | 111.48 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1153 | 107.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1153 | 107.29 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0854 | 104.57 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08544 | 106.59 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08545 | 106.62 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08567 | 103.97 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08568 | 106.9 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08575 | 106.53 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08581 | 103.66 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 103.29 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08603 | 103.13 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08614 | 103.65 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08614 | 103.65 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08615 | 102.88 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08615 | 103.12 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08621 | 102.89 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08628 | 103.45 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0863 | 102.64 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.47 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.47 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.48 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.5 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.65 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.91 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.1 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.11 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.18 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.18 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.18 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.19 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.2 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.35 | GEN-2023-116_POI_640252_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.44 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.51 | P15:230:UMZB:# 2982 #:: DHC IN NE. STEGALL DC CONVERTER STATION AND SHUNT DEVICE:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.54 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.63 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.93 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.98 | P23:345:XEL:8P2 KING | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.01 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.02 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.06 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.12 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.12 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.3 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.07 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.12 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.13 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.2 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.26 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.43 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.44 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.53 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.64 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.79 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 111.13 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0864 | 102.76 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08641 | 102.54 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08641 | 102.66 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08642 | 102.73 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08642 | 102.76 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08643 | 102.91 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08643 | 103.18 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08643 | 103.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08643 | 103.18 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08643 | 103.23 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08644 | 102.54 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08644 | 102.61 | P12:345:AMMO::MAYWOOD:SUBT:77 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08645 | 103.82 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 102.76 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 102.79 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 103.18 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 103.28 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08651 | 103.23 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08651 | 103.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08651 | 103.58 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08653 | 103.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08655 | 102.61 | 300143 4VALLEY 138 514830 FITZGRD4 138 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08656 | 102.86 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08657 | 103.04 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08657 | 103.52 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08657 | 103.52 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08658 | 104.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08661 | 103.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08662 | 103.26 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08663 | 103.02 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08664 | 104.57 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08666 | 104.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08668 | 102.79 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08669 | 103.74 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08669 | 103.74 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0869 | 103.57 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08692 | 102.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.087 | 103.37 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08706 | 103.75 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08706 | 103.75 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08734 | 103.64 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08738 | 103.24 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08749 | 103.95 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08749 | 103.95 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08753 | 104.88 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08758 | 103.64 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08768 | 111.11 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08816 | 104.13 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08816 | 104.13 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0882 | 105.73 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0882 | 105.73 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08822 | 103.92 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08822 | 103.92 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08822 | 103.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08841 | 104.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08841 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08841 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08892 | 105.91 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08892 | 105.96 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08902 | 105.39 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0891 | 105.24 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08929 | 103.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08929 | 104.57 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08973 | 103.35 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09008 | 108.66 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09048 | 106.49 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09048 | 106.62 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09048 | 106.74 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09048 | 108.72 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09148 | 108.81 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09376 | 108.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09455 | 111.24 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09664 | 119.41 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09664 | 119.41 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09664 | 119.41 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09664 | 119.41 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09664 | 119.41 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10434 | 124.17 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10434 | 124.17 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10434 | 124.17 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10946 | 124.55 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10946 | 124.55 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10946 | 124.55 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11275 | 134.94 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11275 | 134.94 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09919 | 104.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09919 | 104.23 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09919 | 104.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09919 | 104.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09919 | 104.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10689 | 109.24 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10689 | 109.24 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10689 | 109.24 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11201 | 109.9 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11201 | 109.9 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11201 | 109.9 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1153 | 121.32 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1153 | 121.32 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13 | 111.5 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13888 | 102.83 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13888 | 102.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13888 | 102.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13915 | 103.68 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13915 | 103.68 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.1395 | 104.16 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17344 | 114.4 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17719 | 107.58 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18762 | 107.83 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18762 | 108.41 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18762 | 108.41 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18788 | 109.17 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18788 | 109.17 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18824 | 109.67 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.11 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.11 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.11 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.12 | ASGI-2011-004_POI_525915_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.17 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.33 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.59 | GEN-2011-025_POI_525803_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.64 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 101.04 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 101.04 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 101.04 | GEN-2023-086_POI_773700_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 103.21 | 774381 GEN-2023-120 115 774382 G23-120XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 103.21 | GEN-2023-120_POI_525192_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 105.36 | 524757 BETHEL_COL 3 115 524755 BETHEL_COL11 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 106.65 | GEN-2014-040_POI_524746_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07656 | 100.11 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07656 | 100.11 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0766 | 100.13 | 515375 WWRDEHV7 345 516059 BECKHAM7 345 2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07661 | 100.84 | Potential P4 Event - POI 776000_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07662 | 100.19 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07662 | 100.25 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07662 | 100.29 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07662 | 100.29 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07662 | 100.31 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07663 | 100.19 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07665 | 100.32 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07665 | 100.32 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07678 | 100.67 | POI 515800_22 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07678 | 100.69 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07682 | 102.94 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07725 | 101.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07725 | 102.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 103.85 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 104.28 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 105.13 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 105.26 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07843 | 102.17 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07935 | 103.83 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08031 | 105.78 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08139 | 118.93 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09004 | 115.77 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09004 | 116.09 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 116.35 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 116.35 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09015 | 116.49 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09265 | 117.56 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09265 | 120.95 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.10347 | 127.17 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.66 | 524757 BETHEL_COL 3 115 524756 BETHEL_COL21 34.5 2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 101.52 | 774381 GEN-2023-120 115 774382 G23-120XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 101.52 | GEN-2023-120_POI_525192_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 103.4 | 524757 BETHEL_COL 3 115 524755 BETHEL_COL11 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 105.44 | GEN-2014-040_POI_524746_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07682 | 101.12 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07725 | 100.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07725 | 100.64 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 102.3 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 102.76 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 103.7 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 103.84 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07935 | 102.14 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08031 | 104.12 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08139 | 118.92 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09004 | 114.41 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09004 | 114.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 115.06 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 115.06 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09015 | 115.22 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09265 | 115.67 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09265 | 119.13 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.10347 | 125.32 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.11102 | 138.46 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1502 | 134.22 | 560022 CRAWFISH_DR 345 774180 G23-110-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15121 | 134.27 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15121 | 134.32 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15122 | 134.67 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.02 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.07 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.08 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.08 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.09 | P23:345:XEL:8N17 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.09 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.1 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.62 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.65 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.65 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.67 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.7 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.7 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.71 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.71 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.74 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.74 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.75 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.77 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.8 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.81 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.87 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.88 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.88 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.88 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.89 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.89 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.9 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.91 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.91 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.91 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.93 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.93 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.94 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.95 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.03 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.05 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.11 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.11 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.12 | P11:21:EES:RVB:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.12 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.12 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.14 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.14 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.17 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.19 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.19 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.19 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.44 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.44 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.5 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.67 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.67 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.67 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 136.51 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 138.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15125 | 134.33 | 539784 ENSNGW 3 115 3WXFMR ENSIGN WIND 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.35 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.36 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.36 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.36 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.58 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.58 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15127 | 134.62 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15127 | 134.68 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15127 | 134.68 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15128 | 133.94 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15128 | 134.74 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15128 | 134.74 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15132 | 134.64 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15135 | 134.82 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15136 | 134.89 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15138 | 134.81 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15138 | 134.81 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15138 | 134.81 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15138 | 134.81 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15142 | 134.86 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15149 | 135.18 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15149 | 135.18 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15175 | 136.3 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15176 | 136.26 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15176 | 136.26 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15181 | 136.03 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15181 | 136.03 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15184 | 135.85 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15184 | 135.9 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1519 | 136.2 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15191 | 135.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15216 | 136.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15225 | 136.42 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15225 | 136.42 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15237 | 137.2 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15258 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15259 | 136.64 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15259 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15321 | 140.07 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15324 | 140.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15333 | 140.41 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15333 | 140.41 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15386 | 140.35 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15504 | 141.43 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15504 | 141.57 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15736 | 138.37 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15747 | 138.2 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15801 | 138.53 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15893 | 146.73 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15893 | 147.76 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16243 | 142.55 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 150.42 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 154 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 156.76 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 157.19 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 159.91 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 161.9 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16762 | 148.33 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17038 | 159.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1998 | 162.73 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1998 | 164.74 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1998 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19991 | 165.01 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19991 | 165.01 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20014 | 165.4 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.2073 | 114.05 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.2073 | 114.9 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10203 | 112.47 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17709 | 108.23 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17709 | 108.23 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17726 | 107.69 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17726 | 107.69 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17729 | 107.69 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17729 | 108.08 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.35 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.38 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.39 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.4 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.4 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.4 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.6 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.69 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.84 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.85 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.86 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.88 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.88 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.02 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.02 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.08 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.1 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.1 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.1 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.12 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.15 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.15 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.19 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.2 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.23 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.34 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.35 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.36 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.36 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.37 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.37 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.37 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.38 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.39 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.39 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.42 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.42 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.43 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.44 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.45 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.5 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.55 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.59 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.67 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.67 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.69 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.69 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.69 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.71 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.71 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.73 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.78 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.78 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.78 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.91 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.91 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.91 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.96 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.97 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.99 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.92 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.95 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 110.21 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 110.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 112.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17735 | 107.69 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17735 | 107.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17735 | 107.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17736 | 107.91 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17737 | 107.91 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 107.96 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 108.02 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 108.03 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17739 | 107.18 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1774 | 108.11 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1774 | 108.11 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17748 | 107.98 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17752 | 108.21 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17757 | 108.21 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17757 | 108.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 108.41 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17767 | 108.27 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17778 | 108.64 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17778 | 108.64 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1783 | 110.01 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17831 | 109.95 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17831 | 109.95 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17841 | 109.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17841 | 109.68 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17845 | 109.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17845 | 109.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17853 | 109.29 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17858 | 109.91 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 111 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 110.26 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 110.27 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17976 | 110.36 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17997 | 112.06 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17999 | 110.39 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18023 | 111.18 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18023 | 111.18 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18104 | 114.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18111 | 114.62 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18127 | 114.95 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18127 | 114.95 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18237 | 115.01 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18418 | 115.82 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18418 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19039 | 120.81 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19039 | 121.59 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19703 | 121.87 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20217 | 136.58 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 130.57 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 133.59 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 134.05 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 137.75 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 137.78 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2936 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15797 | 100.18 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15797 | 100.18 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15893 | 100.23 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1605 | 100.94 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1605 | 101.06 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16592 | 105.29 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16592 | 105.97 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17171 | 106.21 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17618 | 119.03 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 110.17 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 113.79 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 116.43 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 116.82 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 119.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 120.05 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 120.08 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 121.11 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 101.8 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 103.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 103.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28327 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1132 | 100.95 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2206 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22083 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2236 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22378 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22589 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.226 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22616 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22621 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22622 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22626 | 101.44 | Potential P4 Event - POI 523823_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22771 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22855 | 104.75 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22861 | 104.09 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22861 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23058 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24019 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24771 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26243 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37835 | 152.61 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41566 | 184.51 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41702 | 183.79 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 179.87 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 179.92 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 191.94 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22037 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24078 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37802 | 153.1 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41526 | 184.91 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4166 | 184.16 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 180.34 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 180.35 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 192.34 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10203 | 113.2 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17709 | 108.46 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17709 | 108.46 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17726 | 107.93 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17726 | 107.93 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17729 | 107.93 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17729 | 108.31 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.6 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.64 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.64 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.65 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.65 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.84 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.91 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.93 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.93 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.93 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.08 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.09 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.1 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.14 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.14 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.24 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.26 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.26 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.31 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.33 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.34 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.34 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.36 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.38 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.38 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.43 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.43 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.47 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.48 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.57 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.58 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.59 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.59 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.6 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.6 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.6 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.61 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.62 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.62 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.65 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.65 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.66 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.67 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.69 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.73 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.78 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.82 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.9 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.9 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.94 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.94 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.96 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.26 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.26 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.26 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.33 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.33 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.38 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 110.13 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 110.7 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 113.2 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17736 | 108.15 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17737 | 108.15 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 108.2 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 108.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 108.27 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17739 | 107.43 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17739 | 107.43 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1774 | 108.34 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1774 | 108.34 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17748 | 108.22 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17752 | 108.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17757 | 108.38 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17757 | 108.38 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 108.64 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17767 | 108.5 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17778 | 108.87 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17778 | 108.87 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1783 | 110.2 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17831 | 110.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17831 | 110.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17841 | 109.88 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17841 | 109.88 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17845 | 109.68 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17845 | 109.73 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17853 | 109.48 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17858 | 110.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 111.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 110.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 110.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17976 | 110.52 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17997 | 112.33 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17999 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17999 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18023 | 111.45 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18023 | 111.45 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18104 | 114.65 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18111 | 114.7 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18127 | 115.03 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18127 | 115.03 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18237 | 115.2 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18285 | 110.28 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18418 | 115.8 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18418 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19039 | 121.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19039 | 121.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19703 | 122.24 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20217 | 139.23 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 132.76 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 135.94 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 136.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 140.37 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 140.41 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2936 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15797 | 100.26 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15797 | 100.26 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15893 | 100.4 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1605 | 100.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1605 | 101.05 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16592 | 105.57 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16592 | 106.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17171 | 106.54 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17618 | 121.34 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 111.55 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 115.7 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 118.48 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 118.89 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 121.6 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 122.33 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 122.37 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 123.4 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 102.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 104.7 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 104.7 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28327 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10263 | 116.16 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10278 | 106.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 104.1 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 107.2 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 111.56 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 112.2 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 116.48 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 117.09 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 117.11 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 118.06 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11545 | 111.48 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11463 | 107.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11463 | 107.29 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08476 | 104.57 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0848 | 106.59 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08481 | 106.62 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08503 | 103.97 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08504 | 106.9 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 106.53 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08517 | 103.66 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08533 | 103.29 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08538 | 103.13 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08549 | 103.65 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0855 | 103.65 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08551 | 102.88 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08551 | 103.12 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08557 | 102.89 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08564 | 103.45 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08565 | 102.64 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 102.47 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 102.47 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 102.5 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 102.65 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 102.91 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.1 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.11 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.18 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.18 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.18 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.19 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.2 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.35 | GEN-2023-116_POI_640252_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.44 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.51 | P15:230:UMZB:# 2982 #:: DHC IN NE. STEGALL DC CONVERTER STATION AND SHUNT DEVICE:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.54 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.63 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.93 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.98 | P23:345:XEL:8P2 KING | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 104 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 104.01 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 104.02 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 104.06 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 104.12 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 104.12 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 104.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 104.3 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.12 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.2 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.26 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.43 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.44 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.53 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.64 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.79 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 111.13 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08574 | 102.48 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08574 | 105.07 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08574 | 105.13 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08574 | 105.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08576 | 102.76 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08577 | 102.54 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08577 | 102.66 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08578 | 102.73 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08578 | 102.76 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08578 | 102.91 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08578 | 103.18 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08578 | 103.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08578 | 103.18 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08579 | 102.54 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08579 | 103.23 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0858 | 102.61 | P12:345:AMMO::MAYWOOD:SUBT:77 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08581 | 103.82 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08582 | 102.76 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08585 | 102.79 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08585 | 103.18 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08585 | 103.28 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08586 | 103.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08587 | 103.23 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08587 | 103.58 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08589 | 103.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0859 | 102.61 | 300143 4VALLEY 138 514830 FITZGRD4 138 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08592 | 102.86 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.04 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.52 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.52 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 104.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 103.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08598 | 103.26 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08599 | 103.02 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.086 | 104.57 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08602 | 104.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08604 | 102.79 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08605 | 103.74 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08605 | 103.74 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08626 | 103.57 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08628 | 102.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08636 | 103.37 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08642 | 103.75 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08642 | 103.75 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08661 | 103.24 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0867 | 103.64 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08683 | 103.95 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08683 | 103.95 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0869 | 104.88 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08694 | 103.64 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08703 | 111.11 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08753 | 104.13 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08753 | 104.13 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08756 | 105.73 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08756 | 105.73 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08758 | 103.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08759 | 103.92 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08759 | 103.92 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08779 | 104.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08779 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08779 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08821 | 105.91 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08821 | 105.96 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08838 | 105.39 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08846 | 105.24 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0894 | 103.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0894 | 104.57 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08941 | 108.66 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08947 | 103.35 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08981 | 106.49 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08981 | 106.62 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08981 | 106.74 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08981 | 108.72 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09082 | 108.81 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09322 | 108.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0939 | 111.24 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09592 | 119.41 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09592 | 119.41 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09592 | 119.41 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09592 | 119.41 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09592 | 119.41 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10326 | 124.17 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10326 | 124.17 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10326 | 124.17 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10879 | 124.55 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10879 | 124.55 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10879 | 124.55 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11209 | 134.94 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11209 | 134.94 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09847 | 104.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09847 | 104.23 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09847 | 104.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09847 | 104.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09847 | 104.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1058 | 109.24 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1058 | 109.24 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1058 | 109.24 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11134 | 109.9 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11134 | 109.9 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11134 | 109.9 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11463 | 121.32 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11463 | 121.32 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.09938 | 111.5 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10663 | 102.83 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10663 | 102.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10663 | 102.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10697 | 103.68 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10697 | 103.68 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10741 | 104.16 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13183 | 114.4 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13479 | 107.58 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14443 | 107.83 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14443 | 108.41 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14443 | 108.41 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14477 | 109.17 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14477 | 109.17 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14522 | 109.67 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0509 | 117.56 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0509 | 120.95 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05398 | 115.77 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05398 | 116.09 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05404 | 116.35 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05404 | 116.35 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05413 | 116.49 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05864 | 127.17 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0509 | 115.67 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0509 | 119.13 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05398 | 114.41 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05398 | 114.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05404 | 115.06 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05404 | 115.06 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05413 | 115.22 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05864 | 125.32 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.12825 | 138.46 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16739 | 134.22 | 560022 CRAWFISH_DR 345 774180 G23-110-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16844 | 134.27 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16844 | 134.32 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.02 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.07 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.08 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.08 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.09 | P23:345:XEL:8N17 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.09 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.1 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.62 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.65 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.65 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.67 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.67 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.7 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.7 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.71 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.71 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.74 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.74 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.75 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.77 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.8 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.81 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.87 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.88 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.88 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.88 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.89 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.89 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.9 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.91 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.91 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.91 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.93 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.93 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.94 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.95 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.03 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.05 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.11 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.11 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.12 | P11:21:EES:RVB:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.12 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.12 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.14 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.14 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.17 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.19 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.19 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.19 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.44 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.44 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.5 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.67 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.67 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.67 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 136.51 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 138.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16848 | 134.33 | 539784 ENSNGW 3 115 3WXFMR ENSIGN WIND 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16849 | 134.35 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16849 | 134.36 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16849 | 134.36 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16849 | 134.36 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16849 | 134.58 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16849 | 134.58 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1685 | 134.62 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1685 | 134.68 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1685 | 134.68 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16851 | 133.94 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16851 | 134.74 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16851 | 134.74 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16854 | 134.64 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16857 | 134.82 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16858 | 134.89 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16861 | 134.81 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16861 | 134.81 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16861 | 134.81 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16861 | 134.81 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16865 | 134.86 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16871 | 135.18 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16871 | 135.18 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16898 | 136.3 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16899 | 136.26 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16899 | 136.26 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16903 | 136.03 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16903 | 136.03 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16906 | 135.85 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16906 | 135.9 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16912 | 136.2 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16914 | 135.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16925 | 136.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16935 | 136.42 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16935 | 136.42 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1696 | 137.2 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16982 | 136.64 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16982 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16982 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17042 | 140.07 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17046 | 140.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17054 | 140.41 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17054 | 140.41 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17103 | 140.35 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17164 | 138.37 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17225 | 141.43 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17225 | 141.57 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17506 | 138.2 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17563 | 138.53 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17626 | 146.73 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17626 | 147.76 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1831 | 148.33 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18559 | 150.42 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18559 | 154 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18559 | 156.76 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18559 | 157.19 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18559 | 159.91 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18559 | 161.9 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19091 | 159.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19813 | 142.55 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21984 | 162.73 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21984 | 164.74 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21984 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21999 | 165.01 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21999 | 165.01 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22027 | 165.4 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21929 | 114.05 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21929 | 114.9 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09198 | 112.47 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16703 | 108.23 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16703 | 108.23 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16721 | 107.69 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16721 | 107.69 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16723 | 107.69 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16723 | 108.08 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.35 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.38 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.39 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.4 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.4 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.4 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.6 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.69 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.84 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.85 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.86 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.88 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.88 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.02 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.02 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.08 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.1 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.1 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.1 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.12 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.15 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.15 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.19 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.2 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.23 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.34 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.35 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.36 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.36 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.37 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.37 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.37 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.38 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.39 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.39 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.42 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.42 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.43 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.44 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.45 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.5 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.55 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.59 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.67 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.67 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.69 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.69 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.69 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.71 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.71 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.73 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.78 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.78 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.78 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.91 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.91 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.91 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.96 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.97 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.99 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 109.92 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 109.95 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 110.21 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 110.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 112.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1673 | 107.69 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1673 | 107.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1673 | 107.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16731 | 107.91 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16731 | 107.91 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16733 | 107.96 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16733 | 108.02 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16733 | 108.03 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16734 | 107.18 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16734 | 108.11 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16734 | 108.11 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16742 | 107.98 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16746 | 108.21 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16752 | 108.21 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16752 | 108.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16755 | 108.41 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16761 | 108.27 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16773 | 108.64 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16773 | 108.64 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16824 | 110.01 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16825 | 109.95 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16825 | 109.95 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16834 | 109.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16834 | 109.68 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16839 | 109.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16839 | 109.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16847 | 109.29 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16851 | 109.91 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16894 | 110.39 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1693 | 111 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16954 | 112.06 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16961 | 110.26 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16961 | 110.27 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1697 | 110.36 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1698 | 111.18 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1698 | 111.18 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17095 | 114.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17103 | 114.62 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17118 | 114.95 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17118 | 114.95 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17219 | 115.01 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1741 | 115.82 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1741 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18051 | 120.81 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18051 | 121.59 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19038 | 121.87 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19881 | 136.58 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 130.57 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 133.59 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 134.05 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 137.75 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 137.78 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20463 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20463 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20463 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.27695 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14918 | 100.18 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14918 | 100.18 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15006 | 100.23 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15172 | 100.94 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15172 | 101.06 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15731 | 105.29 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15731 | 105.97 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16591 | 106.21 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17326 | 119.03 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 110.17 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 113.79 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 116.43 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 116.82 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 119.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 120.05 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 120.08 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 121.11 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17833 | 101.8 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17833 | 103.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17833 | 103.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.26721 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11569 | 100.95 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22309 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22572 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22582 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22608 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22834 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22844 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2286 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22865 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22866 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22871 | 101.44 | Potential P4 Event - POI 523823_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23002 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23098 | 104.75 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23104 | 104.09 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23104 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23303 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24294 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25177 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27211 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37207 | 152.61 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4202 | 184.51 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42171 | 183.79 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42542 | 179.87 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42542 | 179.92 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42542 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42542 | 191.94 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22289 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24966 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37174 | 153.1 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41979 | 184.91 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42128 | 184.16 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42498 | 180.34 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42498 | 180.35 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42498 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42498 | 192.34 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09198 | 113.2 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16703 | 108.46 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16703 | 108.46 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16721 | 107.93 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16721 | 107.93 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16723 | 107.93 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16723 | 108.31 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.6 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.64 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.64 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.65 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.65 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.84 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.91 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.93 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.93 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.93 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.08 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.09 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.1 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.14 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.14 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.24 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.26 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.26 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.31 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.33 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.34 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.34 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.36 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.38 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.38 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.43 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.43 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.47 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.48 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.57 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.58 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.59 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.59 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.6 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.6 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.6 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.61 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.62 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.62 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.65 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.65 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.66 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.67 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.69 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.73 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.78 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.82 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.9 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.9 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.94 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.94 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.96 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 109 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 109 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 109.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 109.26 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 109.26 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 109.26 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 109.33 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 109.33 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 109.38 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 110.13 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 110.7 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 113.2 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16731 | 108.15 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16731 | 108.15 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16733 | 108.2 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16733 | 108.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16733 | 108.27 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16734 | 107.43 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16734 | 107.43 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16734 | 108.34 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16734 | 108.34 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16742 | 108.22 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16746 | 108.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16752 | 108.38 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16752 | 108.38 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16755 | 108.64 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16761 | 108.5 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16773 | 108.87 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16773 | 108.87 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16824 | 110.2 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16825 | 110.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16825 | 110.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16834 | 109.88 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16834 | 109.88 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16839 | 109.68 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16839 | 109.73 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16847 | 109.48 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16851 | 110.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16894 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16894 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1693 | 111.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16954 | 112.33 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16961 | 110.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16961 | 110.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1697 | 110.52 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1698 | 111.45 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1698 | 111.45 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17095 | 114.65 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17103 | 114.7 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17118 | 115.03 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17118 | 115.03 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17219 | 115.2 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1741 | 115.8 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1741 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18051 | 121.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18051 | 121.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18194 | 110.28 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19038 | 122.24 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19881 | 139.23 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 132.76 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 135.94 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 136.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 140.37 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 140.41 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20463 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20463 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20463 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.27695 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14918 | 100.26 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14918 | 100.26 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15006 | 100.4 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15172 | 100.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15172 | 101.05 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15731 | 105.57 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15731 | 106.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16591 | 106.54 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17326 | 121.34 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 111.55 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 115.7 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 118.48 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 118.89 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 121.6 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 122.33 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 122.37 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 123.4 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17833 | 102.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17833 | 104.7 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17833 | 104.7 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.26721 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09635 | 106.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09767 | 116.16 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09806 | 104.1 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09806 | 107.2 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09806 | 111.56 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09806 | 112.2 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09806 | 116.48 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09806 | 117.09 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09806 | 117.11 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09806 | 118.06 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10952 | 111.48 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11463 | 107.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11463 | 107.29 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08476 | 104.57 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0848 | 106.59 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08481 | 106.62 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08503 | 103.97 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08504 | 106.9 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 106.53 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08517 | 103.66 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08533 | 103.29 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08538 | 103.13 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08549 | 103.65 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0855 | 103.65 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08551 | 102.88 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08551 | 103.12 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08557 | 102.89 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08564 | 103.45 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08565 | 102.64 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 102.47 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 102.47 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 102.5 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 102.65 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 102.91 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.1 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.11 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.18 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.18 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.18 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.19 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.2 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.35 | GEN-2023-116_POI_640252_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.44 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.51 | P15:230:UMZB:# 2982 #:: DHC IN NE. STEGALL DC CONVERTER STATION AND SHUNT DEVICE:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.54 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.63 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.93 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.98 | P23:345:XEL:8P2 KING | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 104 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 104.01 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 104.02 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 104.06 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 104.12 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 104.12 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 104.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 104.3 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.12 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.2 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.26 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.43 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.44 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.53 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.64 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.79 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 105.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 111.13 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08574 | 102.48 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08574 | 105.07 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08574 | 105.13 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08574 | 105.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08576 | 102.76 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08577 | 102.54 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08577 | 102.66 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08578 | 102.73 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08578 | 102.76 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08578 | 102.91 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08578 | 103.18 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08578 | 103.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08578 | 103.18 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08579 | 102.54 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08579 | 103.23 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0858 | 102.61 | P12:345:AMMO::MAYWOOD:SUBT:77 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08581 | 103.82 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08582 | 102.76 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08585 | 102.79 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08585 | 103.18 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08585 | 103.28 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08586 | 103.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08587 | 103.23 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08587 | 103.58 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08589 | 103.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0859 | 102.61 | 300143 4VALLEY 138 514830 FITZGRD4 138 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08592 | 102.86 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.04 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.52 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.52 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 104.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 103.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08598 | 103.26 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08599 | 103.02 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.086 | 104.57 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08602 | 104.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08604 | 102.79 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08605 | 103.74 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08605 | 103.74 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08626 | 103.57 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08628 | 102.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08636 | 103.37 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08642 | 103.75 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08642 | 103.75 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08661 | 103.24 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0867 | 103.64 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08683 | 103.95 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08683 | 103.95 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0869 | 104.88 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08694 | 103.64 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08703 | 111.11 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08753 | 104.13 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08753 | 104.13 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08756 | 105.73 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08756 | 105.73 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08758 | 103.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08759 | 103.92 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08759 | 103.92 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08779 | 104.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08779 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08779 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08821 | 105.91 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08821 | 105.96 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08838 | 105.39 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08846 | 105.24 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0894 | 103.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0894 | 104.57 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08941 | 108.66 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08947 | 103.35 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08981 | 106.49 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08981 | 106.62 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08981 | 106.74 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08981 | 108.72 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09082 | 108.81 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line