Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04393 | 110.15 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04692 | 124.39 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04692 | 124.74 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04692 | 124.74 | Potential P4 Event - POI 515458_6 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04692 | 124.74 | Potential P4 Event - POI 515458_9 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04692 | 124.74 | Potential P4 Event - POI 774180_0 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04692 | 124.74 | Potential P4 Event - POI 774180_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04692 | 125.13 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.06015 | 118.5 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.06548 | 117.79 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.06548 | 117.79 | Potential P4 Event - POI 514801_3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.06664 | 117.86 | Potential P4 Event - POI 514801_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-150 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.06812 | 117.39 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-151 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.18049 | 116.97 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-151 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.18049 | 116.97 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-151 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.18049 | 116.97 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-153 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.04591 | 100.16 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-153 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.04591 | 100.16 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-153 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.04591 | 101.46 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-153 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.04591 | 101.57 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-153 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.05649 | 102.18 | Potential P4 Event - POI 659105_8 | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-153 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.05664 | 100.55 | 659105 LELAND_O-BE3 345 659424 LO.LS-CC-BE3 345 Z | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-153 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.05664 | 100.61 | 659424 LO.LS-CC-BE3 345 764220 G20-021-TAP 345 1 | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-153 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.05664 | 100.61 | P12:345:UMZB:# 7129 #:: CHA IN SD. LOS - CHAPPELLE CREEK 345:EHV: | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-153 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.05664 | 100.61 | P14:345:UMZ:# 7213 #:: PROPER TAKE LINE WITH LELAND OLDS-FORT THOMPSON LINE REACTOR:EHV: | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-153 | FROM->TO | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 239 | 239 | 0.06196 | 107.96 | Potential P4 Event - POI 659105_15 | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-153 | FROM->TO | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z | 239 | 239 | 0.06196 | 100.31 | Potential P4 Event - POI 659105_15 | TDF Impact | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06155 | 112.6 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06155 | 112.6 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06155 | 112.6 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06155 | 112.6 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06155 | 113.1 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06155 | 113.13 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06155 | 113.14 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06155 | 113.18 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06155 | 119.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20397 | 145.76 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 134.94 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.16 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.17 | 546653 NEARMAN5 161 772721 GEN-2023-037 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.17 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.17 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.18 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.18 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.18 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.19 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.19 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.19 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.22 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.22 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.22 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.22 | GEN-2006-002_POI_511541_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.22 | P11:20:AMMO:1LAB G1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.22 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.22 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.23 | P13:MR#2 GSU | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.24 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.24 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.24 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.25 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.26 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.27 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.27 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.27 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.28 | 640588 TURTLE.CRK 3 345 640589 SHOLES.W 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.29 | P11:024:DPC:ALMA2:6 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.3 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.32 | P11:345:WERE:EMPR5-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.33 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.35 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.36 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.38 | P23:345:XEL:8H14 PRI | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.39 | P23:345:XEL:8H17 PRI AS | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.41 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.42 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.45 | P23:345:XEL:8N22 SHC | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.48 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.48 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.49 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.49 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.49 | P23:345:MEC:CBEC 908 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.5 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.51 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.54 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.54 | P23:345:MEC:CBEC 905 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.56 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.59 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.59 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.59 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.61 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.62 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.63 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.67 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.67 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.86 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 136.95 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 136.95 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 146.51 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 146.51 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 146.51 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25228 | 135.32 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25229 | 135.37 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25233 | 135.34 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25271 | 137.79 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25271 | 138.43 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25292 | 139.57 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25307 | 136.71 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25416 | 139.08 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25416 | 139.08 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25416 | 139.13 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25564 | 140.1 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26248 | 141 | P12:115:SPS:V37_1_CASTRO_PLANTX:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26262 | 143.43 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26373 | 145.25 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26373 | 145.32 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26373 | 145.32 | Potential P4 Event - POI 774180_0 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26373 | 145.32 | Potential P4 Event - POI 774180_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26517 | 141.81 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26554 | 150.33 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.27184 | 157.27 | Potential P4 Event - POI 762216_14 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.27184 | 157.27 | Potential P4 Event - POI 762467_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.27191 | 152.27 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.27191 | 152.28 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.27191 | 152.28 | Potential P4 Event - POI 525832_2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.27191 | 152.28 | Potential P4 Event - POI 525832_5 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29731 | 174.44 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.32103 | 170.16 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.09941 | 110.28 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-158 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.09941 | 109.5 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06155 | 112.6 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06155 | 112.6 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06155 | 112.6 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06155 | 112.6 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06155 | 113.1 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06155 | 113.13 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06155 | 113.14 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06155 | 113.18 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06155 | 119.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20397 | 145.76 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 134.94 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.16 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.17 | 546653 NEARMAN5 161 772721 GEN-2023-037 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.17 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.17 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.18 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.18 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.18 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.19 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.19 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.19 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.22 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.22 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.22 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.22 | GEN-2006-002_POI_511541_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.22 | P11:20:AMMO:1LAB G1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.22 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.22 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.23 | P13:MR#2 GSU | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.24 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.24 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.24 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.25 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.26 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.27 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.27 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.27 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.28 | 640588 TURTLE.CRK 3 345 640589 SHOLES.W 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.29 | P11:024:DPC:ALMA2:6 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.3 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.32 | P11:345:WERE:EMPR5-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.33 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.35 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.36 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.38 | P23:345:XEL:8H14 PRI | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.39 | P23:345:XEL:8H17 PRI AS | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.41 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.42 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.45 | P23:345:XEL:8N22 SHC | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.48 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.48 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.49 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.49 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.49 | P23:345:MEC:CBEC 908 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.5 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.51 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.54 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.54 | P23:345:MEC:CBEC 905 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.56 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.59 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.59 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.59 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.61 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.62 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.63 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.67 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.67 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 135.86 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 136.95 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 136.95 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 146.51 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 146.51 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25227 | 146.51 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25228 | 135.32 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25229 | 135.37 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25233 | 135.34 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25271 | 137.79 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25271 | 138.43 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25292 | 139.57 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25307 | 136.71 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25416 | 139.08 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25416 | 139.08 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25416 | 139.13 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25564 | 140.1 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26248 | 141 | P12:115:SPS:V37_1_CASTRO_PLANTX:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26262 | 143.43 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26373 | 145.25 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26373 | 145.32 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26373 | 145.32 | Potential P4 Event - POI 774180_0 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26373 | 145.32 | Potential P4 Event - POI 774180_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26517 | 141.81 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26554 | 150.33 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.27184 | 157.27 | Potential P4 Event - POI 762216_14 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.27184 | 157.27 | Potential P4 Event - POI 762467_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.27191 | 152.27 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.27191 | 152.28 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.27191 | 152.28 | Potential P4 Event - POI 525832_2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.27191 | 152.28 | Potential P4 Event - POI 525832_5 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29731 | 174.44 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.32103 | 170.16 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.09941 | 110.28 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-159 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.09941 | 109.5 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 169 | 169 | 0.04675 | 100.24 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 169 | 169 | 0.04675 | 100.24 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 169 | 169 | 0.04737 | 100.32 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 169 | 169 | 0.04737 | 100.32 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 169 | 169 | 0.05758 | 101.52 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 169 | 169 | 0.05758 | 101.52 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59034 | 112.6 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59034 | 112.6 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59034 | 112.6 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59034 | 112.6 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59034 | 113.1 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59034 | 113.13 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59034 | 113.14 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59034 | 113.18 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59034 | 119.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.41439 | 102.79 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.41439 | 102.79 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.41439 | 103.02 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.41439 | 103.02 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 183 | 201 | 0.07687 | 100.32 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 183 | 201 | 0.07687 | 100.32 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.0586 | 101.26 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.0586 | 101.26 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.05939 | 101.28 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.05939 | 101.28 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.06052 | 100.04 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.06052 | 100.04 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.07687 | 103.56 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.07687 | 103.56 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03707 | 105.47 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03716 | 106.36 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03827 | 107.1 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03827 | 107.1 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03879 | 103.34 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03879 | 103.45 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.15 | 300120 5THMHILB1 161 301504 5THOMHLGSU1 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.15 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.16 | 344011 7HUGHES 345 344012 7HPW-N 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.17 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.2 | P21:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.22 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.24 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.26 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.26 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.28 | 546653 NEARMAN5 161 772721 GEN-2023-037 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.28 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.3 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.3 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.3 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.32 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.34 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.37 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.37 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.38 | P11:20:AMMO:1LAB G1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.38 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.41 | P13:MR#2 GSU | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.42 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.42 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.44 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.46 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.47 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.49 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.53 | 640588 TURTLE.CRK 3 345 640589 SHOLES.W 3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.54 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.55 | P11:024:DPC:ALMA2:6 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.66 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.71 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.78 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.79 | 773981 GEN-2023-100 345 773985 G23-100XFMR2 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.79 | P23:345:XEL:8H14 PRI | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.8 | P23:345:XEL:8H17 PRI AS | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.84 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.88 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.96 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.96 | P23:345:XEL:8N22 SHC | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.02 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.03 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.04 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.05 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.05 | P23:345:MEC:CBEC 908 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.07 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.11 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.17 | P23:345:MEC:CBEC 905 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.18 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.23 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.3 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.3 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.31 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.38 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.39 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.41 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.69 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.7 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.77 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 105.07 | 772281 GEN-2023-015 345 772282 G23-015XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 105.67 | GEN-2008-051_POI_523961_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 107.37 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03881 | 103.25 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03882 | 103.09 | P12:HV:EES::3COUCH%:3LEWISVILLE#:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03882 | 103.37 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03883 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03885 | 103.62 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03935 | 106.98 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03972 | 103.84 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04858 | 108.56 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04858 | 108.56 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04858 | 108.6 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04858 | 109.91 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05182 | 123.96 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05182 | 124.18 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05182 | 124.18 | Potential P4 Event - POI 515458_6 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05182 | 124.18 | Potential P4 Event - POI 515458_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05182 | 124.18 | Potential P4 Event - POI 774180_0 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05182 | 124.18 | Potential P4 Event - POI 774180_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05182 | 124.51 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.06857 | 118.76 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.08166 | 118.05 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.08166 | 118.05 | Potential P4 Event - POI 514801_4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.08282 | 118.14 | Potential P4 Event - POI 514801_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0843 | 117.64 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03707 | 105.98 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03716 | 106.81 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03827 | 107.82 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03827 | 107.83 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03879 | 104 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03879 | 104.12 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.81 | 300120 5THMHILB1 161 301504 5THOMHLGSU1 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.81 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.82 | 344011 7HUGHES 345 344012 7HPW-N 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.84 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.87 | P21:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.89 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.9 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.92 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.92 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.94 | 546653 NEARMAN5 161 772721 GEN-2023-037 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.94 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.96 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.96 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.96 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.99 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.01 | P23:345:OTP::TWIN BRKS 3:BRKY_V2021:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.02 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.02 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.04 | P11:20:AMMO:1LAB G1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.04 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.08 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.08 | P13:MR#2 GSU | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.09 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.11 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.13 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.14 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.16 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.17 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.19 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.2 | 640588 TURTLE.CRK 3 345 640589 SHOLES.W 3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.22 | P11:024:DPC:ALMA2:6 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.33 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.37 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.44 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.44 | P23:345:XEL:8H14 PRI | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.45 | 773981 GEN-2023-100 345 773985 G23-100XFMR2 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.46 | P23:345:XEL:8H17 PRI AS | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.48 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.51 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.61 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.61 | P23:345:XEL:8N22 SHC | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.67 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.68 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.69 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.7 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.7 | P23:345:MEC:CBEC 908 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.71 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.76 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.82 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.82 | P23:345:MEC:CBEC 905 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.87 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.94 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.94 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.94 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 105.01 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 105.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 105.05 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 105.29 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 105.31 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 105.44 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 105.74 | 772281 GEN-2023-015 345 772282 G23-015XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 106.64 | GEN-2008-051_POI_523961_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 107.84 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03881 | 103.91 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03882 | 104.03 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03883 | 103.58 | P12:EHV:EES::7SAREPTA%:7EL DORADO:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03883 | 104.24 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03885 | 104.28 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03935 | 107.52 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03972 | 104.48 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04858 | 108.91 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04858 | 108.91 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04858 | 108.95 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04858 | 110.15 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05182 | 124.39 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05182 | 124.74 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05182 | 124.74 | Potential P4 Event - POI 515458_6 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05182 | 124.74 | Potential P4 Event - POI 515458_9 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05182 | 124.74 | Potential P4 Event - POI 774180_0 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05182 | 124.74 | Potential P4 Event - POI 774180_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05182 | 125.13 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.06857 | 118.5 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.08166 | 117.79 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.08166 | 117.79 | Potential P4 Event - POI 514801_3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.08282 | 117.86 | Potential P4 Event - POI 514801_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-164 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0843 | 117.39 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 169 | 169 | 0.04675 | 100.24 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 169 | 169 | 0.04675 | 100.24 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 169 | 169 | 0.04737 | 100.32 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 169 | 169 | 0.04737 | 100.32 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 169 | 169 | 0.05758 | 101.52 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 169 | 169 | 0.05758 | 101.52 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59034 | 112.6 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59034 | 112.6 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59034 | 112.6 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59034 | 112.6 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59034 | 113.1 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59034 | 113.13 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59034 | 113.14 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59034 | 113.18 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.59034 | 119.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.41439 | 102.79 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.41439 | 102.79 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.41439 | 103.02 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.41439 | 103.02 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 183 | 201 | 0.07687 | 100.32 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 183 | 201 | 0.07687 | 100.32 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.0586 | 101.26 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.0586 | 101.26 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.05939 | 101.28 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.05939 | 101.28 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.06052 | 100.04 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.06052 | 100.04 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.07687 | 103.56 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.07687 | 103.56 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03707 | 105.47 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03716 | 106.36 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03827 | 107.1 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03827 | 107.1 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03879 | 103.34 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03879 | 103.45 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.15 | 300120 5THMHILB1 161 301504 5THOMHLGSU1 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.15 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.16 | 344011 7HUGHES 345 344012 7HPW-N 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.17 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.2 | P21:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.22 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.24 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.26 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.26 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.28 | 546653 NEARMAN5 161 772721 GEN-2023-037 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.28 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.3 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.3 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.3 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.32 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.34 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.37 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.37 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.38 | P11:20:AMMO:1LAB G1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.38 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.41 | P13:MR#2 GSU | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.42 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.42 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.44 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.46 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.47 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.49 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.53 | 640588 TURTLE.CRK 3 345 640589 SHOLES.W 3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.54 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.55 | P11:024:DPC:ALMA2:6 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.66 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.71 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.78 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.79 | 773981 GEN-2023-100 345 773985 G23-100XFMR2 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.79 | P23:345:XEL:8H14 PRI | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.8 | P23:345:XEL:8H17 PRI AS | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.84 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.88 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.96 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.96 | P23:345:XEL:8N22 SHC | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.02 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.03 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.04 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.05 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.05 | P23:345:MEC:CBEC 908 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.07 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.11 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.17 | P23:345:MEC:CBEC 905 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.18 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.23 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.3 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.3 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.31 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.38 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.39 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.41 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.69 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.7 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.77 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 105.07 | 772281 GEN-2023-015 345 772282 G23-015XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 105.67 | GEN-2008-051_POI_523961_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 107.37 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03881 | 103.25 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03882 | 103.09 | P12:HV:EES::3COUCH%:3LEWISVILLE#:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03882 | 103.37 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03883 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03885 | 103.62 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03935 | 106.98 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03972 | 103.84 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04858 | 108.56 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04858 | 108.56 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04858 | 108.6 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04858 | 109.91 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05182 | 123.96 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05182 | 124.18 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05182 | 124.18 | Potential P4 Event - POI 515458_6 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05182 | 124.18 | Potential P4 Event - POI 515458_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05182 | 124.18 | Potential P4 Event - POI 774180_0 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05182 | 124.18 | Potential P4 Event - POI 774180_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05182 | 124.51 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.06857 | 118.76 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.08166 | 118.05 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.08166 | 118.05 | Potential P4 Event - POI 514801_4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.08282 | 118.14 | Potential P4 Event - POI 514801_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0843 | 117.64 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03707 | 105.98 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03716 | 106.81 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03827 | 107.82 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03827 | 107.83 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03879 | 104 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03879 | 104.12 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.81 | 300120 5THMHILB1 161 301504 5THOMHLGSU1 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.81 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.82 | 344011 7HUGHES 345 344012 7HPW-N 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.84 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.87 | P21:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.89 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.9 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.92 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.92 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.94 | 546653 NEARMAN5 161 772721 GEN-2023-037 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.94 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.96 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.96 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.96 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 103.99 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.01 | P23:345:OTP::TWIN BRKS 3:BRKY_V2021:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.02 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.02 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.04 | P11:20:AMMO:1LAB G1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.04 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.08 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.08 | P13:MR#2 GSU | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.09 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.11 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.13 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.14 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.16 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.17 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.19 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.2 | 640588 TURTLE.CRK 3 345 640589 SHOLES.W 3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.22 | P11:024:DPC:ALMA2:6 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.33 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.37 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.44 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.44 | P23:345:XEL:8H14 PRI | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.45 | 773981 GEN-2023-100 345 773985 G23-100XFMR2 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.46 | P23:345:XEL:8H17 PRI AS | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.48 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.51 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.61 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.61 | P23:345:XEL:8N22 SHC | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.67 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.68 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.69 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.7 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.7 | P23:345:MEC:CBEC 908 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.71 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.76 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.82 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.82 | P23:345:MEC:CBEC 905 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.87 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.94 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.94 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 104.94 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 105.01 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 105.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 105.05 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 105.29 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 105.31 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 105.44 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 105.74 | 772281 GEN-2023-015 345 772282 G23-015XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 106.64 | GEN-2008-051_POI_523961_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0388 | 107.84 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03881 | 103.91 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03882 | 104.03 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03883 | 103.58 | P12:EHV:EES::7SAREPTA%:7EL DORADO:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03883 | 104.24 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03885 | 104.28 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03935 | 107.52 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03972 | 104.48 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04858 | 108.91 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04858 | 108.91 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04858 | 108.95 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04858 | 110.15 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05182 | 124.39 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05182 | 124.74 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05182 | 124.74 | Potential P4 Event - POI 515458_6 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05182 | 124.74 | Potential P4 Event - POI 515458_9 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05182 | 124.74 | Potential P4 Event - POI 774180_0 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05182 | 124.74 | Potential P4 Event - POI 774180_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05182 | 125.13 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.06857 | 118.5 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.08166 | 117.79 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.08166 | 117.79 | Potential P4 Event - POI 514801_3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.08282 | 117.86 | Potential P4 Event - POI 514801_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-165 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0843 | 117.39 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-169 | FROM->TO | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 | 233 | 254 | 0.94293 | 104.54 | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | TDF Impact | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-172 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.04269 | 122.73 | Potential P4 Event - POI 531449_3 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-172 | FROM->TO | 531432 PILE 3 115 531433 SCOTCTY3 115 1 | 239 | 239 | 0.1736 | 108.04 | Potential P4 Event - POI 531449_3 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-172 | FROM->TO | 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 | 195.4 | 195.4 | 0.10909 | 102.66 | Potential P4 Event - POI 531449_3 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-173 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.04269 | 122.73 | Potential P4 Event - POI 531449_3 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-173 | FROM->TO | 531432 PILE 3 115 531433 SCOTCTY3 115 1 | 239 | 239 | 0.1736 | 108.04 | Potential P4 Event - POI 531449_3 | TDF Impact | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-173 | FROM->TO | 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 | 195.4 | 195.4 | 0.10909 | 102.66 | Potential P4 Event - POI 531449_3 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05908 | 112.6 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05908 | 112.6 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05908 | 112.6 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05908 | 112.6 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05908 | 113.1 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05908 | 113.13 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05908 | 113.14 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05908 | 113.18 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05908 | 119.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.1933 | 145.76 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 134.94 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.16 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.17 | 546653 NEARMAN5 161 772721 GEN-2023-037 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.17 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.17 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.18 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.18 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.18 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.19 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.19 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.19 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.22 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.22 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.22 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.22 | GEN-2006-002_POI_511541_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.22 | P11:20:AMMO:1LAB G1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.22 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.22 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.23 | P13:MR#2 GSU | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.24 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.24 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.24 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.25 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.26 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.27 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.27 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.27 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.28 | 640588 TURTLE.CRK 3 345 640589 SHOLES.W 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.29 | P11:024:DPC:ALMA2:6 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.3 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.32 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.32 | P11:345:WERE:EMPR5-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.33 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.35 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.36 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.38 | P23:345:XEL:8H14 PRI | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.39 | P23:345:XEL:8H17 PRI AS | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.41 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.42 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.45 | P23:345:XEL:8N22 SHC | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.48 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.48 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.49 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.49 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.49 | P23:345:MEC:CBEC 908 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.5 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.51 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.54 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.54 | P23:345:MEC:CBEC 905 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.56 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.59 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.59 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.59 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.61 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.62 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.63 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.67 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.67 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 135.86 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 136.95 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 136.95 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 146.51 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 146.51 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24161 | 146.51 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24163 | 135.37 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24166 | 135.34 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24203 | 137.79 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24203 | 138.43 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24223 | 139.57 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24238 | 136.71 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24343 | 139.08 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24343 | 139.08 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24343 | 139.13 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24677 | 150.33 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2471 | 140.1 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25087 | 143.43 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25225 | 141 | P12:115:SPS:V37_1_CASTRO_PLANTX:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25264 | 145.25 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25264 | 145.32 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25264 | 145.32 | Potential P4 Event - POI 774180_0 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25264 | 145.32 | Potential P4 Event - POI 774180_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25402 | 141.81 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25972 | 152.27 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25972 | 152.28 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25972 | 152.28 | Potential P4 Event - POI 525832_2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25972 | 152.28 | Potential P4 Event - POI 525832_5 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26047 | 157.27 | Potential P4 Event - POI 762216_14 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26047 | 157.27 | Potential P4 Event - POI 762467_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2853 | 174.44 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.30218 | 170.16 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.06599 | 110.28 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-178 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.06599 | 109.5 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-180 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.06111 | 116.97 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-180 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.06111 | 116.97 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-180 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.06111 | 116.97 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.16543 | 116.97 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.16543 | 116.97 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.16543 | 116.97 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 169 | 169 | 0.03162 | 100.24 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 169 | 169 | 0.03162 | 100.24 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 169 | 169 | 0.03162 | 100.32 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 169 | 169 | 0.03162 | 100.32 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.5044 | 112.6 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.5044 | 112.6 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.5044 | 112.6 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.5044 | 112.6 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.5044 | 113.1 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.5044 | 113.13 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.5044 | 113.14 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.5044 | 113.18 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.5044 | 119.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.12538 | 102.79 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.12538 | 102.79 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.12538 | 103.02 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.12538 | 103.02 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 183 | 201 | 0.03477 | 100.32 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 183 | 201 | 0.03477 | 100.32 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.03477 | 103.56 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.03477 | 103.56 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.0389 | 100.04 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.0389 | 100.04 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.0389 | 101.26 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.0389 | 101.26 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.0389 | 101.28 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.0389 | 101.28 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04394 | 107.82 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04394 | 107.97 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04467 | 105.47 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04521 | 121.64 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04521 | 121.64 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04521 | 128 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04695 | 107.1 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04695 | 107.1 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04789 | 103.37 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04795 | 103.45 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04798 | 103.25 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04809 | 103.24 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0481 | 103.17 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04811 | 103.09 | P12:HV:EES::3COUCH%:3LEWISVILLE#:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04811 | 103.3 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04811 | 103.3 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04811 | 103.32 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04812 | 103.28 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.15 | 300120 5THMHILB1 161 301504 5THOMHLGSU1 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.15 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.16 | 344011 7HUGHES 345 344012 7HPW-N 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.2 | P21:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.22 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.26 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.26 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.28 | 546653 NEARMAN5 161 772721 GEN-2023-037 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.3 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.34 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.37 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.37 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.38 | P11:20:AMMO:1LAB G1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.38 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.41 | P13:MR#2 GSU | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.42 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.42 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.44 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.46 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.47 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.49 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.53 | 640588 TURTLE.CRK 3 345 640589 SHOLES.W 3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.54 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.55 | P11:024:DPC:ALMA2:6 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.66 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.71 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.78 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.79 | 773981 GEN-2023-100 345 773985 G23-100XFMR2 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.79 | P23:345:XEL:8H14 PRI | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.8 | P23:345:XEL:8H17 PRI AS | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.84 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.88 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.96 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.96 | P23:345:XEL:8N22 SHC | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.02 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.03 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.04 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.05 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.05 | P23:345:MEC:CBEC 908 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.07 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.11 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.17 | P23:345:MEC:CBEC 905 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.18 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.23 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.3 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.3 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.31 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.38 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.39 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.41 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.69 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.7 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.77 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 105.07 | 772281 GEN-2023-015 345 772282 G23-015XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 105.51 | GEN-2023-102_POI_515852_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 105.67 | GEN-2008-051_POI_523961_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 107.37 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04821 | 103.34 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04875 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04888 | 103.84 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04892 | 106.98 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0491 | 103.62 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04971 | 106.36 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.06533 | 108.56 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.06533 | 108.56 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.06533 | 108.6 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.06533 | 109.91 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.06859 | 118.76 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.07049 | 123.96 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.07049 | 124.18 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.07049 | 124.18 | Potential P4 Event - POI 515458_6 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.07049 | 124.18 | Potential P4 Event - POI 515458_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.07049 | 124.18 | Potential P4 Event - POI 774180_0 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.07049 | 124.18 | Potential P4 Event - POI 774180_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.07049 | 124.51 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.07749 | 117.64 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.07749 | 118.05 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.07749 | 118.05 | Potential P4 Event - POI 514801_4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.07749 | 118.14 | Potential P4 Event - POI 514801_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04394 | 108.34 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04394 | 108.48 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04467 | 105.98 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04521 | 121.49 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04521 | 121.49 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04521 | 121.49 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04521 | 127.53 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04695 | 107.82 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04695 | 107.83 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04768 | 103.58 | P12:EHV:EES::7SAREPTA%:7EL DORADO:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04789 | 104.03 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04795 | 104.12 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04798 | 103.91 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04809 | 103.9 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0481 | 103.84 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04811 | 103.96 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04811 | 103.96 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04811 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04812 | 103.94 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.81 | 300120 5THMHILB1 161 301504 5THOMHLGSU1 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.81 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.82 | 344011 7HUGHES 345 344012 7HPW-N 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.87 | P21:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.89 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.92 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.92 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.94 | 546653 NEARMAN5 161 772721 GEN-2023-037 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.96 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 103.99 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.01 | P23:345:OTP::TWIN BRKS 3:BRKY_V2021:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.02 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.02 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.04 | P11:20:AMMO:1LAB G1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.04 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.08 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.08 | P13:MR#2 GSU | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.09 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.11 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.13 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.14 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.16 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.17 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.19 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.2 | 640588 TURTLE.CRK 3 345 640589 SHOLES.W 3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.22 | P11:024:DPC:ALMA2:6 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.33 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.37 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.44 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.44 | P23:345:XEL:8H14 PRI | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.45 | 773981 GEN-2023-100 345 773985 G23-100XFMR2 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.46 | P23:345:XEL:8H17 PRI AS | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.48 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.51 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.61 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.61 | P23:345:XEL:8N22 SHC | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.67 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.68 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.69 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.7 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.7 | P23:345:MEC:CBEC 908 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.71 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.76 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.82 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.82 | P23:345:MEC:CBEC 905 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.87 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.94 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.94 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 104.94 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 105.01 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 105.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 105.05 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 105.29 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 105.31 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 105.44 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 105.74 | 772281 GEN-2023-015 345 772282 G23-015XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 106.15 | GEN-2023-102_POI_515852_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 106.64 | GEN-2008-051_POI_523961_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04815 | 107.84 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04821 | 104 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04875 | 104.24 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04888 | 104.48 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04892 | 107.52 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0491 | 104.28 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04971 | 106.81 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.06533 | 108.91 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.06533 | 108.91 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.06533 | 108.95 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.06533 | 110.15 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.06859 | 118.5 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.07049 | 124.39 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.07049 | 124.74 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.07049 | 124.74 | Potential P4 Event - POI 515458_6 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.07049 | 124.74 | Potential P4 Event - POI 515458_9 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.07049 | 124.74 | Potential P4 Event - POI 774180_0 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.07049 | 124.74 | Potential P4 Event - POI 774180_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.07049 | 125.13 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.07749 | 117.39 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.07749 | 117.79 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.07749 | 117.79 | Potential P4 Event - POI 514801_3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-188 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.07749 | 117.86 | Potential P4 Event - POI 514801_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 300101 5MORGAN 161 547478 DAD368 5 161 1 | 223 | 223 | 0.06609 | 100.48 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.12161 | 104.47 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 532935 MARMTNW5 161 532937 NEOSHO 5 161 1 | 148 | 148 | 0.12255 | 122.38 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 533758 CRAWFOR2 69.0 533772 SE1GREE2 69.0 1 | 48 | 57 | 0.04436 | 116.75 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 533762 GIR JCT2 69.0 533772 SE1GREE2 69.0 1 | 55 | 57 | 0.04436 | 111.75 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 533762 GIR JCT2 69.0 533876 FRANKLIN2 69.0 1 | 55 | 57 | 0.04436 | 101.42 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547467 ORO110 5 161 547469 RIV4525 161 1 | 479 | 493 | 0.54642 | 100.38 | 547469 RIV4525 161 547498 STL439 5 161 1 | TDF Impact | Rebuild the ORO110 5 to RIV4525 161 kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.8484 | 113.76 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.8484 | 116.79 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.8484 | 116.79 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85146 | 115.79 | P12:161:GRDA:MIAMI 5-KETCHUM5:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85152 | 111.08 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.11 | 655882 GALAXYTP-MK7 115 659388 KUMMERDG-MK7 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.12 | P12:345:OPPD:S3458-COOPER:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.12 | P22:345:OPPD:S3458-COOPER:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.13 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.13 | P12:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.15 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.15 | P21:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.15 | P23:345:ITCM:HAZLTON3 9985:IA-NE | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.17 | P21:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.18 | 655848 BERG -MK7 115 655873 BBCOMPTP-MK7 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.19 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.19 | P21:115:XEL:RED BUS #1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.2 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.2 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.2 | 655873 BBCOMPTP-MK7 115 659388 KUMMERDG-MK7 115 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.2 | P21:345:AMIL-MEC:AUTO-SINGLE:7SANDBURG:OAKGROV3:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.21 | 640230 HOSK.T89 34.5 640227 HOSKINS4 230 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.22 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.28 | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.3 | 515422 C-RIVER7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.34 | P23:345:MEC:BOONEVILLE:901:_1:: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.37 | P23:500:EES-EAI:DELL:B8320::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.38 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.39 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.46 | P13:230:EES:NINEMI:AT4 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.5 | P13:230:EES:NINEMI:AT5 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.58 | 505461 BULL SH W5 161 505468 BSH5&6 1 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.58 | 505461 BULL SH W5 161 505470 BSH7&8 1 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.64 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.89 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.92 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 110.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 111.01 | P11:25:EES:WATERF:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 111.01 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 111.03 | P11:26:EES-EAI:INDEP2:1:D401 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 111.07 | P11:26:EES-EAI:INDEP2:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 111.49 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 111.49 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 111.55 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 111.55 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 111.8 | P11:HV:EES::FLINTCR1:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 112.09 | 772541 GEN-2023-028 161 772542 G23-028XFMR1 34.5 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 112.09 | GEN-2023-028_POI_772540_Generator_outage | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 112.99 | 547501 RIV453 5 161 547643 R13G167 13.8 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 113.28 | 505488 CARTHAG5 161 773201 GEN-2023-061 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 113.28 | 773201 GEN-2023-061 161 773202 G23-061XFMR1 34.5 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 113.28 | GEN-2023-061_POI_505488_Generator_outage | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85156 | 116.25 | P12:161:GRDA:PENSA 5-KETCHUM5:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85157 | 110.16 | 521157 HUGO 7 345 560088 G16-063-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85157 | 110.23 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85157 | 110.23 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85157 | 110.34 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85157 | 110.35 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.8516 | 110.26 | P12:HV:EES::5CALICO ROCK:NORFORK5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85161 | 111.44 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85161 | 111.46 | P42:345:GRDA:CLEVLND CB13280:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85169 | 111.24 | P12:345:AMMO-GMO::OVERTON:SIBLEY:EHV | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85169 | 112.21 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.8517 | 111.43 | P23:345:GMO:SIBLEY-R1-3:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85171 | 111.59 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85173 | 112.57 | P42:345:OKGE:SB_RARD7313:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85173 | 112.67 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85174 | 112.93 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85174 | 112.93 | Potential P4 Event - POI 514803_6 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85174 | 113.33 | Potential P4 Event - POI 514803_7 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85177 | 113.2 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85179 | 111.71 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85181 | 115.09 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85182 | 111.19 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85182 | 111.26 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85182 | 111.28 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85183 | 110.73 | P12:HV:EES::5CLEVCOV:TABLE R5!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85191 | 110.99 | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85205 | 110.45 | 547561 NOL443 2 69.0 547610 NOL435 2 69.0 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85209 | 113.3 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.8521 | 111.73 | 300950 5JASPER 161 300949 7JASPER 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85213 | 111.83 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85234 | 114.6 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85241 | 115.32 | Potential P4 Event - POI 774740_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85241 | 115.33 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85241 | 115.33 | Potential P4 Event - POI 774740_2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85258 | 112.28 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85298 | 111.62 | P12:69:WERE:SPIT-NSES-69::FUTURE:HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85311 | 111.51 | P12:69:WERE:FRAN-NSES-69:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85388 | 115.59 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85388 | 115.61 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85444 | 123.6 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85541 | 111.95 | P12:161:AEPW-EMDE:FLINTCR5:739952::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85599 | 112.96 | 532930 JAYHAWK5 161 532934 MARMTNE5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85599 | 113.02 | 532930 JAYHAWK5 161 532938 FRANKLIN5 161 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85608 | 114.71 | P12:161:WERE:MARM-NSES-161:::HV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85619 | 130.09 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85988 | 133.78 | P12:345:WERE:N345-AECI-345:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.85988 | 133.79 | Potential P4 Event - POI 532793_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-194 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.86235 | 132.99 | Potential P4 Event - POI 532793_0 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05965 | 112.6 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05965 | 112.6 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05965 | 112.6 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05965 | 112.6 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05965 | 113.1 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05965 | 113.13 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05965 | 113.14 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05965 | 113.18 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.05965 | 119.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20217 | 145.76 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 134.94 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.17 | 546653 NEARMAN5 161 772721 GEN-2023-037 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.17 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.17 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.18 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.19 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.22 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.22 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.22 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.22 | GEN-2006-002_POI_511541_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.22 | P11:20:AMMO:1LAB G1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.22 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.23 | P13:MR#2 GSU | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.24 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.24 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.25 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.26 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.27 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.27 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.27 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.28 | 640588 TURTLE.CRK 3 345 640589 SHOLES.W 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.29 | P11:024:DPC:ALMA2:6 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.32 | P11:345:WERE:EMPR5-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.33 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.35 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.36 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.38 | P23:345:XEL:8H14 PRI | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.39 | P23:345:XEL:8H17 PRI AS | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.41 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.42 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.45 | P23:345:XEL:8N22 SHC | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.48 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.48 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.49 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.49 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.49 | P23:345:MEC:CBEC 908 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.5 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.51 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.54 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.54 | P23:345:MEC:CBEC 905 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.56 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.59 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.59 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.59 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.61 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.63 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.67 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.67 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 135.86 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 136.95 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 136.95 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 146.51 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 146.51 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25047 | 146.51 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25048 | 135.16 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25048 | 135.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25048 | 135.18 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25048 | 135.18 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25048 | 135.19 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25048 | 135.19 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25048 | 135.22 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25048 | 135.24 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25048 | 135.3 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25048 | 135.32 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25048 | 135.62 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25049 | 135.37 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25053 | 135.34 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2509 | 137.79 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2509 | 138.43 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25111 | 139.57 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25125 | 136.71 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25231 | 139.08 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25231 | 139.08 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25231 | 139.13 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25545 | 140.1 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25976 | 143.43 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26002 | 150.33 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26096 | 141 | P12:115:SPS:V37_1_CASTRO_PLANTX:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26161 | 145.25 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26161 | 145.32 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26161 | 145.32 | Potential P4 Event - POI 774180_0 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26161 | 145.32 | Potential P4 Event - POI 774180_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.263 | 141.81 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26785 | 152.27 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26785 | 152.28 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26785 | 152.28 | Potential P4 Event - POI 525832_2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26785 | 152.28 | Potential P4 Event - POI 525832_5 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2695 | 157.27 | Potential P4 Event - POI 762216_14 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2695 | 157.27 | Potential P4 Event - POI 762467_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.29696 | 174.44 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.31565 | 170.16 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.08465 | 110.28 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-195 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.08465 | 109.5 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-199 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 115.33 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-199 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 114.02 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06945 | 112.6 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06945 | 112.6 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06945 | 112.6 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06945 | 112.6 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06945 | 113.1 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06945 | 113.13 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06945 | 113.14 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06945 | 113.18 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.06945 | 119.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.1623 | 145.76 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 134.94 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.16 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.17 | 546653 NEARMAN5 161 772721 GEN-2023-037 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.17 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.17 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.18 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.18 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.18 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.19 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.19 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.19 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.22 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.22 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.22 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.22 | GEN-2006-002_POI_511541_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.22 | P11:20:AMMO:1LAB G1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.22 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.22 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.23 | P13:MR#2 GSU | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.24 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.24 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.24 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.25 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.26 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.27 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.27 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.27 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.28 | 640588 TURTLE.CRK 3 345 640589 SHOLES.W 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.29 | P11:024:DPC:ALMA2:6 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.3 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.32 | P11:345:WERE:EMPR5-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.33 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.35 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.36 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.38 | P23:345:XEL:8H14 PRI | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.39 | P23:345:XEL:8H17 PRI AS | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.41 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.42 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.45 | P23:345:XEL:8N22 SHC | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.48 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.48 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.49 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.49 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.49 | P23:345:MEC:CBEC 908 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.5 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.51 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.54 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.54 | P23:345:MEC:CBEC 905 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.56 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.59 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.59 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.59 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.61 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.62 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.63 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.67 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.67 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 135.86 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 136.95 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 136.95 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 146.51 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 146.51 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2106 | 146.51 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21061 | 135.32 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21062 | 135.37 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21067 | 135.34 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21109 | 137.79 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21109 | 138.43 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21134 | 139.57 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21149 | 136.71 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21271 | 139.08 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21271 | 139.08 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21271 | 139.13 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21939 | 150.33 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22004 | 141 | P12:115:SPS:V37_1_CASTRO_PLANTX:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22241 | 143.43 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22344 | 145.25 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22344 | 145.32 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22344 | 145.32 | Potential P4 Event - POI 774180_0 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22344 | 145.32 | Potential P4 Event - POI 774180_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22508 | 141.81 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.23242 | 157.27 | Potential P4 Event - POI 762216_14 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.23242 | 157.27 | Potential P4 Event - POI 762467_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.23249 | 174.44 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.23317 | 140.1 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25286 | 152.27 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25286 | 152.28 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25286 | 152.28 | Potential P4 Event - POI 525832_2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.25286 | 152.28 | Potential P4 Event - POI 525832_5 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.27224 | 170.16 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.07416 | 110.28 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-201 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.07416 | 109.5 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07046 | 112.6 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07046 | 112.6 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07046 | 112.6 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07046 | 112.6 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07046 | 113.1 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07046 | 113.13 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07046 | 113.14 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07046 | 113.18 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07046 | 119.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.1545 | 145.76 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 134.94 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.16 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.17 | 546653 NEARMAN5 161 772721 GEN-2023-037 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.17 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.17 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.18 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.18 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.18 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.19 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.19 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.19 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.22 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.22 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.22 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.22 | GEN-2006-002_POI_511541_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.22 | P11:20:AMMO:1LAB G1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.22 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.22 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.23 | P13:MR#2 GSU | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.24 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.24 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.24 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.25 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.26 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.27 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.27 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.27 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.28 | 640588 TURTLE.CRK 3 345 640589 SHOLES.W 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.29 | P11:024:DPC:ALMA2:6 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.3 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.32 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.32 | P11:345:WERE:EMPR5-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.33 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.35 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.36 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.38 | P23:345:XEL:8H14 PRI | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.39 | P23:345:XEL:8H17 PRI AS | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.41 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.42 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.45 | P23:345:XEL:8N22 SHC | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.48 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.48 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.49 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.49 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.49 | P23:345:MEC:CBEC 908 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.5 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.51 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.54 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.54 | P23:345:MEC:CBEC 905 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.56 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.59 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.59 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.59 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.61 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.62 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.63 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.67 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.67 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 135.86 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 136.95 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 136.95 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 146.51 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 146.51 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20281 | 146.51 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20283 | 135.37 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20288 | 135.34 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2033 | 137.79 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2033 | 138.43 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20356 | 139.57 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20371 | 136.71 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20495 | 139.08 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20495 | 139.08 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20495 | 139.13 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20963 | 140.1 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21058 | 150.33 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21219 | 141 | P12:115:SPS:V37_1_CASTRO_PLANTX:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21582 | 145.25 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21582 | 145.32 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21582 | 145.32 | Potential P4 Event - POI 774180_0 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21582 | 145.32 | Potential P4 Event - POI 774180_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21749 | 141.81 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21802 | 143.43 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2194 | 174.44 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22492 | 157.27 | Potential P4 Event - POI 762216_14 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22492 | 157.27 | Potential P4 Event - POI 762467_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24447 | 152.27 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24447 | 152.28 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24447 | 152.28 | Potential P4 Event - POI 525832_2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.24447 | 152.28 | Potential P4 Event - POI 525832_5 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26341 | 170.16 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.06872 | 110.28 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-203 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.06872 | 109.5 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-205 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.05704 | 100.01 | 515254 SUNSTCN5 161 515265 SHAD-PT5 161 1 | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-205 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.05704 | 100.28 | P12:161:OKGE-SWPA-WFEC:BKRBKR4:::: | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-205 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.05704 | 100.79 | 505582 RS KERR5 161 515254 SUNSTCN5 161 1 | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-205 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.14946 | 116.97 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-205 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.14946 | 116.97 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-205 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.14946 | 116.97 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-209 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04419 | 136.95 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-209 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.04419 | 136.95 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-210 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.16691 | 102.79 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-210 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.16691 | 102.79 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-210 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.16691 | 103.02 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-210 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.16691 | 103.02 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-211 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03172 | 113.33 | Potential P4 Event - POI 514803_7 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-211 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03231 | 112.57 | P42:345:OKGE:SB_RARD7313:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-211 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03231 | 112.67 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-211 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03254 | 112.93 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-211 | FROM->TO | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.03254 | 112.93 | Potential P4 Event - POI 514803_6 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-212 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.34294 | 116.97 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-212 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.34294 | 116.97 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-212 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.34294 | 116.97 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-213 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.10716 | 116.97 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-213 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.10716 | 116.97 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-213 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.10716 | 116.97 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-216 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 115.33 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-216 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 114.02 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-217 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 115.33 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-217 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 114.02 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-218 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 115.33 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-218 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 114.02 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | 193 | 193 | 0.26615 | 110.74 | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.26729 | 111.2 | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16105 | 105.13 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16105 | 106.67 | P12:115:SUNC:CONCORDIA-CLIFTON:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16878 | 107.86 | P13:115-230:SUNC:CONCORDIA_XFR:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17026 | 100.43 | 533163 HOYT 3 115 533165 HTI JCT3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17052 | 101.49 | P23:345:WERE:SUMM-345-218:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17063 | 101 | 539805 ELMCREEK7 345 3WXFMR ELMCREEK T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17063 | 101.01 | 539805 ELMCREEK7 345 588494 G17-004-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17063 | 101.07 | 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17063 | 102.88 | Potential P4 Event - POI 532773_5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1712 | 102.07 | Potential P4 Event - POI 532773_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 100.02 | P11:25:EES:WATERF:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 100.02 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 100.03 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 100.18 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 100.3 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 100.3 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 100.31 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 100.4 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 100.4 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 100.76 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 100.76 | GEN-2023-081_POI_773600_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 100.77 | 515852 DGRASSE7 345 776821 GEN-2023-102 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 100.78 | GEN-2023-102_POI_515852_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 100.96 | Potential P4 Event - POI 515576_20 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 101.25 | Potential P4 Event - POI 515576_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 101.37 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 101.44 | Potential P4 Event - POI 337561_27 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 102.73 | Potential P4 Event - POI 515852_14 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 104.44 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17139 | 104.44 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.19789 | 110.16 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.19789 | 112.4 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.23421 | 142.47 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.23421 | 142.69 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.2669 | 165.15 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.30415 | 155.56 | Potential P4 Event - POI 640590_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31082 | 154.78 | Potential P4 Event - POI 640525_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31082 | 154.83 | Potential P4 Event - POI 640525_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31362 | 152.45 | P12:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31405 | 154.86 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31412 | 152.73 | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31412 | 152.75 | P23:345:GMO:EASTOWNE-R7-14:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31414 | 153.35 | P23:345:WERE:STRA-345-634-2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31415 | 153.4 | P12:345:WERE:HOYT-STRA-345:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31415 | 153.42 | Potential P4 Event - POI 532772_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31419 | 152.08 | P21:345:MEC-OPPD:AUTO-SINGLE:CBLUFFS3:S34563:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3142 | 152.39 | P42:345:MEC-OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3142 | 152.39 | P45:345:OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31421 | 152.16 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31422 | 153.59 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.52 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.54 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.55 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.59 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.59 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.59 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.61 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.61 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.61 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.66 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.67 | P23:500:EAI-TVA:NBF_WEST M~1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.67 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.72 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.94 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 152 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 152.02 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 152.03 | P23:345:AMMO:::24SPENCERCREEK:EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 152.14 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.24 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.25 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.26 | 338342 1EAI DELLCT1 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.26 | 338343 1EAI DELLCT2 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.26 | 532772 STRANGR7 345 3WXFMR STRANGR TX-3 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.58 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.59 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.62 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.63 | P12:HV:EES::6DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.65 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.68 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.71 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.73 | 640119 COL.COG7 115 640028 COLCOG1G 13.8 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.76 | 48465 J1846 SUB 230 3WXFMR J1846 SUB 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.77 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.78 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.78 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.93 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.04 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.09 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.09 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.11 | P13:MR#2 GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.12 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.15 | GEN-2023-199_POI_640386_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.16 | 775961 GEN-2023-199 230 775962 G23-199XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.28 | 760789 G17-201XFMR1 34.5 760788 GEN-2017-201 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.28 | GEN-2017-201_POI_640226_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.41 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.48 | P11:115:XEL:HBR #6 7 8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.51 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.78 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.85 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.85 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.95 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 153.16 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 153.27 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 153.38 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 153.39 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 153.39 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 153.52 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 153.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 153.88 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 153.94 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 154.74 | Potential P4 Event - POI 640588_8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 158.62 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31425 | 151.75 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31427 | 151.54 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31428 | 151.51 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31428 | 151.74 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31428 | 151.77 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31429 | 151.64 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31482 | 153.01 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31482 | 153.08 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31482 | 153.59 | Potential P4 Event - POI 640065_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31522 | 152.65 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31794 | 152.68 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.32197 | 155.32 | P12:161:OPPD:HUMBOLT-S1280:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.32998 | 154.16 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34988 | 163.46 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34988 | 165.85 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34988 | 165.86 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.37528 | 176.55 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.55878 | 271.93 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.39314 | 145.67 | Potential P4 Event - POI 640590_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40175 | 145.08 | Potential P4 Event - POI 640525_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40175 | 145.13 | Potential P4 Event - POI 640525_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40537 | 142.85 | P12:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40592 | 145.16 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40601 | 143.13 | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40601 | 143.15 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40602 | 143.78 | Potential P4 Event - POI 532772_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40604 | 143.71 | P23:345:WERE:STRA-345-634-2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40605 | 143.77 | P12:345:WERE:HOYT-STRA-345:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4061 | 142.5 | P21:345:MEC-OPPD:AUTO-SINGLE:CBLUFFS3:S34563:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40612 | 142.79 | P42:345:MEC-OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40612 | 142.79 | P45:345:OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40614 | 142.58 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40615 | 143.94 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40616 | 141.97 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40616 | 141.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40616 | 141.99 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40616 | 142.03 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40616 | 142.03 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40616 | 142.04 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40616 | 142.11 | P23:500:EAI-TVA:NBF_WEST M~1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40616 | 142.15 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40616 | 142.42 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40616 | 142.44 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40616 | 142.56 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 141.7 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 141.71 | 301643 FOXTROTGSU 34.5 3WXFMR FOXTROTGSU 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 141.71 | 345125 4MERAMEC 3 138 345148 1MER 3 16.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 141.71 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 141.72 | 505554 WEBFALL5 161 505556 WEB123 1 13.8 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.01 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.02 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.03 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.05 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.05 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.05 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.06 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.07 | P12:HV:EES::6DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.09 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.1 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.11 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.12 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.15 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.17 | 640119 COL.COG7 115 640028 COLCOG1G 13.8 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.21 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.22 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.36 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.42 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.42 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.46 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.51 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.51 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.54 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.57 | GEN-2023-199_POI_640386_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.69 | GEN-2017-201_POI_640226_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.82 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.89 | P11:115:XEL:HBR #6 7 8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.91 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 143.17 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 143.22 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 143.24 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 143.33 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 143.54 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 143.64 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 143.74 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 143.75 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 143.75 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 143.87 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 143.98 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 144.22 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 144.28 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 145.04 | Potential P4 Event - POI 640588_8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 148.76 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40619 | 142.19 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40622 | 141.99 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40622 | 142.21 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40623 | 141.96 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40623 | 142.17 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40624 | 142.08 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40692 | 143.39 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40692 | 143.45 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40692 | 143.95 | Potential P4 Event - POI 640065_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40744 | 143.05 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.41096 | 143.07 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.41617 | 145.6 | P12:161:OPPD:HUMBOLT-S1280:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.42652 | 144.49 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45224 | 153.4 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.48507 | 165.93 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.61409 | 214.64 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.61409 | 217.49 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.61409 | 217.72 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 115.33 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 115.33 | 771999 G23-222-POI 345 776442 G23-223XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 115.33 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 115.33 | 776442 G23-223XFMR1 345 776444 G23-223GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 171.38 | Potential P4 Event - POI 640590_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 171.99 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 172.35 | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 172.36 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 172.36 | P42:345:LES:L3503::103&ROKEBY.MOORE.CB3003:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 172.36 | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 172.36 | Potential P4 Event - POI 640374_7 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 172.37 | Potential P4 Event - POI 640525_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 172.37 | Potential P4 Event - POI 640588_8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 2 | 115.33 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.30415 | 152.65 | Potential P4 Event - POI 640590_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31082 | 152.15 | Potential P4 Event - POI 640525_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31082 | 152.2 | Potential P4 Event - POI 640525_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31362 | 149.78 | P12:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31405 | 152.24 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31412 | 150.07 | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31412 | 150.09 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31412 | 150.77 | Potential P4 Event - POI 532772_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31414 | 150.7 | P23:345:WERE:STRA-345-634-2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31415 | 150.76 | P12:345:WERE:HOYT-STRA-345:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31419 | 149.4 | P21:345:MEC-OPPD:AUTO-SINGLE:CBLUFFS3:S34563:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3142 | 149.7 | P42:345:MEC-OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3142 | 149.7 | P45:345:OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31421 | 149.49 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31422 | 150.94 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 148.84 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 148.86 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 148.86 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 148.89 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 148.91 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 148.91 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 148.91 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 148.93 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 148.93 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 148.93 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 148.98 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 148.99 | P23:500:EAI-TVA:NBF_WEST M~1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 148.99 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 149.04 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 149.26 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 149.32 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 149.34 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 149.36 | P23:345:AMMO:::24SPENCERCREEK:EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 149.47 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 148.55 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 148.58 | 338342 1EAI DELLCT1 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 148.58 | 338343 1EAI DELLCT2 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 148.58 | 515894 THUNDER7 345 765480 GEN-2021-019 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 148.58 | 532772 STRANGR7 345 3WXFMR STRANGR TX-3 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 148.9 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 148.91 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 148.93 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 148.95 | P12:HV:EES::6DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 148.97 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.03 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.05 | 640119 COL.COG7 115 640028 COLCOG1G 13.8 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.08 | 48465 J1846 SUB 230 3WXFMR J1846 SUB 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.09 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.1 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.1 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.26 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.32 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.32 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.37 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.41 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.42 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.44 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.44 | P13:MR#2 GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.48 | 775961 GEN-2023-199 230 775962 G23-199XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.48 | GEN-2023-199_POI_640386_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.61 | 760789 G17-201XFMR1 34.5 760788 GEN-2017-201 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.61 | GEN-2017-201_POI_640226_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.75 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.82 | P11:115:XEL:HBR #6 7 8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.85 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 150.12 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 150.18 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 150.19 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 150.19 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 150.29 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 150.51 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 150.62 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 150.72 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 150.73 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 150.74 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 150.85 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 150.98 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 151.23 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 152.1 | Potential P4 Event - POI 640588_8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 152.15 | 640112 CLATONA9 34.5 3WXFMR CLATONIA T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 156.08 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31425 | 149.07 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31427 | 148.86 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31428 | 148.83 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31428 | 149.06 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31428 | 149.09 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31429 | 148.96 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31482 | 150.36 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31482 | 150.42 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31482 | 150.95 | Potential P4 Event - POI 640065_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31522 | 150 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31794 | 150.02 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.32197 | 152.71 | P12:161:OPPD:HUMBOLT-S1280:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.32998 | 151.52 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34988 | 161.02 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34988 | 163.47 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34988 | 163.48 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.37528 | 174.38 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.55878 | 271.68 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.15417 | 106.27 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 114.02 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 114.02 | 771999 G23-222-POI 345 776442 G23-223XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 114.02 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 114.02 | 776442 G23-223XFMR1 345 776444 G23-223GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 171.18 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 171.18 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 171.52 | Potential P4 Event - POI 640590_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 171.61 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 171.62 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 171.62 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 2 | 114.02 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | 193 | 193 | 0.26615 | 110.74 | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.26729 | 111.2 | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16105 | 105.13 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16105 | 106.67 | P12:115:SUNC:CONCORDIA-CLIFTON:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16878 | 107.86 | P13:115-230:SUNC:CONCORDIA_XFR:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17026 | 100.43 | 533163 HOYT 3 115 533165 HTI JCT3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17052 | 101.49 | P23:345:WERE:SUMM-345-218:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17063 | 101 | 539805 ELMCREEK7 345 3WXFMR ELMCREEK T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17063 | 101.01 | 539805 ELMCREEK7 345 588494 G17-004-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17063 | 101.07 | 532773 SUMMIT 7 345 588494 G17-004-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17063 | 102.88 | Potential P4 Event - POI 532773_5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1712 | 102.07 | Potential P4 Event - POI 532773_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 100.02 | P11:25:EES:WATERF:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 100.02 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 100.03 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 100.18 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 100.3 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 100.3 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 100.31 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 100.4 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 100.4 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 100.76 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 100.76 | GEN-2023-081_POI_773600_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 100.77 | 515852 DGRASSE7 345 776821 GEN-2023-102 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 100.78 | GEN-2023-102_POI_515852_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 100.96 | Potential P4 Event - POI 515576_20 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 101.25 | Potential P4 Event - POI 515576_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 101.37 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 101.44 | Potential P4 Event - POI 337561_27 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 102.73 | Potential P4 Event - POI 515852_14 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17137 | 104.44 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17139 | 104.44 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.19789 | 110.16 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.19789 | 112.4 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.23421 | 142.47 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.23421 | 142.69 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.2669 | 165.15 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.30415 | 155.56 | Potential P4 Event - POI 640590_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31082 | 154.78 | Potential P4 Event - POI 640525_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31082 | 154.83 | Potential P4 Event - POI 640525_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31362 | 152.45 | P12:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31405 | 154.86 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31412 | 152.73 | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31412 | 152.75 | P23:345:GMO:EASTOWNE-R7-14:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31414 | 153.35 | P23:345:WERE:STRA-345-634-2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31415 | 153.4 | P12:345:WERE:HOYT-STRA-345:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31415 | 153.42 | Potential P4 Event - POI 532772_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31419 | 152.08 | P21:345:MEC-OPPD:AUTO-SINGLE:CBLUFFS3:S34563:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3142 | 152.39 | P42:345:MEC-OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3142 | 152.39 | P45:345:OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31421 | 152.16 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31422 | 153.59 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.52 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.54 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.55 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.59 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.59 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.59 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.61 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.61 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.61 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.66 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.67 | P23:500:EAI-TVA:NBF_WEST M~1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.67 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.72 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 151.94 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 152 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 152.02 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 152.03 | P23:345:AMMO:::24SPENCERCREEK:EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31423 | 152.14 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.24 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.25 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.26 | 338342 1EAI DELLCT1 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.26 | 338343 1EAI DELLCT2 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.26 | 532772 STRANGR7 345 3WXFMR STRANGR TX-3 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.58 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.59 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.62 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.63 | P12:HV:EES::6DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.65 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.68 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.71 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.73 | 640119 COL.COG7 115 640028 COLCOG1G 13.8 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.76 | 48465 J1846 SUB 230 3WXFMR J1846 SUB 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.77 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.78 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.78 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 151.93 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.04 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.09 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.09 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.11 | P13:MR#2 GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.12 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.15 | GEN-2023-199_POI_640386_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.16 | 775961 GEN-2023-199 230 775962 G23-199XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.28 | 760789 G17-201XFMR1 34.5 760788 GEN-2017-201 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.28 | GEN-2017-201_POI_640226_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.41 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.48 | P11:115:XEL:HBR #6 7 8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.51 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.78 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.85 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.85 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 152.95 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 153.16 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 153.27 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 153.38 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 153.39 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 153.39 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 153.52 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 153.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 153.88 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 153.94 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 154.74 | Potential P4 Event - POI 640588_8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31424 | 158.62 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31425 | 151.75 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31427 | 151.54 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31428 | 151.51 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31428 | 151.74 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31428 | 151.77 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31429 | 151.64 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31482 | 153.01 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31482 | 153.08 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31482 | 153.59 | Potential P4 Event - POI 640065_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31522 | 152.65 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31794 | 152.68 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.32197 | 155.32 | P12:161:OPPD:HUMBOLT-S1280:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.32998 | 154.16 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34988 | 163.46 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34988 | 165.85 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34988 | 165.86 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.37528 | 176.55 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.55878 | 271.93 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.39314 | 145.67 | Potential P4 Event - POI 640590_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40175 | 145.08 | Potential P4 Event - POI 640525_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40175 | 145.13 | Potential P4 Event - POI 640525_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40537 | 142.85 | P12:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40592 | 145.16 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40601 | 143.13 | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40601 | 143.15 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40602 | 143.78 | Potential P4 Event - POI 532772_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40604 | 143.71 | P23:345:WERE:STRA-345-634-2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40605 | 143.77 | P12:345:WERE:HOYT-STRA-345:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4061 | 142.5 | P21:345:MEC-OPPD:AUTO-SINGLE:CBLUFFS3:S34563:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40612 | 142.79 | P42:345:MEC-OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40612 | 142.79 | P45:345:OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40614 | 142.58 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40615 | 143.94 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40616 | 141.97 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40616 | 141.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40616 | 141.99 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40616 | 142.03 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40616 | 142.03 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40616 | 142.04 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40616 | 142.11 | P23:500:EAI-TVA:NBF_WEST M~1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40616 | 142.15 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40616 | 142.42 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40616 | 142.44 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40616 | 142.56 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 141.7 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 141.71 | 301643 FOXTROTGSU 34.5 3WXFMR FOXTROTGSU 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 141.71 | 345125 4MERAMEC 3 138 345148 1MER 3 16.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 141.71 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 141.72 | 505554 WEBFALL5 161 505556 WEB123 1 13.8 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.01 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.02 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.03 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.05 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.05 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.05 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.06 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.07 | P12:HV:EES::6DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.09 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.1 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.11 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.12 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.15 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.17 | 640119 COL.COG7 115 640028 COLCOG1G 13.8 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.21 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.22 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.36 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.42 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.42 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.46 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.51 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.51 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.54 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.57 | GEN-2023-199_POI_640386_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.69 | GEN-2017-201_POI_640226_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.82 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.89 | P11:115:XEL:HBR #6 7 8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 142.91 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 143.17 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 143.22 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 143.24 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 143.33 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 143.54 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 143.64 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 143.74 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 143.75 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 143.75 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 143.87 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 143.98 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 144.22 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 144.28 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 145.04 | Potential P4 Event - POI 640588_8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40617 | 148.76 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40619 | 142.19 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40622 | 141.99 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40622 | 142.21 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40623 | 141.96 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40623 | 142.17 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40624 | 142.08 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40692 | 143.39 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40692 | 143.45 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40692 | 143.95 | Potential P4 Event - POI 640065_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40744 | 143.05 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.41096 | 143.07 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.41617 | 145.6 | P12:161:OPPD:HUMBOLT-S1280:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.42652 | 144.49 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45224 | 153.4 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.48507 | 165.93 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.61409 | 214.64 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.61409 | 217.49 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.61409 | 217.72 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 115.33 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 115.33 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 115.33 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 171.38 | Potential P4 Event - POI 640590_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 171.99 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 172.35 | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 172.36 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 172.36 | P42:345:LES:L3503::103&ROKEBY.MOORE.CB3003:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 172.36 | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 172.36 | Potential P4 Event - POI 640374_7 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 172.37 | Potential P4 Event - POI 640525_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 172.37 | Potential P4 Event - POI 640588_8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.30415 | 152.65 | Potential P4 Event - POI 640590_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31082 | 152.15 | Potential P4 Event - POI 640525_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31082 | 152.2 | Potential P4 Event - POI 640525_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31362 | 149.78 | P12:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31405 | 152.24 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31412 | 150.07 | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31412 | 150.09 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31412 | 150.77 | Potential P4 Event - POI 532772_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31414 | 150.7 | P23:345:WERE:STRA-345-634-2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31415 | 150.76 | P12:345:WERE:HOYT-STRA-345:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31419 | 149.4 | P21:345:MEC-OPPD:AUTO-SINGLE:CBLUFFS3:S34563:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3142 | 149.7 | P42:345:MEC-OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3142 | 149.7 | P45:345:OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31421 | 149.49 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31422 | 150.94 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 148.84 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 148.86 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 148.86 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 148.89 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 148.91 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 148.91 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 148.91 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 148.93 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 148.93 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 148.93 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 148.98 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 148.99 | P23:500:EAI-TVA:NBF_WEST M~1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 148.99 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 149.04 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 149.26 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 149.32 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 149.34 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 149.36 | P23:345:AMMO:::24SPENCERCREEK:EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31423 | 149.47 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 148.55 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 148.58 | 338342 1EAI DELLCT1 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 148.58 | 338343 1EAI DELLCT2 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 148.58 | 515894 THUNDER7 345 765480 GEN-2021-019 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 148.58 | 532772 STRANGR7 345 3WXFMR STRANGR TX-3 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 148.9 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 148.91 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 148.93 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 148.95 | P12:HV:EES::6DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 148.97 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.03 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.05 | 640119 COL.COG7 115 640028 COLCOG1G 13.8 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.08 | 48465 J1846 SUB 230 3WXFMR J1846 SUB 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.09 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.1 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.1 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.26 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.32 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.32 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.37 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.41 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.42 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.44 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.44 | P13:MR#2 GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.48 | 775961 GEN-2023-199 230 775962 G23-199XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.48 | GEN-2023-199_POI_640386_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.61 | 760789 G17-201XFMR1 34.5 760788 GEN-2017-201 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.61 | GEN-2017-201_POI_640226_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.75 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.82 | P11:115:XEL:HBR #6 7 8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 149.85 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 150.12 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 150.18 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 150.19 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 150.19 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 150.29 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 150.51 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 150.62 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 150.72 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 150.73 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 150.74 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 150.85 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 150.98 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 151.23 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 152.1 | Potential P4 Event - POI 640588_8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 152.15 | 640112 CLATONA9 34.5 3WXFMR CLATONIA T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31424 | 156.08 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31425 | 149.07 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31427 | 148.86 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31428 | 148.83 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31428 | 149.06 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31428 | 149.09 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31429 | 148.96 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31482 | 150.36 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31482 | 150.42 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31482 | 150.95 | Potential P4 Event - POI 640065_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31522 | 150 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31794 | 150.02 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.32197 | 152.71 | P12:161:OPPD:HUMBOLT-S1280:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.32998 | 151.52 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34988 | 161.02 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34988 | 163.47 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34988 | 163.48 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.37528 | 174.38 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.55878 | 271.68 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.15417 | 106.27 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 114.02 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 114.02 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 114.02 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 171.18 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 171.18 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 171.52 | Potential P4 Event - POI 640590_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 171.61 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 171.62 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 417 | 417 | 1 | 171.62 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.21495 | 112.6 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.21495 | 112.6 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.21495 | 112.6 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.21495 | 112.6 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.21495 | 113.1 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.21495 | 113.13 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.21495 | 113.14 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.21495 | 113.18 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.21495 | 119.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.04308 | 102.79 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 478 | 478 | 0.04308 | 102.79 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.04308 | 103.02 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 478 | 478 | 0.04308 | 103.02 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.0307 | 145.76 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.05636 | 174.44 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.0653 | 152.27 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.0653 | 152.28 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.0653 | 152.28 | Potential P4 Event - POI 525832_2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.0653 | 152.28 | Potential P4 Event - POI 525832_5 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.07336 | 143.43 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.07602 | 140.1 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 134.94 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.17 | 546653 NEARMAN5 161 772721 GEN-2023-037 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.17 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.17 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.18 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.18 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.18 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.19 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.19 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.22 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.22 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.22 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.22 | GEN-2006-002_POI_511541_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.22 | P11:20:AMMO:1LAB G1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.22 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.23 | P13:MR#2 GSU | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.24 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.24 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.25 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.26 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.27 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.27 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.27 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.28 | 640588 TURTLE.CRK 3 345 640589 SHOLES.W 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.29 | P11:024:DPC:ALMA2:6 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.32 | P11:345:WERE:EMPR5-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.33 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.35 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.36 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.38 | P23:345:XEL:8H14 PRI | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.39 | P23:345:XEL:8H17 PRI AS | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.41 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.42 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.45 | P23:345:XEL:8N22 SHC | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.48 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.48 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.49 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.49 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.49 | P23:345:MEC:CBEC 908 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.5 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.51 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.54 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.54 | P23:345:MEC:CBEC 905 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.56 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.59 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.59 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.59 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.61 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.62 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.63 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.67 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.67 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 135.86 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 136.95 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 136.95 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 146.51 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 146.51 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.079 | 146.51 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.07901 | 135.16 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.07901 | 135.19 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.07901 | 135.22 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.07901 | 135.24 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.07901 | 135.3 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.07902 | 135.32 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.07907 | 135.37 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.07917 | 135.34 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.0804 | 137.79 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.0804 | 138.43 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.08068 | 150.33 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.08132 | 136.71 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.08134 | 139.57 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.08386 | 141 | P12:115:SPS:V37_1_CASTRO_PLANTX:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.08455 | 139.08 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.08455 | 139.08 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.08455 | 139.13 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.08678 | 145.25 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.08678 | 145.32 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.08678 | 145.32 | Potential P4 Event - POI 774180_0 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.08678 | 145.32 | Potential P4 Event - POI 774180_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.09056 | 141.81 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-228 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.11173 | 170.16 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.1606 | 116.97 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.1606 | 116.97 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 905 | 1059 | 0.1606 | 116.97 | Potential P4 Event - POI 508359_5 | TDF Impact | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 169 | 169 | 0.10056 | 100.24 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 169 | 169 | 0.10056 | 100.24 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 169 | 169 | 0.10056 | 100.32 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 169 | 169 | 0.10056 | 100.32 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 169 | 169 | 0.1037 | 101.52 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 169 | 169 | 0.1037 | 101.52 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.38791 | 112.6 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.38791 | 112.6 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.38791 | 112.6 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.38791 | 112.6 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.38791 | 113.1 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.38791 | 113.13 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.38791 | 113.14 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.38791 | 113.18 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.38791 | 119.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 183 | 201 | 0.06766 | 100.32 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 183 | 201 | 0.06766 | 100.32 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.06213 | 100.04 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.06213 | 100.04 | Potential P4 Event - POI 515800_13 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.06213 | 101.26 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.06213 | 101.26 | Potential P4 Event - POI 514801_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.06213 | 101.28 | P42:345:OKGE:SB_MICO7312:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.06213 | 101.28 | Potential P4 Event - POI 514801_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.06766 | 103.56 | P42:345:OKGE:SB_GRNT7313:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 183 | 201 | 0.06766 | 103.56 | Potential P4 Event - POI 515800_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03007 | 105.47 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03034 | 106.36 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0309 | 107.1 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0309 | 107.1 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03097 | 103.37 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03102 | 107.82 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03102 | 107.97 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03103 | 103.45 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03106 | 103.25 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03117 | 103.24 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03119 | 103.09 | P12:HV:EES::3COUCH%:3LEWISVILLE#:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03119 | 103.17 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03119 | 103.32 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0312 | 103.3 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0312 | 103.3 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03121 | 103.28 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03123 | 104.39 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.15 | 300120 5THMHILB1 161 301504 5THOMHLGSU1 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.15 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.16 | 344011 7HUGHES 345 344012 7HPW-N 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.2 | P21:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.22 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.26 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.26 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.28 | 546653 NEARMAN5 161 772721 GEN-2023-037 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.3 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.34 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.37 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.37 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.38 | P11:20:AMMO:1LAB G1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.38 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.41 | P13:MR#2 GSU | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.42 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.42 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.44 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.46 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.47 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.49 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.53 | 640588 TURTLE.CRK 3 345 640589 SHOLES.W 3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.54 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.55 | P11:024:DPC:ALMA2:6 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.66 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.71 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.78 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.79 | 773981 GEN-2023-100 345 773985 G23-100XFMR2 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.79 | P23:345:XEL:8H14 PRI | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.8 | P23:345:XEL:8H17 PRI AS | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.84 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.88 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.96 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.96 | P23:345:XEL:8N22 SHC | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.02 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.03 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.04 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.05 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.05 | P23:345:MEC:CBEC 908 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.07 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.11 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.17 | P23:345:MEC:CBEC 905 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.18 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.23 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.3 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.3 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.31 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.38 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.41 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.69 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.7 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.77 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 105.07 | 772281 GEN-2023-015 345 772282 G23-015XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 105.51 | GEN-2023-102_POI_515852_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 105.67 | GEN-2008-051_POI_523961_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 107.37 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0313 | 103.34 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03168 | 106.98 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03183 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03217 | 103.62 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03315 | 103.84 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04045 | 123.96 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04045 | 124.18 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04045 | 124.18 | Potential P4 Event - POI 515458_6 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04045 | 124.18 | Potential P4 Event - POI 515458_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04045 | 124.18 | Potential P4 Event - POI 774180_0 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04045 | 124.18 | Potential P4 Event - POI 774180_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04045 | 124.51 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04275 | 108.56 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04275 | 108.56 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04275 | 108.6 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04275 | 109.91 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05054 | 118.76 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0552 | 117.64 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0552 | 118.05 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0552 | 118.05 | Potential P4 Event - POI 514801_4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0552 | 118.14 | Potential P4 Event - POI 514801_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03007 | 105.98 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03034 | 106.81 | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03076 | 103.58 | P12:EHV:EES::7SAREPTA%:7EL DORADO:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0309 | 107.82 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0309 | 107.83 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03097 | 104.03 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03102 | 108.34 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03102 | 108.48 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03103 | 104.12 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03106 | 103.91 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03117 | 103.9 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03119 | 103.84 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03119 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0312 | 103.96 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0312 | 103.96 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03121 | 103.94 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03123 | 105.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.81 | 300120 5THMHILB1 161 301504 5THOMHLGSU1 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.81 | 655554 KNGSBURY-ER7 115 772221 GEN-2023-012 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.82 | 344011 7HUGHES 345 344012 7HPW-N 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.87 | P21:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.89 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.92 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.92 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.94 | 546653 NEARMAN5 161 772721 GEN-2023-037 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.96 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 103.99 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.01 | P23:345:OTP::TWIN BRKS 3:BRKY_V2021:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.02 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.02 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.04 | P11:20:AMMO:1LAB G1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.04 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.08 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.08 | P13:MR#2 GSU | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.09 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.11 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.13 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.14 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.16 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.17 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.19 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.2 | 640588 TURTLE.CRK 3 345 640589 SHOLES.W 3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.22 | P11:024:DPC:ALMA2:6 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.33 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.37 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.44 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.44 | P23:345:XEL:8H14 PRI | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.45 | 773981 GEN-2023-100 345 773985 G23-100XFMR2 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.46 | P23:345:XEL:8H17 PRI AS | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.48 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.51 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.61 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.61 | P23:345:XEL:8N22 SHC | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.67 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.68 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.69 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.7 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.7 | P23:345:MEC:CBEC 908 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.71 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.76 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.82 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.82 | P23:345:MEC:CBEC 905 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.87 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.94 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.94 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 104.94 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 105.01 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 105.05 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 105.29 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 105.31 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 105.44 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 105.74 | 772281 GEN-2023-015 345 772282 G23-015XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 106.15 | GEN-2023-102_POI_515852_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 106.64 | GEN-2008-051_POI_523961_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03124 | 107.84 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0313 | 104 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03168 | 107.52 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03183 | 104.24 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03217 | 104.28 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.03315 | 104.48 | P12:138:WFEC:ANADRKO_SUNSHINE:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04045 | 124.39 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04045 | 124.74 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04045 | 124.74 | Potential P4 Event - POI 515458_6 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04045 | 124.74 | Potential P4 Event - POI 515458_9 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04045 | 124.74 | Potential P4 Event - POI 774180_0 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04045 | 124.74 | Potential P4 Event - POI 774180_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04045 | 125.13 | 525832 TUCO_INT 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04275 | 108.91 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04275 | 108.91 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04275 | 108.95 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.04275 | 110.15 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.05054 | 118.5 | P42:345:OKGE:SB_GRNT7381:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0552 | 117.39 | P12:345:OKGE:BKRBKR367:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0552 | 117.79 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0552 | 117.79 | Potential P4 Event - POI 514801_3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-229 | FROM->TO | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 516 | 559 | 0.0552 | 117.86 | Potential P4 Event - POI 514801_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07051 | 112.6 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07051 | 112.6 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07051 | 112.6 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07051 | 112.6 | Potential P4 Event - POI 511568_3 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07051 | 113.1 | Potential P4 Event - POI 764115_1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07051 | 113.13 | Potential P4 Event - POI 764115_2 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07051 | 113.14 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07051 | 113.18 | Potential P4 Event - POI 511568_4 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 1195 | 1195 | 0.07051 | 119.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.15706 | 145.76 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 134.94 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.17 | 546653 NEARMAN5 161 772721 GEN-2023-037 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.17 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.17 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.18 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.19 | 542940 ATLNTIC7 345 765115 GEN-2020-057 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.22 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.22 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.22 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.22 | GEN-2006-002_POI_511541_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.22 | P11:20:AMMO:1LAB G1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.22 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.23 | P13:MR#2 GSU | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.24 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.24 | 659130 CHAPELLE-BE3 345 774081 GEN-2023-105 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.26 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.27 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.27 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.27 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.28 | 640588 TURTLE.CRK 3 345 640589 SHOLES.W 3 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.29 | P11:024:DPC:ALMA2:6 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.32 | P11:345:WERE:EMPR5-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.35 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.36 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.38 | P23:345:XEL:8H14 PRI | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.39 | P23:345:XEL:8H17 PRI AS | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.41 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.42 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.45 | P23:345:XEL:8N22 SHC | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.48 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.48 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.49 | 640588 TURTLE.CRK 3 345 776301 GEN-2023-216 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.49 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.49 | P23:345:MEC:CBEC 908 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.5 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.51 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.54 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.56 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.59 | 640088 BPS SUB7 115 3WXFMR BPS_345_115 T1 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.59 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.59 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.61 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.63 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.67 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.67 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 135.86 | 531449 HOLCOMB7 345 775421 GEN-2023-172 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 136.95 | 776161 GEN-2023-209 115 776162 G23-209XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 136.95 | GEN-2023-209_POI_524414_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 146.51 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 146.51 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20536 | 146.51 | GEN-2023-086_POI_773700_Generator_outage | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20537 | 135.16 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20537 | 135.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20537 | 135.18 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20537 | 135.18 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20537 | 135.19 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20537 | 135.19 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20537 | 135.22 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20537 | 135.24 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20537 | 135.25 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20537 | 135.3 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20537 | 135.32 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20537 | 135.33 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20537 | 135.54 | P23:345:MEC:CBEC 905 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20537 | 135.62 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20539 | 135.37 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20543 | 135.34 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20586 | 137.79 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20586 | 138.43 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20611 | 139.57 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20627 | 136.71 | 515800 GRACMNT7 345 769260 G22-114-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20751 | 139.08 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20751 | 139.08 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.20751 | 139.13 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21368 | 150.33 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2147 | 141 | P12:115:SPS:V37_1_CASTRO_PLANTX:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21727 | 143.43 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21839 | 145.25 | P12:345:OKGE:BKRBKR429:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21839 | 145.32 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21839 | 145.32 | Potential P4 Event - POI 774180_0 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.21839 | 145.32 | Potential P4 Event - POI 774180_1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22005 | 141.81 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22434 | 174.44 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22749 | 157.27 | Potential P4 Event - POI 762216_14 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.22749 | 157.27 | Potential P4 Event - POI 762467_7 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.23115 | 140.1 | 764866 G20-059-TAP 345 776700 G23-236-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2508 | 152.27 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2508 | 152.28 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2508 | 152.28 | Potential P4 Event - POI 525832_2 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.2508 | 152.28 | Potential P4 Event - POI 525832_5 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 321.1 | 321.1 | 0.26616 | 170.16 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | TDF Impact | Newhart - Plant X 230 kV Ckt 1 Rebuild
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 251 | 251 | 0.07132 | 110.28 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-236 | FROM->TO | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 251 | 251 | 0.07132 | 109.5 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-033 | FROM->TO | 541210 MARTCTY5 161 543002 MARTCIT5 161 1 | 311 | 334 | 0.03073 | 105.85 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Martin City (East) - Martin City (West) 161 kV Terminal Equipment
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-135 | FROM->TO | 508808 LONGWD 4 138 997975 LONGWOOD 138 1 | 451.7 | 478.4 | 0.04722 | 107.81 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-135 | FROM->TO | 508808 LONGWD 4 138 997975 LONGWOOD 138 1 | 451.7 | 478.4 | 0.04722 | 107.81 | P42:345:AEPW:SW SHREVEPORT CB 10500 NBTB+FAULT:::: | TDF Impact | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-135 | FROM->TO | 508809 LONGWD 7 345 997975 LONGWOOD 138 1 | 451.7 | 478.4 | 0.04722 | 109.46 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-135 | FROM->TO | 508809 LONGWD 7 345 997975 LONGWOOD 138 1 | 451.7 | 478.4 | 0.04722 | 109.46 | P42:345:AEPW:SW SHREVEPORT CB 10500 NBTB+FAULT:::: | TDF Impact | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-149 | FROM->TO | 541210 MARTCTY5 161 543002 MARTCIT5 161 1 | 311 | 334 | 0.17054 | 105.85 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Martin City (East) - Martin City (West) 161 kV Terminal Equipment
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-169 | FROM->TO | 541210 MARTCTY5 161 543002 MARTCIT5 161 1 | 311 | 334 | 0.03154 | 105.85 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Martin City (East) - Martin City (West) 161 kV Terminal Equipment
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-212 | FROM->TO | 508808 LONGWD 4 138 997975 LONGWOOD 138 1 | 451.7 | 478.4 | 0.04326 | 107.81 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-212 | FROM->TO | 508808 LONGWD 4 138 997975 LONGWOOD 138 1 | 451.7 | 478.4 | 0.04326 | 107.81 | P42:345:AEPW:SW SHREVEPORT CB 10500 NBTB+FAULT:::: | TDF Impact | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-212 | FROM->TO | 508809 LONGWD 7 345 997975 LONGWOOD 138 1 | 451.7 | 478.4 | 0.04326 | 109.46 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-212 | FROM->TO | 508809 LONGWD 7 345 997975 LONGWOOD 138 1 | 451.7 | 478.4 | 0.04326 | 109.46 | P42:345:AEPW:SW SHREVEPORT CB 10500 NBTB+FAULT:::: | TDF Impact | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-227 | FROM->TO | 508808 LONGWD 4 138 997975 LONGWOOD 138 1 | 451.7 | 478.4 | 0.03409 | 107.81 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-227 | FROM->TO | 508808 LONGWD 4 138 997975 LONGWOOD 138 1 | 451.7 | 478.4 | 0.03409 | 107.81 | P42:345:AEPW:SW SHREVEPORT CB 10500 NBTB+FAULT:::: | TDF Impact | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-227 | FROM->TO | 508809 LONGWD 7 345 997975 LONGWOOD 138 1 | 451.7 | 478.4 | 0.03409 | 109.46 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 24SP | GEN-2023-227 | FROM->TO | 508809 LONGWD 7 345 997975 LONGWOOD 138 1 | 451.7 | 478.4 | 0.03409 | 109.46 | P42:345:AEPW:SW SHREVEPORT CB 10500 NBTB+FAULT:::: | TDF Impact | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-033 | FROM->TO | 541210 MARTCTY5 161 543002 MARTCIT5 161 1 | 311 | 334 | 0.03599 | 111.68 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Martin City (East) - Martin City (West) 161 kV Terminal Equipment
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-033 | FROM->TO | 541210 MARTCTY5 161 543002 MARTCIT5 161 1 | 311 | 334 | 0.03636 | 105.67 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Martin City (East) - Martin City (West) 161 kV Terminal Equipment
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-135 | FROM->TO | 508808 LONGWD 4 138 997975 LONGWOOD 138 1 | 451.7 | 478.4 | 0.05708 | 100.74 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-135 | FROM->TO | 508808 LONGWD 4 138 997975 LONGWOOD 138 1 | 451.7 | 478.4 | 0.05708 | 100.74 | P42:345:AEPW:SW SHREVEPORT CB 10500 NBTB+FAULT:::: | TDF Impact | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-135 | FROM->TO | 508809 LONGWD 7 345 997975 LONGWOOD 138 1 | 451.7 | 478.4 | 0.05708 | 102.12 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-135 | FROM->TO | 508809 LONGWD 7 345 997975 LONGWOOD 138 1 | 451.7 | 478.4 | 0.05708 | 102.12 | P42:345:AEPW:SW SHREVEPORT CB 10500 NBTB+FAULT:::: | TDF Impact | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-149 | FROM->TO | 541210 MARTCTY5 161 543002 MARTCIT5 161 1 | 311 | 334 | 0.16813 | 105.67 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Martin City (East) - Martin City (West) 161 kV Terminal Equipment
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-149 | FROM->TO | 541210 MARTCTY5 161 543002 MARTCIT5 161 1 | 311 | 334 | 0.17599 | 111.68 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Martin City (East) - Martin City (West) 161 kV Terminal Equipment
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-151 | FROM->TO | 508808 LONGWD 4 138 997975 LONGWOOD 138 1 | 451.7 | 478.4 | 0.03682 | 100.74 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-151 | FROM->TO | 508808 LONGWD 4 138 997975 LONGWOOD 138 1 | 451.7 | 478.4 | 0.03682 | 100.74 | P42:345:AEPW:SW SHREVEPORT CB 10500 NBTB+FAULT:::: | TDF Impact | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-151 | FROM->TO | 508809 LONGWD 7 345 997975 LONGWOOD 138 1 | 451.7 | 478.4 | 0.03682 | 102.12 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-151 | FROM->TO | 508809 LONGWD 7 345 997975 LONGWOOD 138 1 | 451.7 | 478.4 | 0.03682 | 102.12 | P42:345:AEPW:SW SHREVEPORT CB 10500 NBTB+FAULT:::: | TDF Impact | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-169 | FROM->TO | 541210 MARTCTY5 161 543002 MARTCIT5 161 1 | 311 | 334 | 0.03657 | 111.68 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Martin City (East) - Martin City (West) 161 kV Terminal Equipment
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-169 | FROM->TO | 541210 MARTCTY5 161 543002 MARTCIT5 161 1 | 311 | 334 | 0.03684 | 105.67 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Martin City (East) - Martin City (West) 161 kV Terminal Equipment
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-212 | FROM->TO | 508808 LONGWD 4 138 997975 LONGWOOD 138 1 | 451.7 | 478.4 | 0.05313 | 100.74 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-212 | FROM->TO | 508808 LONGWD 4 138 997975 LONGWOOD 138 1 | 451.7 | 478.4 | 0.05313 | 100.74 | P42:345:AEPW:SW SHREVEPORT CB 10500 NBTB+FAULT:::: | TDF Impact | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-212 | FROM->TO | 508809 LONGWD 7 345 997975 LONGWOOD 138 1 | 451.7 | 478.4 | 0.05313 | 102.12 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-212 | FROM->TO | 508809 LONGWD 7 345 997975 LONGWOOD 138 1 | 451.7 | 478.4 | 0.05313 | 102.12 | P42:345:AEPW:SW SHREVEPORT CB 10500 NBTB+FAULT:::: | TDF Impact | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-219 | FROM->TO | 533301 EAST ST3 115 533309 WEMPORI3 115 1 | 92 | 92 | 0.10322 | 100.77 | P12:115:WERE:LANG-WEMP-115:::HV: | TDF Impact | Rebuild the EAST ST3 to WEMPORI3 115kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-219 | FROM->TO | 533301 EAST ST3 115 533309 WEMPORI3 115 1 | 92 | 92 | 0.10322 | 107.96 | 533304 LANG 3 115 533307 PRAIRIE3 115 1 | TDF Impact | Rebuild the EAST ST3 to WEMPORI3 115kV Line 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-227 | FROM->TO | 508808 LONGWD 4 138 997975 LONGWOOD 138 1 | 451.7 | 478.4 | 0.04396 | 100.74 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-227 | FROM->TO | 508808 LONGWD 4 138 997975 LONGWOOD 138 1 | 451.7 | 478.4 | 0.04396 | 100.74 | P42:345:AEPW:SW SHREVEPORT CB 10500 NBTB+FAULT:::: | TDF Impact | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-227 | FROM->TO | 508809 LONGWD 7 345 997975 LONGWOOD 138 1 | 451.7 | 478.4 | 0.04396 | 102.12 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27SP | GEN-2023-227 | FROM->TO | 508809 LONGWD 7 345 997975 LONGWOOD 138 1 | 451.7 | 478.4 | 0.04396 | 102.12 | P42:345:AEPW:SW SHREVEPORT CB 10500 NBTB+FAULT:::: | TDF Impact | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
Thermal | DISIS-2023-001 CF | 00NR | 1 | 27WP | GEN-2023-149 | FROM->TO | 541210 MARTCTY5 161 543002 MARTCIT5 161 1 | 311 | 334 | 0.14509 | 103.11 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Martin City (East) - Martin City (West) 161 kV Terminal Equipment
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-009 |  | Non-Converged |  |  | 0.12602 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-022 |  | Non-Converged |  |  | 0.03829 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-027 |  | Non-Converged |  |  | 0.0382 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-038 |  | Non-Converged |  |  | 0.03843 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-063 |  | Non-Converged |  |  | 0.03903 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-069 |  | Non-Converged |  |  | 0.09639 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-088 |  | Non-Converged |  |  | 0.06784 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-092 |  | Non-Converged |  |  | 0.12697 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.07571 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.08727 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.08727 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-177 |  | Non-Converged |  |  | 0.03604 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-210 |  | Non-Converged |  |  | 0.05455 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-213 |  | Non-Converged |  |  | 0.03624 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34747 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.12053 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-009 |  | Non-Converged |  |  | 0.12602 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-022 |  | Non-Converged |  |  | 0.03829 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-027 |  | Non-Converged |  |  | 0.0382 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-038 |  | Non-Converged |  |  | 0.03843 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-063 |  | Non-Converged |  |  | 0.03903 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-069 |  | Non-Converged |  |  | 0.09639 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-088 |  | Non-Converged |  |  | 0.06784 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-092 |  | Non-Converged |  |  | 0.12697 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.07571 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.08727 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.08727 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-177 |  | Non-Converged |  |  | 0.03604 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-210 |  | Non-Converged |  |  | 0.05455 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-213 |  | Non-Converged |  |  | 0.03624 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34747 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.12053 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34747 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34747 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | ASGI-2023-001 |  | Non-Converged |  |  | 0.11296 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-001 |  | Non-Converged |  |  | 0.13876 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.05241 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-081 |  | Non-Converged |  |  | 0.09503 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.0403 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.05082 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-158 |  | Non-Converged |  |  | 0.83714 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-159 |  | Non-Converged |  |  | 0.83714 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-201 |  | Non-Converged |  |  | 0.10905 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-203 |  | Non-Converged |  |  | 0.16092 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.04326 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.06398 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-236 |  | Non-Converged |  |  | 0.11915 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | G17-151-Tap to G18-015-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | G17-151-Tap to G18-015-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | G17-151-Tap to G18-015-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | G17-151-Tap to G18-015-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | G17-151-Tap to G18-015-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | G17-151-Tap to G18-015-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | G17-151-Tap to G18-015-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | G17-151-Tap to G18-015-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | G17-151-Tap to G18-015-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | G17-151-Tap to G18-015-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.65253 |  | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | G17-151-Tap to G18-015-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | G17-151-Tap to G18-015-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-219 |  | Non-Converged |  |  | 0.68012 |  | 533304 LANG 3 115 767120 G22-007-TAP 115 1 | TDF Impact | Build 2nd LANG 3 to G22-007-TAP 115 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | G17-151-Tap to G18-015-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | G17-151-Tap to G18-015-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | G17-151-Tap to G18-015-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | G17-151-Tap to G18-015-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | G17-151-Tap to G18-015-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | G17-151-Tap to G18-015-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | G17-151-Tap to G18-015-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | G17-151-Tap to G18-015-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | G17-151-Tap to G18-015-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | G17-151-Tap to G18-015-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.65253 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | G17-151-Tap to G18-015-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | G17-151-Tap to G18-015-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34747 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34747 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34747 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34747 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34747 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34747 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34747 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34747 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-009 |  | Non-Converged |  |  | 0.12602 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-022 |  | Non-Converged |  |  | 0.03829 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-027 |  | Non-Converged |  |  | 0.0382 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-038 |  | Non-Converged |  |  | 0.03843 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-063 |  | Non-Converged |  |  | 0.03903 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-069 |  | Non-Converged |  |  | 0.09639 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-088 |  | Non-Converged |  |  | 0.06784 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-092 |  | Non-Converged |  |  | 0.12697 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.07571 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.08727 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.08727 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-177 |  | Non-Converged |  |  | 0.03604 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-210 |  | Non-Converged |  |  | 0.05455 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-213 |  | Non-Converged |  |  | 0.03624 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34747 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.12053 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-009 |  | Non-Converged |  |  | 0.12602 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-022 |  | Non-Converged |  |  | 0.03829 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-027 |  | Non-Converged |  |  | 0.0382 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-038 |  | Non-Converged |  |  | 0.03843 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-063 |  | Non-Converged |  |  | 0.03903 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-069 |  | Non-Converged |  |  | 0.09639 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-088 |  | Non-Converged |  |  | 0.06784 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-092 |  | Non-Converged |  |  | 0.12697 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.07571 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.08727 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.08727 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-177 |  | Non-Converged |  |  | 0.03604 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-210 |  | Non-Converged |  |  | 0.05455 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-213 |  | Non-Converged |  |  | 0.03624 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34747 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.12053 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34747 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-009 |  | Non-Converged |  |  | 0.06285 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-038 |  | Non-Converged |  |  | 0.03488 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-063 |  | Non-Converged |  |  | 0.03063 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-069 |  | Non-Converged |  |  | 0.04467 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-092 |  | Non-Converged |  |  | 0.06423 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.14059 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.14059 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34747 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-009 |  | Non-Converged |  |  | 0.04755 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-069 |  | Non-Converged |  |  | 0.0338 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-092 |  | Non-Converged |  |  | 0.0486 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.10637 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.10637 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34747 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34747 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34747 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 762216_10 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 762216_10 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 762216_10 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 762216_10 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 762216_10 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 762216_10 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | Potential P4 Event - POI 762216_10 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 762216_10 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 762216_10 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 762216_10 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.65253 |  | Potential P4 Event - POI 762216_10 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 762216_10 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 762216_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 762216_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 762216_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 762216_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 762216_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 762216_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | Potential P4 Event - POI 762216_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 762216_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 762216_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 762216_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.65253 |  | Potential P4 Event - POI 762216_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 762216_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 762216_14 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 762216_14 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 762216_14 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 762216_14 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 762216_14 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 762216_14 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | Potential P4 Event - POI 762216_14 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 762216_14 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 762216_14 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 762216_14 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.65253 |  | Potential P4 Event - POI 762216_14 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 762216_14 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 762216_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 762216_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 762216_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 762216_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 762216_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 762216_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | Potential P4 Event - POI 762216_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 762216_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 762216_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 762216_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.65253 |  | Potential P4 Event - POI 762216_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 762216_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 762216_7 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 762216_7 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 762216_7 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 762216_7 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 762216_7 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 762216_7 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | Potential P4 Event - POI 762216_7 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 762216_7 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 762216_7 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 762216_7 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.65253 |  | Potential P4 Event - POI 762216_7 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 762216_7 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 762467_1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 762467_1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 762467_1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 762467_1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 762467_1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 762467_1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | Potential P4 Event - POI 762467_1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 762467_1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 762467_1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 762467_1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.65253 |  | Potential P4 Event - POI 762467_1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 762467_1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 762467_4 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 762467_4 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 762467_4 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 762467_4 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 762467_4 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 762467_4 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | Potential P4 Event - POI 762467_4 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 762467_4 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 762467_4 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 762467_4 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.65253 |  | Potential P4 Event - POI 762467_4 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 762467_4 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 762467_7 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 762467_7 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 762467_7 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 762467_7 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 762467_7 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 762467_7 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | Potential P4 Event - POI 762467_7 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 762467_7 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 762467_7 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 762467_7 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.65253 |  | Potential P4 Event - POI 762467_7 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 762467_7 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 762467_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 762467_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 762467_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 762467_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 762467_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 762467_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | Potential P4 Event - POI 762467_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 762467_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 762467_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 762467_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 1 |  | Potential P4 Event - POI 762467_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 762467_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34747 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34747 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34747 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34747 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34747 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34747 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.24931 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10123 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25803 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04499 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06362 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-150 |  | Non-Converged |  |  | 0.04028 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04348 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.1214 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34747 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-009 |  | Non-Converged |  |  | 0.12955 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.2493 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-022 |  | Non-Converged |  |  | 0.0346 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-027 |  | Non-Converged |  |  | 0.03884 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-038 |  | Non-Converged |  |  | 0.03365 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-063 |  | Non-Converged |  |  | 0.0398 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-069 |  | Non-Converged |  |  | 0.09931 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10134 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-088 |  | Non-Converged |  |  | 0.07113 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-092 |  | Non-Converged |  |  | 0.13029 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04822 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25822 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04822 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06551 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-134 |  | Non-Converged |  |  | 0.03102 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-150 |  | Non-Converged |  |  | 0.08005 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-161 |  | Non-Converged |  |  | 0.03283 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-164 |  | Non-Converged |  |  | 0.09153 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-165 |  | Non-Converged |  |  | 0.09153 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-177 |  | Non-Converged |  |  | 0.03152 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.12152 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-210 |  | Non-Converged |  |  | 0.05808 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-213 |  | Non-Converged |  |  | 0.03684 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34724 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-229 |  | Non-Converged |  |  | 0.12189 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-009 |  | Non-Converged |  |  | 0.12955 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.2493 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-022 |  | Non-Converged |  |  | 0.0346 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-027 |  | Non-Converged |  |  | 0.03884 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-038 |  | Non-Converged |  |  | 0.03365 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-063 |  | Non-Converged |  |  | 0.0398 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-069 |  | Non-Converged |  |  | 0.09931 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10134 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-088 |  | Non-Converged |  |  | 0.07113 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-092 |  | Non-Converged |  |  | 0.13029 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04822 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25822 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04822 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06551 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-134 |  | Non-Converged |  |  | 0.03102 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-150 |  | Non-Converged |  |  | 0.08005 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-161 |  | Non-Converged |  |  | 0.03283 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-164 |  | Non-Converged |  |  | 0.09153 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-165 |  | Non-Converged |  |  | 0.09153 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-177 |  | Non-Converged |  |  | 0.03152 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.12152 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-210 |  | Non-Converged |  |  | 0.05808 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-213 |  | Non-Converged |  |  | 0.03684 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34724 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-229 |  | Non-Converged |  |  | 0.12189 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.2493 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10134 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04822 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25822 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04822 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06551 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-150 |  | Non-Converged |  |  | 0.0374 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04054 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04054 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.12152 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34724 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03069 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.2493 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10134 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04822 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25822 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04822 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06551 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-150 |  | Non-Converged |  |  | 0.0374 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04054 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04054 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.12152 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34724 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03069 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | ASGI-2023-001 |  | Non-Converged |  |  | 0.11335 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-001 |  | Non-Converged |  |  | 0.13891 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.05268 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-081 |  | Non-Converged |  |  | 0.09536 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.04058 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.05109 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-158 |  | Non-Converged |  |  | 0.83741 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-159 |  | Non-Converged |  |  | 0.83741 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-201 |  | Non-Converged |  |  | 0.10937 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-203 |  | Non-Converged |  |  | 0.16113 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.04353 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.06426 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-236 |  | Non-Converged |  |  | 0.11947 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-219 |  | Non-Converged |  |  | 0.68275 |  | 533304 LANG 3 115 767120 G22-007-TAP 115 1 | TDF Impact | Build 2nd LANG 3 to G22-007-TAP 115 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.2493 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10134 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04822 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25822 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04822 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06551 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-150 |  | Non-Converged |  |  | 0.0374 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04054 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04054 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.12152 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34724 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03069 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.2493 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10134 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04822 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25822 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04822 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06551 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-150 |  | Non-Converged |  |  | 0.0374 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04054 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04054 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.12152 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34724 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03069 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.2493 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10134 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25822 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06551 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-150 |  | Non-Converged |  |  | 0.0374 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.12152 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34724 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03069 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.2493 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10134 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25822 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06551 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-150 |  | Non-Converged |  |  | 0.0374 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.12152 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34724 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03069 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.2493 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10134 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25822 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06551 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-150 |  | Non-Converged |  |  | 0.0374 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.12152 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34724 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03069 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.2493 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10134 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25822 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06551 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-150 |  | Non-Converged |  |  | 0.0374 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.12152 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34724 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03069 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.2493 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10134 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25822 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06551 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-150 |  | Non-Converged |  |  | 0.0374 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.12152 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34724 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03069 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.2493 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10134 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25822 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06551 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-150 |  | Non-Converged |  |  | 0.0374 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.12152 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34724 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03069 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-009 |  | Non-Converged |  |  | 0.12955 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.2493 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-022 |  | Non-Converged |  |  | 0.0346 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-027 |  | Non-Converged |  |  | 0.03884 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-038 |  | Non-Converged |  |  | 0.03365 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-063 |  | Non-Converged |  |  | 0.0398 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-069 |  | Non-Converged |  |  | 0.09931 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10134 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-088 |  | Non-Converged |  |  | 0.07113 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-092 |  | Non-Converged |  |  | 0.13029 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25822 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06551 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-134 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-150 |  | Non-Converged |  |  | 0.08005 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-161 |  | Non-Converged |  |  | 0.03283 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-164 |  | Non-Converged |  |  | 0.09153 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-165 |  | Non-Converged |  |  | 0.09153 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-177 |  | Non-Converged |  |  | 0.03152 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.12152 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-210 |  | Non-Converged |  |  | 0.05808 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-213 |  | Non-Converged |  |  | 0.03684 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34724 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-229 |  | Non-Converged |  |  | 0.12189 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-009 |  | Non-Converged |  |  | 0.12955 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.2493 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-022 |  | Non-Converged |  |  | 0.0346 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-027 |  | Non-Converged |  |  | 0.03884 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-038 |  | Non-Converged |  |  | 0.03365 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-063 |  | Non-Converged |  |  | 0.0398 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-069 |  | Non-Converged |  |  | 0.09931 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10134 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-088 |  | Non-Converged |  |  | 0.07113 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-092 |  | Non-Converged |  |  | 0.13029 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25822 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06551 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-134 |  | Non-Converged |  |  | 0.03102 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-150 |  | Non-Converged |  |  | 0.08005 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-161 |  | Non-Converged |  |  | 0.03283 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-164 |  | Non-Converged |  |  | 0.09153 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-165 |  | Non-Converged |  |  | 0.09153 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-177 |  | Non-Converged |  |  | 0.03152 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.12152 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-210 |  | Non-Converged |  |  | 0.05808 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-213 |  | Non-Converged |  |  | 0.03684 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34724 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-229 |  | Non-Converged |  |  | 0.12189 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.2493 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10134 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25822 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06551 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-150 |  | Non-Converged |  |  | 0.0374 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.12152 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34724 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03069 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-009 |  | Non-Converged |  |  | 0.06471 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.2493 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-038 |  | Non-Converged |  |  | 0.0313 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-063 |  | Non-Converged |  |  | 0.03121 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-069 |  | Non-Converged |  |  | 0.04611 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10134 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-092 |  | Non-Converged |  |  | 0.06599 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25822 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06551 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-150 |  | Non-Converged |  |  | 0.03753 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-164 |  | Non-Converged |  |  | 0.14372 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-165 |  | Non-Converged |  |  | 0.14372 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.12152 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34724 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03069 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-009 |  | Non-Converged |  |  | 0.04896 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.2493 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-069 |  | Non-Converged |  |  | 0.03488 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10134 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-092 |  | Non-Converged |  |  | 0.04993 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25822 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06551 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-150 |  | Non-Converged |  |  | 0.0374 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-164 |  | Non-Converged |  |  | 0.10873 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-165 |  | Non-Converged |  |  | 0.10873 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.12152 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34724 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03069 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.2493 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10134 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25822 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06551 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-150 |  | Non-Converged |  |  | 0.0374 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.12152 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34724 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03069 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.2493 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10134 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25822 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06551 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-150 |  | Non-Converged |  |  | 0.0374 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.12152 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34724 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03069 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.2493 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10134 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25822 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06551 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-150 |  | Non-Converged |  |  | 0.0374 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.12152 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34724 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03069 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.2493 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10134 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25822 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06551 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-150 |  | Non-Converged |  |  | 0.0374 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.12152 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34724 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03069 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.2493 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10134 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25822 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06551 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-150 |  | Non-Converged |  |  | 0.0374 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.12152 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34724 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03069 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.2493 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10134 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25822 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06551 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-150 |  | Non-Converged |  |  | 0.0374 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.12152 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34724 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03069 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.2493 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10134 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25822 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06551 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-150 |  | Non-Converged |  |  | 0.0374 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.12152 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34724 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03069 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.2493 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10134 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25822 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06551 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-150 |  | Non-Converged |  |  | 0.0374 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.12152 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34724 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03069 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.2493 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.10134 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.25822 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.04822 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.06551 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-150 |  | Non-Converged |  |  | 0.0374 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-164 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-165 |  | Non-Converged |  |  | 0.04054 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.12152 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.34724 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-229 |  | Non-Converged |  |  | 0.03069 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-222 |  | Non-Converged |  |  | 0.39475 |  | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Multi - Sheldon - Monolith 115 kV
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-223 |  | Non-Converged |  |  | 0.39475 |  | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Multi - Sheldon - Monolith 115 kV
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-222 |  | Non-Converged |  |  | 0.3054 |  | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | TDF Impact | Multi - Sheldon - Monolith 115 kV
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-223 |  | Non-Converged |  |  | 0.3054 |  | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | TDF Impact | Multi - Sheldon - Monolith 115 kV
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-199 |  | Non-Converged |  |  | 0.04014 |  | P13:115-345:NPPD:T960::MOORE.CKT1:: | TDF Impact | Multi - Sheldon - Monolith 115 kV
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-216 |  | Non-Converged |  |  | 0.04086 |  | P13:115-345:NPPD:T960::MOORE.CKT1:: | TDF Impact | Multi - Sheldon - Monolith 115 kV
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-217 |  | Non-Converged |  |  | 0.04086 |  | P13:115-345:NPPD:T960::MOORE.CKT1:: | TDF Impact | Multi - Sheldon - Monolith 115 kV
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-218 |  | Non-Converged |  |  | 0.04086 |  | P13:115-345:NPPD:T960::MOORE.CKT1:: | TDF Impact | Multi - Sheldon - Monolith 115 kV
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-222 |  | Non-Converged |  |  | 0.31188 |  | P13:115-345:NPPD:T960::MOORE.CKT1:: | TDF Impact | Multi - Sheldon - Monolith 115 kV
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-223 |  | Non-Converged |  |  | 0.31188 |  | P13:115-345:NPPD:T960::MOORE.CKT1:: | TDF Impact | Multi - Sheldon - Monolith 115 kV
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-222 |  | Non-Converged |  |  | 0.3054 |  | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Multi - Sheldon - Monolith 115 kV
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-223 |  | Non-Converged |  |  | 0.3054 |  | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Multi - Sheldon - Monolith 115 kV
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-199 |  | Non-Converged |  |  | 0.04014 |  | P13:115-345:NPPD:MOORE 3:T1::: | TDF Impact | Multi - Sheldon - Monolith 115 kV
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-216 |  | Non-Converged |  |  | 0.04086 |  | P13:115-345:NPPD:MOORE 3:T1::: | TDF Impact | Multi - Sheldon - Monolith 115 kV
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-217 |  | Non-Converged |  |  | 0.04086 |  | P13:115-345:NPPD:MOORE 3:T1::: | TDF Impact | Multi - Sheldon - Monolith 115 kV
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-218 |  | Non-Converged |  |  | 0.04086 |  | P13:115-345:NPPD:MOORE 3:T1::: | TDF Impact | Multi - Sheldon - Monolith 115 kV
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-222 |  | Non-Converged |  |  | 0.31188 |  | P13:115-345:NPPD:MOORE 3:T1::: | TDF Impact | Multi - Sheldon - Monolith 115 kV
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-223 |  | Non-Converged |  |  | 0.31188 |  | P13:115-345:NPPD:MOORE 3:T1::: | TDF Impact | Multi - Sheldon - Monolith 115 kV
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.13823 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.13976 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.11388 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-009 |  | Non-Converged |  |  | 0.12445 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.12215 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-022 |  | Non-Converged |  |  | 0.03865 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-027 |  | Non-Converged |  |  | 0.03749 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-038 |  | Non-Converged |  |  | 0.03781 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.11388 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-063 |  | Non-Converged |  |  | 0.03855 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-069 |  | Non-Converged |  |  | 0.09414 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.13649 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-088 |  | Non-Converged |  |  | 0.0658 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-092 |  | Non-Converged |  |  | 0.12518 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-100 |  | Non-Converged |  |  | 0.04496 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.13088 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-102 |  | Non-Converged |  |  | 0.04496 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.06316 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.11388 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.11388 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-150 |  | Non-Converged |  |  | 0.07502 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.12586 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.12586 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-164 |  | Non-Converged |  |  | 0.08626 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-165 |  | Non-Converged |  |  | 0.08626 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-177 |  | Non-Converged |  |  | 0.03566 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.11973 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.12075 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.13872 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.14065 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-210 |  | Non-Converged |  |  | 0.05278 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-213 |  | Non-Converged |  |  | 0.03554 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.47217 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-229 |  | Non-Converged |  |  | 0.11973 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.14067 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.13823 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.13976 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.11388 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-009 |  | Non-Converged |  |  | 0.12445 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.12215 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-022 |  | Non-Converged |  |  | 0.03865 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-027 |  | Non-Converged |  |  | 0.03749 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-038 |  | Non-Converged |  |  | 0.03781 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.11388 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-063 |  | Non-Converged |  |  | 0.03855 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-069 |  | Non-Converged |  |  | 0.09414 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.13649 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-088 |  | Non-Converged |  |  | 0.0658 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-092 |  | Non-Converged |  |  | 0.12518 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-100 |  | Non-Converged |  |  | 0.04496 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.13088 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-102 |  | Non-Converged |  |  | 0.04496 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.06316 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.11388 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.11388 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-150 |  | Non-Converged |  |  | 0.07502 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.12586 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.12586 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-164 |  | Non-Converged |  |  | 0.08626 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-165 |  | Non-Converged |  |  | 0.08626 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-177 |  | Non-Converged |  |  | 0.03566 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.11973 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.12075 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.13872 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.14065 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-210 |  | Non-Converged |  |  | 0.05278 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-213 |  | Non-Converged |  |  | 0.03554 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.47217 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-229 |  | Non-Converged |  |  | 0.11973 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.14067 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.13823 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.13976 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.11388 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.12215 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.11388 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.13649 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-100 |  | Non-Converged |  |  | 0.04496 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.13088 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-102 |  | Non-Converged |  |  | 0.04496 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.06316 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.11388 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.11388 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-150 |  | Non-Converged |  |  | 0.04087 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.12586 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.12586 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-164 |  | Non-Converged |  |  | 0.04405 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-165 |  | Non-Converged |  |  | 0.04405 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.11973 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.12075 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.13872 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.14065 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.47217 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-229 |  | Non-Converged |  |  | 0.03126 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.14067 |  | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.13823 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.13976 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.11388 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.12215 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.11388 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.13649 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-100 |  | Non-Converged |  |  | 0.04496 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.13088 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-102 |  | Non-Converged |  |  | 0.04496 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.06316 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.11388 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.11388 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-150 |  | Non-Converged |  |  | 0.04087 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.12586 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.12586 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-164 |  | Non-Converged |  |  | 0.04405 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-165 |  | Non-Converged |  |  | 0.04405 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.11973 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.12075 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.13872 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.14065 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.47217 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-229 |  | Non-Converged |  |  | 0.03126 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.14067 |  | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.07004 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.09559 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.05209 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.79429 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.79429 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.03056 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.03762 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.06607 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.1178 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.07615 |  | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | TDF Impact | Build new Tolk to Needmore 230 kV Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-222 |  | Non-Converged |  |  | 0.3054 |  | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Multi - Sheldon - Monolith 115 kV
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-223 |  | Non-Converged |  |  | 0.3054 |  | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Multi - Sheldon - Monolith 115 kV
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.13823 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.13976 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.11388 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.12215 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.11388 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.13649 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-100 |  | Non-Converged |  |  | 0.04496 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.13088 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-102 |  | Non-Converged |  |  | 0.04496 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.06316 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.11388 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.11388 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-150 |  | Non-Converged |  |  | 0.04087 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.12586 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.12586 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-164 |  | Non-Converged |  |  | 0.04405 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-165 |  | Non-Converged |  |  | 0.04405 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.11973 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.12075 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.13872 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.14065 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.47217 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-229 |  | Non-Converged |  |  | 0.03126 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.14067 |  | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.13823 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.13976 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.11388 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.12215 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.11388 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.13649 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-100 |  | Non-Converged |  |  | 0.04496 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.13088 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-102 |  | Non-Converged |  |  | 0.04496 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.06316 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.11388 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.11388 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-150 |  | Non-Converged |  |  | 0.04087 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.12586 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.12586 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-164 |  | Non-Converged |  |  | 0.04405 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-165 |  | Non-Converged |  |  | 0.04405 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.11973 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.12075 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.13872 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.14065 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.47217 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-229 |  | Non-Converged |  |  | 0.03126 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.14067 |  | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.13823 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.13976 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.12215 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.13649 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-100 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.13088 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-102 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.06316 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-150 |  | Non-Converged |  |  | 0.04087 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-164 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-165 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.11973 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.12075 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.13872 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.14065 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.47217 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-229 |  | Non-Converged |  |  | 0.03126 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.14067 |  | Potential P4 Event - POI 511456_12 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.13823 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.13976 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.12215 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.13649 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-100 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.13088 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-102 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.06316 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-150 |  | Non-Converged |  |  | 0.04087 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-164 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-165 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.11973 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.12075 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.13872 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.14065 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.47217 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-229 |  | Non-Converged |  |  | 0.03126 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.14067 |  | Potential P4 Event - POI 511456_15 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.13823 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.13976 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.12215 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.13649 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-100 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.13088 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-102 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.06316 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-150 |  | Non-Converged |  |  | 0.04087 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-164 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-165 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.11973 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.12075 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.13872 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.14065 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.47217 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-229 |  | Non-Converged |  |  | 0.03126 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.14067 |  | Potential P4 Event - POI 511456_18 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.13823 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.13976 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.12215 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.13649 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-100 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.13088 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-102 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.06316 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-150 |  | Non-Converged |  |  | 0.04087 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-164 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-165 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.11973 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.12075 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.13872 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.14065 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.47217 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-229 |  | Non-Converged |  |  | 0.03126 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.14067 |  | Potential P4 Event - POI 511456_19 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.13823 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.13976 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.12215 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.13649 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-100 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.13088 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-102 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.06316 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-150 |  | Non-Converged |  |  | 0.04087 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-164 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-165 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.11973 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.12075 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.13872 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.14065 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.47217 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-229 |  | Non-Converged |  |  | 0.03126 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.14067 |  | Potential P4 Event - POI 511456_3 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.13823 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.13976 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.12215 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.13649 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-100 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.13088 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-102 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.06316 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-150 |  | Non-Converged |  |  | 0.04087 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-164 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-165 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.11973 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.12075 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.13872 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.14065 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.47217 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-229 |  | Non-Converged |  |  | 0.03126 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.14067 |  | Potential P4 Event - POI 511456_8 | TDF Impact | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.13823 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.13976 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-009 |  | Non-Converged |  |  | 0.12445 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.12215 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-022 |  | Non-Converged |  |  | 0.03865 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-027 |  | Non-Converged |  |  | 0.03749 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-038 |  | Non-Converged |  |  | 0.03781 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-063 |  | Non-Converged |  |  | 0.03855 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-069 |  | Non-Converged |  |  | 0.09414 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.13649 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-088 |  | Non-Converged |  |  | 0.0658 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-092 |  | Non-Converged |  |  | 0.12518 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-100 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.13088 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-102 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.06316 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-150 |  | Non-Converged |  |  | 0.07502 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-164 |  | Non-Converged |  |  | 0.08626 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-165 |  | Non-Converged |  |  | 0.08626 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-177 |  | Non-Converged |  |  | 0.03566 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.11973 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.12075 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.13872 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.14065 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-210 |  | Non-Converged |  |  | 0.05278 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-213 |  | Non-Converged |  |  | 0.03554 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.47217 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-229 |  | Non-Converged |  |  | 0.11973 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.14067 |  | Potential P4 Event - POI 511468_11 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.13823 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.13976 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-009 |  | Non-Converged |  |  | 0.12445 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.12215 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-022 |  | Non-Converged |  |  | 0.03865 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-027 |  | Non-Converged |  |  | 0.03749 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-038 |  | Non-Converged |  |  | 0.0378 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-063 |  | Non-Converged |  |  | 0.03855 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-069 |  | Non-Converged |  |  | 0.09414 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.13649 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-088 |  | Non-Converged |  |  | 0.06579 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-092 |  | Non-Converged |  |  | 0.12518 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-100 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.13088 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-102 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.06316 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-150 |  | Non-Converged |  |  | 0.07502 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-164 |  | Non-Converged |  |  | 0.08626 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-165 |  | Non-Converged |  |  | 0.08626 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-177 |  | Non-Converged |  |  | 0.03566 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.11973 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.12075 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.13872 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.14065 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-210 |  | Non-Converged |  |  | 0.05278 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-213 |  | Non-Converged |  |  | 0.03554 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.47217 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-229 |  | Non-Converged |  |  | 0.11973 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.14067 |  | Potential P4 Event - POI 511468_16 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.13823 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.13976 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.12215 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.13649 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-100 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.13088 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-102 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.06316 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-150 |  | Non-Converged |  |  | 0.04087 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-164 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-165 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.11973 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.12075 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.13872 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.14065 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.47217 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-229 |  | Non-Converged |  |  | 0.03126 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.14067 |  | Potential P4 Event - POI 511468_20 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.13823 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.13976 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-009 |  | Non-Converged |  |  | 0.06003 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.12215 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-038 |  | Non-Converged |  |  | 0.03341 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-069 |  | Non-Converged |  |  | 0.04196 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.13649 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-092 |  | Non-Converged |  |  | 0.06127 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-100 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.13088 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-102 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.06316 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-150 |  | Non-Converged |  |  | 0.04087 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-164 |  | Non-Converged |  |  | 0.13511 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-165 |  | Non-Converged |  |  | 0.13511 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.11973 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.12075 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.13872 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.14065 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.47217 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-229 |  | Non-Converged |  |  | 0.03126 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.14067 |  | Potential P4 Event - POI 511468_23 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.13823 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.13976 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-009 |  | Non-Converged |  |  | 0.04873 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.12215 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-069 |  | Non-Converged |  |  | 0.03406 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.13649 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-092 |  | Non-Converged |  |  | 0.04973 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-100 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.13088 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-102 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.06316 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-150 |  | Non-Converged |  |  | 0.04087 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-164 |  | Non-Converged |  |  | 0.10968 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-165 |  | Non-Converged |  |  | 0.10968 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.11973 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.12075 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.13872 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.14065 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.47217 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-229 |  | Non-Converged |  |  | 0.03126 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.14067 |  | Potential P4 Event - POI 511468_25 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.13823 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.13976 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.12215 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.13649 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-100 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.13088 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-102 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.06316 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-150 |  | Non-Converged |  |  | 0.04087 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-164 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-165 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.11973 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.12075 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.13872 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.14065 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.47217 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-229 |  | Non-Converged |  |  | 0.03126 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.14067 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.13823 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.13976 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.12215 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.13649 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-100 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.13088 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-102 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.06316 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-150 |  | Non-Converged |  |  | 0.04087 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-164 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-165 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.11973 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.12075 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.13872 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.14065 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.47217 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-229 |  | Non-Converged |  |  | 0.03126 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.14067 |  | Potential P4 Event - POI 511468_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.13823 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.13976 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.12215 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.13649 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-100 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.13088 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-102 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.06316 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-150 |  | Non-Converged |  |  | 0.04087 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-164 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-165 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.11973 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.12075 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.13872 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.14065 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.47217 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-229 |  | Non-Converged |  |  | 0.03126 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.14067 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.13823 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.13976 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.12215 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.13649 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-100 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.13088 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-102 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.06316 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-150 |  | Non-Converged |  |  | 0.04087 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-164 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-165 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.11973 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.12075 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.13872 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.14065 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.47217 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-229 |  | Non-Converged |  |  | 0.03126 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.14067 |  | Potential P4 Event - POI 766291_1 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.13823 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.13976 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.12215 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.13649 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-100 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.13088 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-102 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.06316 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-150 |  | Non-Converged |  |  | 0.04087 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-164 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-165 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.11973 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.12075 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.13872 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.14065 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.47217 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-229 |  | Non-Converged |  |  | 0.03126 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.14067 |  | Potential P4 Event - POI 766291_2 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.13823 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.13976 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.12215 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.13649 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-100 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.13088 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-102 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.06316 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-150 |  | Non-Converged |  |  | 0.04087 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-164 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-165 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.11973 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.12075 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.13872 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.14065 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.47217 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-229 |  | Non-Converged |  |  | 0.03126 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.14067 |  | Potential P4 Event - POI 766291_3 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.13823 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.13976 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.12215 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.13649 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-100 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.13088 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-102 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.06316 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-150 |  | Non-Converged |  |  | 0.04087 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-164 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-165 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.11973 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.12075 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.13872 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.14065 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.47217 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-229 |  | Non-Converged |  |  | 0.03126 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.14067 |  | Potential P4 Event - POI 766291_5 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.13823 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.13976 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.12215 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.13649 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-100 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.13088 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-102 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.06316 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-150 |  | Non-Converged |  |  | 0.04087 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-164 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-165 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.11973 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.12075 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.13872 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.14065 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.47217 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-229 |  | Non-Converged |  |  | 0.03126 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.14067 |  | Potential P4 Event - POI 766291_7 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.13823 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.13976 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.12215 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.13649 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-100 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.13088 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-102 |  | Non-Converged |  |  | 0.04496 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.06316 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.11388 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-150 |  | Non-Converged |  |  | 0.04087 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.12586 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-164 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-165 |  | Non-Converged |  |  | 0.04405 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.11973 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.12075 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.13872 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.14065 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.47217 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-229 |  | Non-Converged |  |  | 0.03126 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.14067 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.15685 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.06369 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.16233 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.04086 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-188 |  | Non-Converged |  |  | 0.42326 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.07638 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.15086 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.15685 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.06369 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.16233 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.04086 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-188 |  | Non-Converged |  |  | 0.42326 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.07638 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.15086 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-015 |  | Non-Converged |  |  | 0.18136 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  | 0.07364 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-100 |  | Non-Converged |  |  | 0.03329 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-101 |  | Non-Converged |  |  | 0.1877 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-102 |  | Non-Converged |  |  | 0.03329 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-104 |  | Non-Converged |  |  | 0.04724 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-164 |  | Non-Converged |  |  | 0.03106 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-165 |  | Non-Converged |  |  | 0.03106 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-188 |  | Non-Converged |  |  | 0.84405 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  | 0.08832 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  | 0.17443 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.15685 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.06377 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.0307 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.16245 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.0307 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.04193 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-188 |  | Non-Converged |  |  | 0.42364 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.07646 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.15072 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.15685 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.06377 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.0307 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.16245 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.0307 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.04193 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-188 |  | Non-Converged |  |  | 0.42364 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.07646 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.15072 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-015 |  | Non-Converged |  |  | 0.18135 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  | 0.07373 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-100 |  | Non-Converged |  |  | 0.0355 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-101 |  | Non-Converged |  |  | 0.18783 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-102 |  | Non-Converged |  |  | 0.0355 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-104 |  | Non-Converged |  |  | 0.04848 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-188 |  | Non-Converged |  |  | 0.84437 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  | 0.08841 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  | 0.17426 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.0869 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.08783 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.07169 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.07702 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.07169 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.08583 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.08251 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.0405 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.07169 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.07169 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.0782 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.0782 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.07537 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-188 |  | Non-Converged |  |  | 0.42247 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.07603 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.08721 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.08836 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.2292 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.08843 |  | Potential P4 Event - POI 511468_27 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.0869 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.08783 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.07169 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.07702 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.07169 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.08583 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.08251 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.0405 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.07169 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.07169 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.0782 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.0782 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.07537 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-188 |  | Non-Converged |  |  | 0.42247 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.07603 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.08721 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.08836 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.2292 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.08843 |  | Potential P4 Event - POI 766291_0 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  | 0.10047 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  | 0.10155 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  | 0.08289 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-015 |  | Non-Converged |  |  | 0.08905 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  | 0.08289 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  | 0.09924 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-100 |  | Non-Converged |  |  | 0.03302 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-101 |  | Non-Converged |  |  | 0.09541 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-102 |  | Non-Converged |  |  | 0.03302 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-104 |  | Non-Converged |  |  | 0.04683 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  | 0.08289 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  | 0.08289 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  | 0.09042 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  | 0.09042 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-164 |  | Non-Converged |  |  | 0.0318 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-165 |  | Non-Converged |  |  | 0.0318 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  | 0.08715 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-188 |  | Non-Converged |  |  | 0.84338 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  | 0.0879 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  | 0.10084 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  | 0.10217 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  | 0.26501 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 00NR | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  | 0.10224 |  | Potential P4 Event - POI 766291_9 | TDF Impact | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | ASGI-2023-001 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-001 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-005 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-008 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-010 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-060 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-081 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-110 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-120 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-123 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-142 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-143 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-158 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-159 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-176 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-178 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-184 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-188 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-195 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-201 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-203 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-208 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-236 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 24SP | GEN-2023-237 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | ASGI-2023-001 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-001 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-005 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-008 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-010 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-060 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-081 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-110 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-120 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-123 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-142 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-143 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-158 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-159 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-176 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-178 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-184 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-188 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-195 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-201 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-203 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-208 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-236 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27SP | GEN-2023-237 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-008 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-010 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-086 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-110 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-120 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-123 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-176 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-184 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-188 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-208 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-209 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 | 05ALL | 0 | 27WP | GEN-2023-237 |  | Non-Converged |  |  |  |  | System Intact |  | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 24SP | ASGI-2023-001 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 24SP | GEN-2023-001 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 24SP | GEN-2023-005 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 24SP | GEN-2023-008 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 24SP | GEN-2023-010 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 24SP | GEN-2023-060 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 24SP | GEN-2023-081 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 24SP | GEN-2023-086 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 24SP | GEN-2023-110 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 24SP | GEN-2023-120 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 24SP | GEN-2023-123 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 24SP | GEN-2023-142 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 24SP | GEN-2023-143 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 24SP | GEN-2023-158 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 24SP | GEN-2023-159 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 24SP | GEN-2023-176 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 24SP | GEN-2023-178 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 24SP | GEN-2023-184 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 24SP | GEN-2023-188 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 24SP | GEN-2023-195 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 24SP | GEN-2023-201 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 24SP | GEN-2023-203 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 24SP | GEN-2023-208 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 24SP | GEN-2023-209 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 24SP | GEN-2023-228 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 24SP | GEN-2023-236 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 24SP | GEN-2023-237 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27SP | ASGI-2023-001 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27SP | GEN-2023-001 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27SP | GEN-2023-005 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27SP | GEN-2023-008 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27SP | GEN-2023-010 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27SP | GEN-2023-060 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27SP | GEN-2023-081 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27SP | GEN-2023-086 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27SP | GEN-2023-110 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27SP | GEN-2023-120 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27SP | GEN-2023-123 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27SP | GEN-2023-142 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27SP | GEN-2023-143 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27SP | GEN-2023-158 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27SP | GEN-2023-159 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27SP | GEN-2023-176 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27SP | GEN-2023-178 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27SP | GEN-2023-184 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27SP | GEN-2023-188 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27SP | GEN-2023-195 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27SP | GEN-2023-201 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27SP | GEN-2023-203 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27SP | GEN-2023-208 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27SP | GEN-2023-209 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27SP | GEN-2023-228 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27SP | GEN-2023-236 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27SP | GEN-2023-237 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27WP | ASGI-2023-001 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27WP | GEN-2023-001 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27WP | GEN-2023-005 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27WP | GEN-2023-008 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27WP | GEN-2023-010 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27WP | GEN-2023-060 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27WP | GEN-2023-081 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27WP | GEN-2023-086 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27WP | GEN-2023-110 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27WP | GEN-2023-120 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27WP | GEN-2023-123 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27WP | GEN-2023-142 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27WP | GEN-2023-143 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27WP | GEN-2023-158 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27WP | GEN-2023-159 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27WP | GEN-2023-176 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27WP | GEN-2023-178 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27WP | GEN-2023-184 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27WP | GEN-2023-188 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27WP | GEN-2023-195 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27WP | GEN-2023-201 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27WP | GEN-2023-203 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27WP | GEN-2023-208 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27WP | GEN-2023-209 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27WP | GEN-2023-228 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27WP | GEN-2023-236 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
Non-Converged | DISIS-2023-001 CF | 05ALL | 0 | 27WP | GEN-2023-237 |  | Non-Converged |  |  |  |  | System Intact |  | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line

## All Voltage
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME | Upgrade Name
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-011 | SAT-TAP3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.05953 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-116 | SAT-TAP3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.12834 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-117 | SAT-TAP3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.12834 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-133 | SAT-TAP3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.09943 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-153 | SAT-TAP3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.13341 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-199 | SAT-TAP3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.05844 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-216 | SAT-TAP3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.06283 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-217 | SAT-TAP3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.06283 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-218 | SAT-TAP3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.06283 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-011 | SAT-TAP3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.05953 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-116 | SAT-TAP3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.12834 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-117 | SAT-TAP3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.12834 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-133 | SAT-TAP3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.09943 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-153 | SAT-TAP3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.13341 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-199 | SAT-TAP3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.05844 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-216 | SAT-TAP3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.06283 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-217 | SAT-TAP3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.06283 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-218 | SAT-TAP3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.06283 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-011 | SATMKEC3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.05953 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-116 | SATMKEC3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.12834 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-117 | SATMKEC3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.12834 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-133 | SATMKEC3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.09943 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-153 | SATMKEC3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.13341 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-199 | SATMKEC3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.05844 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-216 | SATMKEC3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.06283 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-217 | SATMKEC3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.06283 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-218 | SATMKEC3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.06283 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-011 | SATMKEC3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.05953 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-116 | SATMKEC3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.12834 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-117 | SATMKEC3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.12834 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-133 | SATMKEC3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.09943 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-153 | SATMKEC3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.13341 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-199 | SATMKEC3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.05844 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-216 | SATMKEC3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.06283 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-217 | SATMKEC3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.06283 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-218 | SATMKEC3 | 0.959 | 0.897 | -0.062 |  | 0.9 | 1.05 | 0.06283 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-011 | HASKELL3 | 0.959 | 0.8972 | -0.0618 |  | 0.9 | 1.05 | 0.05953 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-116 | HASKELL3 | 0.959 | 0.8972 | -0.0618 |  | 0.9 | 1.05 | 0.12834 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-117 | HASKELL3 | 0.959 | 0.8972 | -0.0618 |  | 0.9 | 1.05 | 0.12834 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-133 | HASKELL3 | 0.959 | 0.8972 | -0.0618 |  | 0.9 | 1.05 | 0.09943 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-153 | HASKELL3 | 0.959 | 0.8972 | -0.0618 |  | 0.9 | 1.05 | 0.13341 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-199 | HASKELL3 | 0.959 | 0.8972 | -0.0618 |  | 0.9 | 1.05 | 0.05844 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-216 | HASKELL3 | 0.959 | 0.8972 | -0.0618 |  | 0.9 | 1.05 | 0.06283 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-217 | HASKELL3 | 0.959 | 0.8972 | -0.0618 |  | 0.9 | 1.05 | 0.06283 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-218 | HASKELL3 | 0.959 | 0.8972 | -0.0618 |  | 0.9 | 1.05 | 0.06283 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-011 | HASKELL3 | 0.959 | 0.8972 | -0.0618 |  | 0.9 | 1.05 | 0.05953 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-116 | HASKELL3 | 0.959 | 0.8972 | -0.0618 |  | 0.9 | 1.05 | 0.12834 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-117 | HASKELL3 | 0.959 | 0.8972 | -0.0618 |  | 0.9 | 1.05 | 0.12834 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-133 | HASKELL3 | 0.959 | 0.8972 | -0.0618 |  | 0.9 | 1.05 | 0.09943 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-153 | HASKELL3 | 0.959 | 0.8972 | -0.0618 |  | 0.9 | 1.05 | 0.13341 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-199 | HASKELL3 | 0.959 | 0.8972 | -0.0618 |  | 0.9 | 1.05 | 0.05844 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-216 | HASKELL3 | 0.959 | 0.8972 | -0.0618 |  | 0.9 | 1.05 | 0.06283 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-217 | HASKELL3 | 0.959 | 0.8972 | -0.0618 |  | 0.9 | 1.05 | 0.06283 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-218 | HASKELL3 | 0.959 | 0.8972 | -0.0618 |  | 0.9 | 1.05 | 0.06283 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-011 | GRANT 3 | 0.9668 | 0.8984 | -0.0684 |  | 0.9 | 1.05 | 0.05953 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-116 | GRANT 3 | 0.9668 | 0.8984 | -0.0684 |  | 0.9 | 1.05 | 0.12834 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-117 | GRANT 3 | 0.9668 | 0.8984 | -0.0684 |  | 0.9 | 1.05 | 0.12834 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-133 | GRANT 3 | 0.9668 | 0.8984 | -0.0684 |  | 0.9 | 1.05 | 0.09943 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-153 | GRANT 3 | 0.9668 | 0.8984 | -0.0684 |  | 0.9 | 1.05 | 0.13341 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-199 | GRANT 3 | 0.9668 | 0.8984 | -0.0684 |  | 0.9 | 1.05 | 0.05844 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-216 | GRANT 3 | 0.9668 | 0.8984 | -0.0684 |  | 0.9 | 1.05 | 0.06283 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-217 | GRANT 3 | 0.9668 | 0.8984 | -0.0684 |  | 0.9 | 1.05 | 0.06283 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-218 | GRANT 3 | 0.9668 | 0.8984 | -0.0684 |  | 0.9 | 1.05 | 0.06283 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-011 | GRANT 3 | 0.9668 | 0.8984 | -0.0684 |  | 0.9 | 1.05 | 0.05953 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-116 | GRANT 3 | 0.9668 | 0.8984 | -0.0684 |  | 0.9 | 1.05 | 0.12834 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-117 | GRANT 3 | 0.9668 | 0.8984 | -0.0684 |  | 0.9 | 1.05 | 0.12834 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-133 | GRANT 3 | 0.9668 | 0.8984 | -0.0684 |  | 0.9 | 1.05 | 0.09943 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-153 | GRANT 3 | 0.9668 | 0.8984 | -0.0684 |  | 0.9 | 1.05 | 0.13341 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-199 | GRANT 3 | 0.9668 | 0.8984 | -0.0684 |  | 0.9 | 1.05 | 0.05844 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-216 | GRANT 3 | 0.9668 | 0.8984 | -0.0684 |  | 0.9 | 1.05 | 0.06283 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-217 | GRANT 3 | 0.9668 | 0.8984 | -0.0684 |  | 0.9 | 1.05 | 0.06283 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-218 | GRANT 3 | 0.9668 | 0.8984 | -0.0684 |  | 0.9 | 1.05 | 0.06283 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-011 | GRANTTP3 | 0.9669 | 0.8986 | -0.0683 |  | 0.9 | 1.05 | 0.05953 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-116 | GRANTTP3 | 0.9669 | 0.8986 | -0.0683 |  | 0.9 | 1.05 | 0.12834 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-117 | GRANTTP3 | 0.9669 | 0.8986 | -0.0683 |  | 0.9 | 1.05 | 0.12834 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-133 | GRANTTP3 | 0.9669 | 0.8986 | -0.0683 |  | 0.9 | 1.05 | 0.09943 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-153 | GRANTTP3 | 0.9669 | 0.8986 | -0.0683 |  | 0.9 | 1.05 | 0.13341 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-199 | GRANTTP3 | 0.9669 | 0.8986 | -0.0683 |  | 0.9 | 1.05 | 0.05844 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-216 | GRANTTP3 | 0.9669 | 0.8986 | -0.0683 |  | 0.9 | 1.05 | 0.06283 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-217 | GRANTTP3 | 0.9669 | 0.8986 | -0.0683 |  | 0.9 | 1.05 | 0.06283 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-218 | GRANTTP3 | 0.9669 | 0.8986 | -0.0683 |  | 0.9 | 1.05 | 0.06283 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-011 | GRANTTP3 | 0.9669 | 0.8986 | -0.0683 |  | 0.9 | 1.05 | 0.05953 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-116 | GRANTTP3 | 0.9669 | 0.8986 | -0.0683 |  | 0.9 | 1.05 | 0.12834 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-117 | GRANTTP3 | 0.9669 | 0.8986 | -0.0683 |  | 0.9 | 1.05 | 0.12834 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-133 | GRANTTP3 | 0.9669 | 0.8986 | -0.0683 |  | 0.9 | 1.05 | 0.09943 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-153 | GRANTTP3 | 0.9669 | 0.8986 | -0.0683 |  | 0.9 | 1.05 | 0.13341 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-199 | GRANTTP3 | 0.9669 | 0.8986 | -0.0683 |  | 0.9 | 1.05 | 0.05844 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-216 | GRANTTP3 | 0.9669 | 0.8986 | -0.0683 |  | 0.9 | 1.05 | 0.06283 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-217 | GRANTTP3 | 0.9669 | 0.8986 | -0.0683 |  | 0.9 | 1.05 | 0.06283 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 27WP | GEN-2023-218 | GRANTTP3 | 0.9669 | 0.8986 | -0.0683 |  | 0.9 | 1.05 | 0.06283 | POI 531449_1 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
Voltage | DISIS-2023-001 | 02ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 | 02ALL | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 | 02ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-015 | 523823 CARPENTER 7 345 | 0.9914 | 0.8676 | 0.1238 | 0.9498 | 0.9 | 1.05 | 0.4521 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-015 | 764980 GEN-2020-008 345 | 0.9914 | 0.8676 | 0.1238 | 0.9498 | 0.9 | 1.05 | 0.4521 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-015 | 765490 GEN-2021-021 345 | 0.9914 | 0.8677 | 0.1237 | 0.9498 | 0.9 | 1.05 | 0.4521 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-015 | 531512 HARBNGR7 345 | 0.9914 | 0.8677 | 0.1237 | 0.9498 | 0.9 | 1.05 | 0.4521 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-015 | 531510 HARBNGR3 115 | 0.991 | 0.8866 | 0.1044 | 0.9554 | 0.9 | 1.05 | 0.4521 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-015 | 531405 WALKMYR3 115 | 0.991 | 0.8905 | 0.1005 | 0.9567 | 0.9 | 1.05 | 0.4521 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-015 | 531481 HUGOTON3 115 | 0.9896 | 0.8999 | 0.0897 | 0.9602 | 0.9 | 1.05 | 0.4521 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-107 | 523823 CARPENTER 7 345 | 0.9914 | 0.8676 | 0.1238 | 0.9498 | 0.9 | 1.05 | 0.3967 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-107 | 764980 GEN-2020-008 345 | 0.9914 | 0.8676 | 0.1238 | 0.9498 | 0.9 | 1.05 | 0.3967 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-107 | 765490 GEN-2021-021 345 | 0.9914 | 0.8677 | 0.1237 | 0.9498 | 0.9 | 1.05 | 0.3967 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-107 | 531512 HARBNGR7 345 | 0.9914 | 0.8677 | 0.1237 | 0.9498 | 0.9 | 1.05 | 0.3967 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-107 | 531510 HARBNGR3 115 | 0.991 | 0.8866 | 0.1044 | 0.9554 | 0.9 | 1.05 | 0.3967 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-107 | 531405 WALKMYR3 115 | 0.991 | 0.8905 | 0.1005 | 0.9567 | 0.9 | 1.05 | 0.3967 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-107 | 531481 HUGOTON3 115 | 0.9896 | 0.8999 | 0.0897 | 0.9602 | 0.9 | 1.05 | 0.3967 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-172 | 523823 CARPENTER 7 345 | 0.9914 | 0.8676 | 0.1238 | 0.9498 | 0.9 | 1.05 | 0.4765 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-172 | 764980 GEN-2020-008 345 | 0.9914 | 0.8676 | 0.1238 | 0.9498 | 0.9 | 1.05 | 0.4765 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-172 | 765490 GEN-2021-021 345 | 0.9914 | 0.8677 | 0.1237 | 0.9498 | 0.9 | 1.05 | 0.4765 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-172 | 531512 HARBNGR7 345 | 0.9914 | 0.8677 | 0.1237 | 0.9498 | 0.9 | 1.05 | 0.4765 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-172 | 531510 HARBNGR3 115 | 0.991 | 0.8866 | 0.1044 | 0.9554 | 0.9 | 1.05 | 0.4765 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-172 | 531405 WALKMYR3 115 | 0.991 | 0.8905 | 0.1005 | 0.9567 | 0.9 | 1.05 | 0.4765 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-172 | 531481 HUGOTON3 115 | 0.9896 | 0.8999 | 0.0897 | 0.9602 | 0.9 | 1.05 | 0.4765 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-173 | 523823 CARPENTER 7 345 | 0.9914 | 0.8676 | 0.1238 | 0.9498 | 0.9 | 1.05 | 0.4765 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-173 | 764980 GEN-2020-008 345 | 0.9914 | 0.8676 | 0.1238 | 0.9498 | 0.9 | 1.05 | 0.4765 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-173 | 765490 GEN-2021-021 345 | 0.9914 | 0.8677 | 0.1237 | 0.9498 | 0.9 | 1.05 | 0.4765 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-173 | 531512 HARBNGR7 345 | 0.9914 | 0.8677 | 0.1237 | 0.9498 | 0.9 | 1.05 | 0.4765 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-173 | 531510 HARBNGR3 115 | 0.991 | 0.8866 | 0.1044 | 0.9554 | 0.9 | 1.05 | 0.4765 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-173 | 531405 WALKMYR3 115 | 0.991 | 0.8905 | 0.1005 | 0.9567 | 0.9 | 1.05 | 0.4765 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-173 | 531481 HUGOTON3 115 | 0.9896 | 0.8999 | 0.0897 | 0.9602 | 0.9 | 1.05 | 0.4765 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-015 | 523823 CARPENTER 7 345 | 0.9906 | 0.9498 | 0.0408 | 0.9498 | 0.95 | 1.05 | 0.2909 | System Intact | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-107 | 523823 CARPENTER 7 345 | 0.9906 | 0.9498 | 0.0408 | 0.9498 | 0.95 | 1.05 | 0.2131 | System Intact | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-172 | 523823 CARPENTER 7 345 | 0.9906 | 0.9498 | 0.0408 | 0.9498 | 0.95 | 1.05 | 0.2474 | System Intact | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27WP | GEN-2023-173 | 523823 CARPENTER 7 345 | 0.9906 | 0.9498 | 0.0408 | 0.9498 | 0.95 | 1.05 | 0.2474 | System Intact | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27SP | GEN-2023-015 | 523823 CARPENTER 7 345 | 0.9771 | 0.8948 | 0.0823 | 0.9833 | 0.9 | 1.05 | 0.1984 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27SP | GEN-2023-015 | 765490 GEN-2021-021 345 | 0.9772 | 0.8948 | 0.0824 | 0.9833 | 0.9 | 1.05 | 0.1984 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27SP | GEN-2023-015 | 764980 GEN-2020-008 345 | 0.9772 | 0.8949 | 0.0823 | 0.9833 | 0.9 | 1.05 | 0.1984 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27SP | GEN-2023-015 | 531512 HARBNGR7 345 | 0.9771 | 0.8949 | 0.0822 | 0.9833 | 0.9 | 1.05 | 0.1984 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27SP | GEN-2023-172 | 523823 CARPENTER 7 345 | 0.9771 | 0.8948 | 0.0823 | 0.9833 | 0.9 | 1.05 | 0.2082 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27SP | GEN-2023-172 | 765490 GEN-2021-021 345 | 0.9772 | 0.8948 | 0.0824 | 0.9833 | 0.9 | 1.05 | 0.2082 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27SP | GEN-2023-172 | 764980 GEN-2020-008 345 | 0.9772 | 0.8949 | 0.0823 | 0.9833 | 0.9 | 1.05 | 0.2082 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27SP | GEN-2023-172 | 531512 HARBNGR7 345 | 0.9771 | 0.8949 | 0.0822 | 0.9833 | 0.9 | 1.05 | 0.2082 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27SP | GEN-2023-173 | 523823 CARPENTER 7 345 | 0.9771 | 0.8948 | 0.0823 | 0.9833 | 0.9 | 1.05 | 0.2082 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27SP | GEN-2023-173 | 765490 GEN-2021-021 345 | 0.9772 | 0.8948 | 0.0824 | 0.9833 | 0.9 | 1.05 | 0.2082 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27SP | GEN-2023-173 | 764980 GEN-2020-008 345 | 0.9772 | 0.8949 | 0.0823 | 0.9833 | 0.9 | 1.05 | 0.2082 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27SP | GEN-2023-173 | 531512 HARBNGR7 345 | 0.9771 | 0.8949 | 0.0822 | 0.9833 | 0.9 | 1.05 | 0.2082 | POI 531449_3 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
Voltage | DISIS-2023-001 | 03ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 | 03ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 | 03ALL | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 | 03ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 CF | 03ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 | 03NR | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 CF | 03NR | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | DOLTON-ER8 | 0.8832 | 0.8373 | -0.0459 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | DOLTON-ER8 | 0.8832 | 0.8373 | -0.0459 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | DOLTON-ER8 | 0.8832 | 0.8373 | -0.0459 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | DOLTON-ER8 | 0.8832 | 0.8373 | -0.0459 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | DOLTON-ER8 | 0.8832 | 0.8373 | -0.0459 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | DOLTON-ER8 | 0.8832 | 0.8373 | -0.0459 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | DOLTON-ER8 | 0.883 | 0.8375 | -0.0455 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | DOLTON-ER8 | 0.883 | 0.8375 | -0.0455 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | DOLTON-ER8 | 0.883 | 0.8375 | -0.0455 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | DOLTON-ER8 | 0.883 | 0.8375 | -0.0455 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | DOLTON-ER8 | 0.883 | 0.8375 | -0.0455 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | DOLTON-ER8 | 0.883 | 0.8375 | -0.0455 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | DOLTON-ER8 | 0.8848 | 0.842 | -0.0428 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | DOLTON-ER8 | 0.8848 | 0.842 | -0.0428 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | DOLTON-ER8 | 0.8848 | 0.842 | -0.0428 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | DOLTON-ER8 | 0.8848 | 0.842 | -0.0428 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | DOLTON-ER8 | 0.8848 | 0.842 | -0.0428 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | DOLTON-ER8 | 0.8848 | 0.842 | -0.0428 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | DOLTON-ER8 | 0.8856 | 0.8429 | -0.0427 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | DOLTON-ER8 | 0.8856 | 0.8429 | -0.0427 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | DOLTON-ER8 | 0.8856 | 0.8429 | -0.0427 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | DOLTON-ER8 | 0.8856 | 0.8429 | -0.0427 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | DOLTON-ER8 | 0.8856 | 0.8429 | -0.0427 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | DOLTON-ER8 | 0.8856 | 0.8429 | -0.0427 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | DOLTON-ER8 | 0.887 | 0.8432 | -0.0438 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | DOLTON-ER8 | 0.887 | 0.8432 | -0.0438 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | DOLTON-ER8 | 0.887 | 0.8432 | -0.0438 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | DOLTON-ER8 | 0.887 | 0.8432 | -0.0438 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | DOLTON-ER8 | 0.887 | 0.8432 | -0.0438 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | DOLTON-ER8 | 0.887 | 0.8432 | -0.0438 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | DOLTON-ER8 | 0.887 | 0.8438 | -0.0432 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | DOLTON-ER8 | 0.887 | 0.8438 | -0.0432 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | DOLTON-ER8 | 0.887 | 0.8438 | -0.0432 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | DOLTON-ER8 | 0.887 | 0.8438 | -0.0432 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | DOLTON-ER8 | 0.887 | 0.8438 | -0.0432 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | DOLTON-ER8 | 0.887 | 0.8438 | -0.0432 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | DOLTON-ER8 | 0.8863 | 0.8443 | -0.042 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | DOLTON-ER8 | 0.8863 | 0.8443 | -0.042 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | DOLTON-ER8 | 0.8863 | 0.8443 | -0.042 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | DOLTON-ER8 | 0.8863 | 0.8443 | -0.042 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | DOLTON-ER8 | 0.8863 | 0.8443 | -0.042 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | DOLTON-ER8 | 0.8863 | 0.8443 | -0.042 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | DOLTON-ER8 | 0.889 | 0.8471 | -0.0419 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | DOLTON-ER8 | 0.889 | 0.8471 | -0.0419 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | DOLTON-ER8 | 0.889 | 0.8471 | -0.0419 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | DOLTON-ER8 | 0.889 | 0.8471 | -0.0419 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | DOLTON-ER8 | 0.889 | 0.8471 | -0.0419 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | DOLTON-ER8 | 0.889 | 0.8471 | -0.0419 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | DOLTON-ER8 | 0.89 | 0.8489 | -0.0411 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | DOLTON-ER8 | 0.89 | 0.8489 | -0.0411 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | DOLTON-ER8 | 0.89 | 0.8489 | -0.0411 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | DOLTON-ER8 | 0.89 | 0.8489 | -0.0411 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | DOLTON-ER8 | 0.89 | 0.8489 | -0.0411 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | DOLTON-ER8 | 0.89 | 0.8489 | -0.0411 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | DOLTON-ER8 | 0.8903 | 0.8495 | -0.0408 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | DOLTON-ER8 | 0.8903 | 0.8495 | -0.0408 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | DOLTON-ER8 | 0.8903 | 0.8495 | -0.0408 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | DOLTON-ER8 | 0.8903 | 0.8495 | -0.0408 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | DOLTON-ER8 | 0.8903 | 0.8495 | -0.0408 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | DOLTON-ER8 | 0.8903 | 0.8495 | -0.0408 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | DOLTON-ER8 | 0.9111 | 0.8806 | -0.0305 |  | 0.9 | 1.05 | 0.10642 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | DOLTON-ER8 | 0.9111 | 0.8806 | -0.0305 |  | 0.9 | 1.05 | 0.24279 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | DOLTON-ER8 | 0.9111 | 0.8806 | -0.0305 |  | 0.9 | 1.05 | 0.09958 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | DOLTON-ER8 | 0.9111 | 0.8806 | -0.0305 |  | 0.9 | 1.05 | 0.03529 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | DOLTON-ER8 | 0.9111 | 0.8806 | -0.0305 |  | 0.9 | 1.05 | 0.0709 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | DOLTON-ER8 | 0.9111 | 0.8806 | -0.0305 |  | 0.9 | 1.05 | 0.14646 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | DOLTON-ER8 | 0.9111 | 0.8806 | -0.0305 |  | 0.9 | 1.05 | 0.10642 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | DOLTON-ER8 | 0.9111 | 0.8806 | -0.0305 |  | 0.9 | 1.05 | 0.24279 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | DOLTON-ER8 | 0.9111 | 0.8806 | -0.0305 |  | 0.9 | 1.05 | 0.09958 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | DOLTON-ER8 | 0.9111 | 0.8806 | -0.0305 |  | 0.9 | 1.05 | 0.03529 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | DOLTON-ER8 | 0.9111 | 0.8806 | -0.0305 |  | 0.9 | 1.05 | 0.0709 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | DOLTON-ER8 | 0.9111 | 0.8806 | -0.0305 |  | 0.9 | 1.05 | 0.14646 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | DOLTON-ER8 | 0.9111 | 0.8806 | -0.0305 |  | 0.9 | 1.05 | 0.10642 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | DOLTON-ER8 | 0.9111 | 0.8806 | -0.0305 |  | 0.9 | 1.05 | 0.24279 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | DOLTON-ER8 | 0.9111 | 0.8806 | -0.0305 |  | 0.9 | 1.05 | 0.09958 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | DOLTON-ER8 | 0.9111 | 0.8806 | -0.0305 |  | 0.9 | 1.05 | 0.03529 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | DOLTON-ER8 | 0.9111 | 0.8806 | -0.0305 |  | 0.9 | 1.05 | 0.0709 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | DOLTON-ER8 | 0.9111 | 0.8806 | -0.0305 |  | 0.9 | 1.05 | 0.14646 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | DOLTON-ER8 | 0.9134 | 0.8849 | -0.0285 |  | 0.9 | 1.05 | 0.10623 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | DOLTON-ER8 | 0.9134 | 0.8849 | -0.0285 |  | 0.9 | 1.05 | 0.24261 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | DOLTON-ER8 | 0.9134 | 0.8849 | -0.0285 |  | 0.9 | 1.05 | 0.1005 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | DOLTON-ER8 | 0.9134 | 0.8849 | -0.0285 |  | 0.9 | 1.05 | 0.03506 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | DOLTON-ER8 | 0.9134 | 0.8849 | -0.0285 |  | 0.9 | 1.05 | 0.07067 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | DOLTON-ER8 | 0.9134 | 0.8849 | -0.0285 |  | 0.9 | 1.05 | 0.14607 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | DOLTON-ER8 | 0.9134 | 0.8849 | -0.0285 |  | 0.9 | 1.05 | 0.10623 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | DOLTON-ER8 | 0.9134 | 0.8849 | -0.0285 |  | 0.9 | 1.05 | 0.24261 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | DOLTON-ER8 | 0.9134 | 0.8849 | -0.0285 |  | 0.9 | 1.05 | 0.1005 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | DOLTON-ER8 | 0.9134 | 0.8849 | -0.0285 |  | 0.9 | 1.05 | 0.03506 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | DOLTON-ER8 | 0.9134 | 0.8849 | -0.0285 |  | 0.9 | 1.05 | 0.07067 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | DOLTON-ER8 | 0.9134 | 0.8849 | -0.0285 |  | 0.9 | 1.05 | 0.14607 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | DOLTON-ER8 | 0.9134 | 0.8849 | -0.0285 |  | 0.9 | 1.05 | 0.10623 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | DOLTON-ER8 | 0.9134 | 0.8849 | -0.0285 |  | 0.9 | 1.05 | 0.24261 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | DOLTON-ER8 | 0.9134 | 0.8849 | -0.0285 |  | 0.9 | 1.05 | 0.1005 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | DOLTON-ER8 | 0.9134 | 0.8849 | -0.0285 |  | 0.9 | 1.05 | 0.03506 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | DOLTON-ER8 | 0.9134 | 0.8849 | -0.0285 |  | 0.9 | 1.05 | 0.07067 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | DOLTON-ER8 | 0.9134 | 0.8849 | -0.0285 |  | 0.9 | 1.05 | 0.14607 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | DOLTON-ER8 | 0.9166 | 0.8924 | -0.0242 |  | 0.9 | 1.05 | 0.10941 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | DOLTON-ER8 | 0.9166 | 0.8924 | -0.0242 |  | 0.9 | 1.05 | 0.05493 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | DOLTON-ER8 | 0.9204 | 0.8963 | -0.0241 |  | 0.9 | 1.05 | 0.03069 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | DOLTON-ER8 | 0.9204 | 0.8963 | -0.0241 |  | 0.9 | 1.05 | 0.10922 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | DOLTON-ER8 | 0.9204 | 0.8963 | -0.0241 |  | 0.9 | 1.05 | 0.05476 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | DOLTON-ER8 | 0.9191 | 0.8969 | -0.0222 |  | 0.9 | 1.05 | 0.05765 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | DOLTON-ER8 | 0.9191 | 0.8969 | -0.0222 |  | 0.9 | 1.05 | 0.04499 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | DOLTON-ER8 | 0.9191 | 0.8969 | -0.0222 |  | 0.9 | 1.05 | 0.05213 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | DOLTON-ER8 | 0.9191 | 0.8969 | -0.0222 |  | 0.9 | 1.05 | 0.07544 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | DOLTON-ER8 | 0.9191 | 0.8969 | -0.0222 |  | 0.9 | 1.05 | 0.07656 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | DOLTON-ER8 | 0.9191 | 0.8969 | -0.0222 |  | 0.9 | 1.05 | 0.05236 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | DOLTON-ER8 | 0.9197 | 0.8973 | -0.0224 |  | 0.9 | 1.05 | 0.03199 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | DOLTON-ER8 | 0.9197 | 0.8973 | -0.0224 |  | 0.9 | 1.05 | 0.04873 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | DOLTON-ER8 | 0.9197 | 0.8973 | -0.0224 |  | 0.9 | 1.05 | 0.09554 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | DOLTON-ER8 | 0.9197 | 0.8973 | -0.0224 |  | 0.9 | 1.05 | 0.08589 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | DOLTON-ER8 | 0.9197 | 0.8973 | -0.0224 |  | 0.9 | 1.05 | 0.04498 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | DOLTON-ER8 | 0.9197 | 0.8976 | -0.0221 |  | 0.9 | 1.05 | 0.03222 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | DOLTON-ER8 | 0.9197 | 0.8976 | -0.0221 |  | 0.9 | 1.05 | 0.04909 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | DOLTON-ER8 | 0.9197 | 0.8976 | -0.0221 |  | 0.9 | 1.05 | 0.09624 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | DOLTON-ER8 | 0.9197 | 0.8976 | -0.0221 |  | 0.9 | 1.05 | 0.08652 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | DOLTON-ER8 | 0.9197 | 0.8976 | -0.0221 |  | 0.9 | 1.05 | 0.04531 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | DOLTON-ER8 | 0.9205 | 0.8982 | -0.0223 |  | 0.9 | 1.05 | 0.03222 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | DOLTON-ER8 | 0.9205 | 0.8982 | -0.0223 |  | 0.9 | 1.05 | 0.04909 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | DOLTON-ER8 | 0.9205 | 0.8982 | -0.0223 |  | 0.9 | 1.05 | 0.09624 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | DOLTON-ER8 | 0.9205 | 0.8982 | -0.0223 |  | 0.9 | 1.05 | 0.08652 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | DOLTON-ER8 | 0.9205 | 0.8982 | -0.0223 |  | 0.9 | 1.05 | 0.04531 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | DOLTON-ER8 | 0.9214 | 0.8986 | -0.0228 |  | 0.9 | 1.05 | 0.05765 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | DOLTON-ER8 | 0.9214 | 0.8986 | -0.0228 |  | 0.9 | 1.05 | 0.04499 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | DOLTON-ER8 | 0.9214 | 0.8986 | -0.0228 |  | 0.9 | 1.05 | 0.05213 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | DOLTON-ER8 | 0.9214 | 0.8986 | -0.0228 |  | 0.9 | 1.05 | 0.07544 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | DOLTON-ER8 | 0.9214 | 0.8986 | -0.0228 |  | 0.9 | 1.05 | 0.07656 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | DOLTON-ER8 | 0.9214 | 0.8986 | -0.0228 |  | 0.9 | 1.05 | 0.05236 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | EMERY-ER8 | 0.922 | 0.8754 | -0.0466 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | EMERY-ER8 | 0.922 | 0.8754 | -0.0466 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | EMERY-ER8 | 0.922 | 0.8754 | -0.0466 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | EMERY-ER8 | 0.922 | 0.8754 | -0.0466 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | EMERY-ER8 | 0.922 | 0.8754 | -0.0466 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | EMERY-ER8 | 0.922 | 0.8754 | -0.0466 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | EMERY-ER8 | 0.9217 | 0.8756 | -0.0461 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | EMERY-ER8 | 0.9217 | 0.8756 | -0.0461 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | EMERY-ER8 | 0.9217 | 0.8756 | -0.0461 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | EMERY-ER8 | 0.9217 | 0.8756 | -0.0461 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | EMERY-ER8 | 0.9217 | 0.8756 | -0.0461 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | EMERY-ER8 | 0.9217 | 0.8756 | -0.0461 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | EMERY-ER8 | 0.9229 | 0.8774 | -0.0455 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | EMERY-ER8 | 0.9229 | 0.8774 | -0.0455 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | EMERY-ER8 | 0.9229 | 0.8774 | -0.0455 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | EMERY-ER8 | 0.9229 | 0.8774 | -0.0455 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | EMERY-ER8 | 0.9229 | 0.8774 | -0.0455 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | EMERY-ER8 | 0.9229 | 0.8774 | -0.0455 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | EMERY-ER8 | 0.9229 | 0.8803 | -0.0426 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | EMERY-ER8 | 0.9229 | 0.8803 | -0.0426 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | EMERY-ER8 | 0.9229 | 0.8803 | -0.0426 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | EMERY-ER8 | 0.9229 | 0.8803 | -0.0426 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | EMERY-ER8 | 0.9229 | 0.8803 | -0.0426 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | EMERY-ER8 | 0.9229 | 0.8803 | -0.0426 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | EMERY-ER8 | 0.925 | 0.8812 | -0.0438 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | EMERY-ER8 | 0.925 | 0.8812 | -0.0438 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | EMERY-ER8 | 0.925 | 0.8812 | -0.0438 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | EMERY-ER8 | 0.925 | 0.8812 | -0.0438 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | EMERY-ER8 | 0.925 | 0.8812 | -0.0438 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | EMERY-ER8 | 0.925 | 0.8812 | -0.0438 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | EMERY-ER8 | 0.9235 | 0.8815 | -0.042 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | EMERY-ER8 | 0.9235 | 0.8815 | -0.042 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | EMERY-ER8 | 0.9235 | 0.8815 | -0.042 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | EMERY-ER8 | 0.9235 | 0.8815 | -0.042 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | EMERY-ER8 | 0.9235 | 0.8815 | -0.042 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | EMERY-ER8 | 0.9235 | 0.8815 | -0.042 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | EMERY-ER8 | 0.9249 | 0.8818 | -0.0431 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | EMERY-ER8 | 0.9249 | 0.8818 | -0.0431 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | EMERY-ER8 | 0.9249 | 0.8818 | -0.0431 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | EMERY-ER8 | 0.9249 | 0.8818 | -0.0431 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | EMERY-ER8 | 0.9249 | 0.8818 | -0.0431 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | EMERY-ER8 | 0.9249 | 0.8818 | -0.0431 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | EMERY-ER8 | 0.926 | 0.8848 | -0.0412 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | EMERY-ER8 | 0.926 | 0.8848 | -0.0412 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | EMERY-ER8 | 0.926 | 0.8848 | -0.0412 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | EMERY-ER8 | 0.926 | 0.8848 | -0.0412 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | EMERY-ER8 | 0.926 | 0.8848 | -0.0412 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | EMERY-ER8 | 0.926 | 0.8848 | -0.0412 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | EMERY-ER8 | 0.9274 | 0.8868 | -0.0406 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | EMERY-ER8 | 0.9274 | 0.8868 | -0.0406 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | EMERY-ER8 | 0.9274 | 0.8868 | -0.0406 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | EMERY-ER8 | 0.9274 | 0.8868 | -0.0406 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | EMERY-ER8 | 0.9274 | 0.8868 | -0.0406 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | EMERY-ER8 | 0.9274 | 0.8868 | -0.0406 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | EMERY-ER8 | 0.9278 | 0.8873 | -0.0405 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | EMERY-ER8 | 0.9278 | 0.8873 | -0.0405 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | EMERY-ER8 | 0.9278 | 0.8873 | -0.0405 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | EMERY-ER8 | 0.9278 | 0.8873 | -0.0405 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | EMERY-ER8 | 0.9278 | 0.8873 | -0.0405 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | EMERY-ER8 | 0.9278 | 0.8873 | -0.0405 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | FARMER-ER8 | 0.9244 | 0.8779 | -0.0465 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | FARMER-ER8 | 0.9244 | 0.8779 | -0.0465 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | FARMER-ER8 | 0.9244 | 0.8779 | -0.0465 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | FARMER-ER8 | 0.9244 | 0.8779 | -0.0465 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | FARMER-ER8 | 0.9244 | 0.8779 | -0.0465 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | FARMER-ER8 | 0.9244 | 0.8779 | -0.0465 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | FARMER-ER8 | 0.924 | 0.8781 | -0.0459 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | FARMER-ER8 | 0.924 | 0.8781 | -0.0459 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | FARMER-ER8 | 0.924 | 0.8781 | -0.0459 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | FARMER-ER8 | 0.924 | 0.8781 | -0.0459 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | FARMER-ER8 | 0.924 | 0.8781 | -0.0459 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | FARMER-ER8 | 0.924 | 0.8781 | -0.0459 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | FARMER-ER8 | 0.9253 | 0.8799 | -0.0454 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | FARMER-ER8 | 0.9253 | 0.8799 | -0.0454 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | FARMER-ER8 | 0.9253 | 0.8799 | -0.0454 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | FARMER-ER8 | 0.9253 | 0.8799 | -0.0454 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | FARMER-ER8 | 0.9253 | 0.8799 | -0.0454 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | FARMER-ER8 | 0.9253 | 0.8799 | -0.0454 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | FARMER-ER8 | 0.9253 | 0.8829 | -0.0424 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | FARMER-ER8 | 0.9253 | 0.8829 | -0.0424 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | FARMER-ER8 | 0.9253 | 0.8829 | -0.0424 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | FARMER-ER8 | 0.9253 | 0.8829 | -0.0424 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | FARMER-ER8 | 0.9253 | 0.8829 | -0.0424 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | FARMER-ER8 | 0.9253 | 0.8829 | -0.0424 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | FARMER-ER8 | 0.9273 | 0.8837 | -0.0436 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | FARMER-ER8 | 0.9273 | 0.8837 | -0.0436 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | FARMER-ER8 | 0.9273 | 0.8837 | -0.0436 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | FARMER-ER8 | 0.9273 | 0.8837 | -0.0436 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | FARMER-ER8 | 0.9273 | 0.8837 | -0.0436 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | FARMER-ER8 | 0.9273 | 0.8837 | -0.0436 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | FARMER-ER8 | 0.9259 | 0.884 | -0.0419 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | FARMER-ER8 | 0.9259 | 0.884 | -0.0419 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | FARMER-ER8 | 0.9259 | 0.884 | -0.0419 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | FARMER-ER8 | 0.9259 | 0.884 | -0.0419 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | FARMER-ER8 | 0.9259 | 0.884 | -0.0419 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | FARMER-ER8 | 0.9259 | 0.884 | -0.0419 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | FARMER-ER8 | 0.9273 | 0.8843 | -0.043 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | FARMER-ER8 | 0.9273 | 0.8843 | -0.043 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | FARMER-ER8 | 0.9273 | 0.8843 | -0.043 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | FARMER-ER8 | 0.9273 | 0.8843 | -0.043 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | FARMER-ER8 | 0.9273 | 0.8843 | -0.043 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | FARMER-ER8 | 0.9273 | 0.8843 | -0.043 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | FARMER-ER8 | 0.9283 | 0.8873 | -0.041 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | FARMER-ER8 | 0.9283 | 0.8873 | -0.041 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | FARMER-ER8 | 0.9283 | 0.8873 | -0.041 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | FARMER-ER8 | 0.9283 | 0.8873 | -0.041 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | FARMER-ER8 | 0.9283 | 0.8873 | -0.041 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | FARMER-ER8 | 0.9283 | 0.8873 | -0.041 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | FARMER-ER8 | 0.9298 | 0.8894 | -0.0404 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | FARMER-ER8 | 0.9298 | 0.8894 | -0.0404 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | FARMER-ER8 | 0.9298 | 0.8894 | -0.0404 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | FARMER-ER8 | 0.9298 | 0.8894 | -0.0404 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | FARMER-ER8 | 0.9298 | 0.8894 | -0.0404 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | FARMER-ER8 | 0.9298 | 0.8894 | -0.0404 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | FARMER-ER8 | 0.9302 | 0.8899 | -0.0403 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | FARMER-ER8 | 0.9302 | 0.8899 | -0.0403 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | FARMER-ER8 | 0.9302 | 0.8899 | -0.0403 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | FARMER-ER8 | 0.9302 | 0.8899 | -0.0403 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | FARMER-ER8 | 0.9302 | 0.8899 | -0.0403 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | FARMER-ER8 | 0.9302 | 0.8899 | -0.0403 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HURLEY-ER8 | 0.9203 | 0.8843 | -0.036 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HURLEY-ER8 | 0.9203 | 0.8843 | -0.036 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HURLEY-ER8 | 0.9203 | 0.8843 | -0.036 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HURLEY-ER8 | 0.9203 | 0.8843 | -0.036 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HURLEY-ER8 | 0.9203 | 0.8843 | -0.036 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HURLEY-ER8 | 0.9203 | 0.8843 | -0.036 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HURLEY-ER8 | 0.9201 | 0.8844 | -0.0357 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HURLEY-ER8 | 0.9201 | 0.8844 | -0.0357 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HURLEY-ER8 | 0.9201 | 0.8844 | -0.0357 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HURLEY-ER8 | 0.9201 | 0.8844 | -0.0357 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HURLEY-ER8 | 0.9201 | 0.8844 | -0.0357 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HURLEY-ER8 | 0.9201 | 0.8844 | -0.0357 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HURLEY-ER8 | 0.921 | 0.8865 | -0.0345 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HURLEY-ER8 | 0.921 | 0.8865 | -0.0345 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HURLEY-ER8 | 0.921 | 0.8865 | -0.0345 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HURLEY-ER8 | 0.921 | 0.8865 | -0.0345 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HURLEY-ER8 | 0.921 | 0.8865 | -0.0345 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HURLEY-ER8 | 0.921 | 0.8865 | -0.0345 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | CHMBRLAN-ER8 | 0.9325 | 0.8814 | -0.0511 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | CHMBRLAN-ER8 | 0.9325 | 0.8814 | -0.0511 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | CHMBRLAN-ER8 | 0.9325 | 0.8814 | -0.0511 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | CHMBRLAN-ER8 | 0.9325 | 0.8814 | -0.0511 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | CHMBRLAN-ER8 | 0.9325 | 0.8814 | -0.0511 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | CHMBRLAN-ER8 | 0.9325 | 0.8814 | -0.0511 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | CHMBRLAN-ER8 | 0.9322 | 0.8816 | -0.0506 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | CHMBRLAN-ER8 | 0.9322 | 0.8816 | -0.0506 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | CHMBRLAN-ER8 | 0.9322 | 0.8816 | -0.0506 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | CHMBRLAN-ER8 | 0.9322 | 0.8816 | -0.0506 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | CHMBRLAN-ER8 | 0.9322 | 0.8816 | -0.0506 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | CHMBRLAN-ER8 | 0.9322 | 0.8816 | -0.0506 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | CHMBRLAN-ER8 | 0.9341 | 0.8871 | -0.047 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | CHMBRLAN-ER8 | 0.9341 | 0.8871 | -0.047 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | CHMBRLAN-ER8 | 0.9341 | 0.8871 | -0.047 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | CHMBRLAN-ER8 | 0.9341 | 0.8871 | -0.047 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | CHMBRLAN-ER8 | 0.9341 | 0.8871 | -0.047 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | CHMBRLAN-ER8 | 0.9341 | 0.8871 | -0.047 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | CHMBRLAN-ER8 | 0.9341 | 0.8877 | -0.0464 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | CHMBRLAN-ER8 | 0.9341 | 0.8877 | -0.0464 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | CHMBRLAN-ER8 | 0.9341 | 0.8877 | -0.0464 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | CHMBRLAN-ER8 | 0.9341 | 0.8877 | -0.0464 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | CHMBRLAN-ER8 | 0.9341 | 0.8877 | -0.0464 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | CHMBRLAN-ER8 | 0.9341 | 0.8877 | -0.0464 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | CHMBRLAN-ER8 | 0.9352 | 0.8899 | -0.0453 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | CHMBRLAN-ER8 | 0.9352 | 0.8899 | -0.0453 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | CHMBRLAN-ER8 | 0.9352 | 0.8899 | -0.0453 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | CHMBRLAN-ER8 | 0.9352 | 0.8899 | -0.0453 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | CHMBRLAN-ER8 | 0.9352 | 0.8899 | -0.0453 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | CHMBRLAN-ER8 | 0.9352 | 0.8899 | -0.0453 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | CHMBRLAN-ER8 | 0.9368 | 0.8919 | -0.0449 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | CHMBRLAN-ER8 | 0.9368 | 0.8919 | -0.0449 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | CHMBRLAN-ER8 | 0.9368 | 0.8919 | -0.0449 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | CHMBRLAN-ER8 | 0.9368 | 0.8919 | -0.0449 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | CHMBRLAN-ER8 | 0.9368 | 0.8919 | -0.0449 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | CHMBRLAN-ER8 | 0.9368 | 0.8919 | -0.0449 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | CHMBRLAN-ER8 | 0.9375 | 0.8932 | -0.0443 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | CHMBRLAN-ER8 | 0.9375 | 0.8932 | -0.0443 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | CHMBRLAN-ER8 | 0.9375 | 0.8932 | -0.0443 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | CHMBRLAN-ER8 | 0.9375 | 0.8932 | -0.0443 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | CHMBRLAN-ER8 | 0.9375 | 0.8932 | -0.0443 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | CHMBRLAN-ER8 | 0.9375 | 0.8932 | -0.0443 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | CHMBRLAN-ER8 | 0.9372 | 0.8932 | -0.044 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | CHMBRLAN-ER8 | 0.9372 | 0.8932 | -0.044 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | CHMBRLAN-ER8 | 0.9372 | 0.8932 | -0.044 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | CHMBRLAN-ER8 | 0.9372 | 0.8932 | -0.044 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | CHMBRLAN-ER8 | 0.9372 | 0.8932 | -0.044 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | CHMBRLAN-ER8 | 0.9372 | 0.8932 | -0.044 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | CHMBRLAN-ER8 | 0.939 | 0.8959 | -0.0431 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | CHMBRLAN-ER8 | 0.939 | 0.8959 | -0.0431 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | CHMBRLAN-ER8 | 0.939 | 0.8959 | -0.0431 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | CHMBRLAN-ER8 | 0.939 | 0.8959 | -0.0431 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | CHMBRLAN-ER8 | 0.939 | 0.8959 | -0.0431 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | CHMBRLAN-ER8 | 0.939 | 0.8959 | -0.0431 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | CHMBRLAN-ER8 | 0.9393 | 0.8964 | -0.0429 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | CHMBRLAN-ER8 | 0.9393 | 0.8964 | -0.0429 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | CHMBRLAN-ER8 | 0.9393 | 0.8964 | -0.0429 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | CHMBRLAN-ER8 | 0.9393 | 0.8964 | -0.0429 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | CHMBRLAN-ER8 | 0.9393 | 0.8964 | -0.0429 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | CHMBRLAN-ER8 | 0.9393 | 0.8964 | -0.0429 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | COLTON-ER8 | 0.9072 | 0.8635 | -0.0437 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | COLTON-ER8 | 0.9072 | 0.8635 | -0.0437 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | COLTON-ER8 | 0.9072 | 0.8635 | -0.0437 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | COLTON-ER8 | 0.9072 | 0.8635 | -0.0437 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | COLTON-ER8 | 0.9072 | 0.8635 | -0.0437 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | COLTON-ER8 | 0.9072 | 0.8635 | -0.0437 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | COLTON-ER8 | 0.907 | 0.8637 | -0.0433 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | COLTON-ER8 | 0.907 | 0.8637 | -0.0433 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | COLTON-ER8 | 0.907 | 0.8637 | -0.0433 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | COLTON-ER8 | 0.907 | 0.8637 | -0.0433 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | COLTON-ER8 | 0.907 | 0.8637 | -0.0433 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | COLTON-ER8 | 0.907 | 0.8637 | -0.0433 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | COLTON-ER8 | 0.9086 | 0.8668 | -0.0418 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | COLTON-ER8 | 0.9086 | 0.8668 | -0.0418 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | COLTON-ER8 | 0.9086 | 0.8668 | -0.0418 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | COLTON-ER8 | 0.9086 | 0.8668 | -0.0418 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | COLTON-ER8 | 0.9086 | 0.8668 | -0.0418 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | COLTON-ER8 | 0.9086 | 0.8668 | -0.0418 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | COLTON-ER8 | 0.9085 | 0.8673 | -0.0412 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | COLTON-ER8 | 0.9085 | 0.8673 | -0.0412 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | COLTON-ER8 | 0.9085 | 0.8673 | -0.0412 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | COLTON-ER8 | 0.9085 | 0.8673 | -0.0412 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | COLTON-ER8 | 0.9085 | 0.8673 | -0.0412 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | COLTON-ER8 | 0.9085 | 0.8673 | -0.0412 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | COLTON-ER8 | 0.9088 | 0.8679 | -0.0409 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | COLTON-ER8 | 0.9088 | 0.8679 | -0.0409 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | COLTON-ER8 | 0.9088 | 0.8679 | -0.0409 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | COLTON-ER8 | 0.9088 | 0.8679 | -0.0409 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | COLTON-ER8 | 0.9088 | 0.8679 | -0.0409 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | COLTON-ER8 | 0.9088 | 0.8679 | -0.0409 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | COLTON-ER8 | 0.9095 | 0.8688 | -0.0407 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | COLTON-ER8 | 0.9095 | 0.8688 | -0.0407 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | COLTON-ER8 | 0.9095 | 0.8688 | -0.0407 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | COLTON-ER8 | 0.9095 | 0.8688 | -0.0407 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | COLTON-ER8 | 0.9095 | 0.8688 | -0.0407 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | COLTON-ER8 | 0.9095 | 0.8688 | -0.0407 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | COLTON-ER8 | 0.9102 | 0.8701 | -0.0401 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | COLTON-ER8 | 0.9102 | 0.8701 | -0.0401 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | COLTON-ER8 | 0.9102 | 0.8701 | -0.0401 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | COLTON-ER8 | 0.9102 | 0.8701 | -0.0401 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | COLTON-ER8 | 0.9102 | 0.8701 | -0.0401 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | COLTON-ER8 | 0.9102 | 0.8701 | -0.0401 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | COLTON-ER8 | 0.9105 | 0.8704 | -0.0401 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | COLTON-ER8 | 0.9105 | 0.8704 | -0.0401 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | COLTON-ER8 | 0.9105 | 0.8704 | -0.0401 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | COLTON-ER8 | 0.9105 | 0.8704 | -0.0401 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | COLTON-ER8 | 0.9105 | 0.8704 | -0.0401 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | COLTON-ER8 | 0.9105 | 0.8704 | -0.0401 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | COLTON-ER8 | 0.9114 | 0.8722 | -0.0392 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | COLTON-ER8 | 0.9114 | 0.8722 | -0.0392 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | COLTON-ER8 | 0.9114 | 0.8722 | -0.0392 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | COLTON-ER8 | 0.9114 | 0.8722 | -0.0392 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | COLTON-ER8 | 0.9114 | 0.8722 | -0.0392 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | COLTON-ER8 | 0.9114 | 0.8722 | -0.0392 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | COLTON-ER8 | 0.9117 | 0.8727 | -0.039 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | COLTON-ER8 | 0.9117 | 0.8727 | -0.039 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | COLTON-ER8 | 0.9117 | 0.8727 | -0.039 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | COLTON-ER8 | 0.9117 | 0.8727 | -0.039 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | COLTON-ER8 | 0.9117 | 0.8727 | -0.039 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | COLTON-ER8 | 0.9117 | 0.8727 | -0.039 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | DAYTON__-ER7 | 0.928 | 0.892 | -0.036 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | DAYTON__-ER7 | 0.928 | 0.892 | -0.036 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | DAYTON__-ER7 | 0.928 | 0.892 | -0.036 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | DAYTON__-ER7 | 0.928 | 0.892 | -0.036 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | DAYTON__-ER7 | 0.928 | 0.892 | -0.036 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | DAYTON__-ER7 | 0.928 | 0.892 | -0.036 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | DAYTON__-ER7 | 0.9278 | 0.8922 | -0.0356 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | DAYTON__-ER7 | 0.9278 | 0.8922 | -0.0356 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | DAYTON__-ER7 | 0.9278 | 0.8922 | -0.0356 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | DAYTON__-ER7 | 0.9278 | 0.8922 | -0.0356 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | DAYTON__-ER7 | 0.9278 | 0.8922 | -0.0356 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | DAYTON__-ER7 | 0.9278 | 0.8922 | -0.0356 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | DAYTON__-ER7 | 0.9287 | 0.8943 | -0.0344 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | DAYTON__-ER7 | 0.9287 | 0.8943 | -0.0344 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | DAYTON__-ER7 | 0.9287 | 0.8943 | -0.0344 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | DAYTON__-ER7 | 0.9287 | 0.8943 | -0.0344 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | DAYTON__-ER7 | 0.9287 | 0.8943 | -0.0344 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | DAYTON__-ER7 | 0.9287 | 0.8943 | -0.0344 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | DAYTON__-ER7 | 0.9294 | 0.8952 | -0.0342 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | DAYTON__-ER7 | 0.9294 | 0.8952 | -0.0342 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | DAYTON__-ER7 | 0.9294 | 0.8952 | -0.0342 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | DAYTON__-ER7 | 0.9294 | 0.8952 | -0.0342 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | DAYTON__-ER7 | 0.9294 | 0.8952 | -0.0342 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | DAYTON__-ER7 | 0.9294 | 0.8952 | -0.0342 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | DAYTON__-ER7 | 0.93 | 0.8962 | -0.0338 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | DAYTON__-ER7 | 0.93 | 0.8962 | -0.0338 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | DAYTON__-ER7 | 0.93 | 0.8962 | -0.0338 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | DAYTON__-ER7 | 0.93 | 0.8962 | -0.0338 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | DAYTON__-ER7 | 0.93 | 0.8962 | -0.0338 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | DAYTON__-ER7 | 0.93 | 0.8962 | -0.0338 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HURLEY-ER8 | 0.9217 | 0.8875 | -0.0342 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HURLEY-ER8 | 0.9217 | 0.8875 | -0.0342 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HURLEY-ER8 | 0.9217 | 0.8875 | -0.0342 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HURLEY-ER8 | 0.9217 | 0.8875 | -0.0342 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HURLEY-ER8 | 0.9217 | 0.8875 | -0.0342 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HURLEY-ER8 | 0.9217 | 0.8875 | -0.0342 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HURLEY-ER8 | 0.9224 | 0.8885 | -0.0339 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HURLEY-ER8 | 0.9224 | 0.8885 | -0.0339 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HURLEY-ER8 | 0.9224 | 0.8885 | -0.0339 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HURLEY-ER8 | 0.9224 | 0.8885 | -0.0339 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HURLEY-ER8 | 0.9224 | 0.8885 | -0.0339 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HURLEY-ER8 | 0.9224 | 0.8885 | -0.0339 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | HURLEY-ER8 | 0.9269 | 0.8933 | -0.0336 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | HURLEY-ER8 | 0.9269 | 0.8933 | -0.0336 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | HURLEY-ER8 | 0.9269 | 0.8933 | -0.0336 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | HURLEY-ER8 | 0.9269 | 0.8933 | -0.0336 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | HURLEY-ER8 | 0.9269 | 0.8933 | -0.0336 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | HURLEY-ER8 | 0.9269 | 0.8933 | -0.0336 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | HURLEY-ER8 | 0.9269 | 0.8936 | -0.0333 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | HURLEY-ER8 | 0.9269 | 0.8936 | -0.0333 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | HURLEY-ER8 | 0.9269 | 0.8936 | -0.0333 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | HURLEY-ER8 | 0.9269 | 0.8936 | -0.0333 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | HURLEY-ER8 | 0.9269 | 0.8936 | -0.0333 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | HURLEY-ER8 | 0.9269 | 0.8936 | -0.0333 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | HURLEY-ER8 | 0.9278 | 0.8952 | -0.0326 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | HURLEY-ER8 | 0.9278 | 0.8952 | -0.0326 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | HURLEY-ER8 | 0.9278 | 0.8952 | -0.0326 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | HURLEY-ER8 | 0.9278 | 0.8952 | -0.0326 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | HURLEY-ER8 | 0.9278 | 0.8952 | -0.0326 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | HURLEY-ER8 | 0.9278 | 0.8952 | -0.0326 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | HURLEY-ER8 | 0.9287 | 0.8968 | -0.0319 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | HURLEY-ER8 | 0.9287 | 0.8968 | -0.0319 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | HURLEY-ER8 | 0.9287 | 0.8968 | -0.0319 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | HURLEY-ER8 | 0.9287 | 0.8968 | -0.0319 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | HURLEY-ER8 | 0.9287 | 0.8968 | -0.0319 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | HURLEY-ER8 | 0.9287 | 0.8968 | -0.0319 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | HURLEY-ER8 | 0.929 | 0.8972 | -0.0318 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | HURLEY-ER8 | 0.929 | 0.8972 | -0.0318 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | HURLEY-ER8 | 0.929 | 0.8972 | -0.0318 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | HURLEY-ER8 | 0.929 | 0.8972 | -0.0318 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | HURLEY-ER8 | 0.929 | 0.8972 | -0.0318 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | HURLEY-ER8 | 0.929 | 0.8972 | -0.0318 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | INDMARIN-ER8 | 0.8715 | 0.8249 | -0.0466 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | INDMARIN-ER8 | 0.8715 | 0.8249 | -0.0466 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | INDMARIN-ER8 | 0.8715 | 0.8249 | -0.0466 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | INDMARIN-ER8 | 0.8715 | 0.8249 | -0.0466 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | INDMARIN-ER8 | 0.8715 | 0.8249 | -0.0466 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | INDMARIN-ER8 | 0.8715 | 0.8249 | -0.0466 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | GRNDMEAD-ER8 | 0.9096 | 0.866 | -0.0436 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | GRNDMEAD-ER8 | 0.9096 | 0.866 | -0.0436 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | GRNDMEAD-ER8 | 0.9096 | 0.866 | -0.0436 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | GRNDMEAD-ER8 | 0.9096 | 0.866 | -0.0436 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | GRNDMEAD-ER8 | 0.9096 | 0.866 | -0.0436 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | GRNDMEAD-ER8 | 0.9096 | 0.866 | -0.0436 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | GRNDMEAD-ER8 | 0.9094 | 0.8662 | -0.0432 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | GRNDMEAD-ER8 | 0.9094 | 0.8662 | -0.0432 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | GRNDMEAD-ER8 | 0.9094 | 0.8662 | -0.0432 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | GRNDMEAD-ER8 | 0.9094 | 0.8662 | -0.0432 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | GRNDMEAD-ER8 | 0.9094 | 0.8662 | -0.0432 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | GRNDMEAD-ER8 | 0.9094 | 0.8662 | -0.0432 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | GRNDMEAD-ER8 | 0.9112 | 0.8695 | -0.0417 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | GRNDMEAD-ER8 | 0.9112 | 0.8695 | -0.0417 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | GRNDMEAD-ER8 | 0.9112 | 0.8695 | -0.0417 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | GRNDMEAD-ER8 | 0.9112 | 0.8695 | -0.0417 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | GRNDMEAD-ER8 | 0.9112 | 0.8695 | -0.0417 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | GRNDMEAD-ER8 | 0.9112 | 0.8695 | -0.0417 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | GRNDMEAD-ER8 | 0.9112 | 0.87 | -0.0412 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | GRNDMEAD-ER8 | 0.9112 | 0.87 | -0.0412 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | GRNDMEAD-ER8 | 0.9112 | 0.87 | -0.0412 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | GRNDMEAD-ER8 | 0.9112 | 0.87 | -0.0412 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | GRNDMEAD-ER8 | 0.9112 | 0.87 | -0.0412 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | GRNDMEAD-ER8 | 0.9112 | 0.87 | -0.0412 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | GRNDMEAD-ER8 | 0.9111 | 0.8704 | -0.0407 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | GRNDMEAD-ER8 | 0.9111 | 0.8704 | -0.0407 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | GRNDMEAD-ER8 | 0.9111 | 0.8704 | -0.0407 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | GRNDMEAD-ER8 | 0.9111 | 0.8704 | -0.0407 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | GRNDMEAD-ER8 | 0.9111 | 0.8704 | -0.0407 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | GRNDMEAD-ER8 | 0.9111 | 0.8704 | -0.0407 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | GRNDMEAD-ER8 | 0.9119 | 0.8713 | -0.0406 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | GRNDMEAD-ER8 | 0.9119 | 0.8713 | -0.0406 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | GRNDMEAD-ER8 | 0.9119 | 0.8713 | -0.0406 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | GRNDMEAD-ER8 | 0.9119 | 0.8713 | -0.0406 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | GRNDMEAD-ER8 | 0.9119 | 0.8713 | -0.0406 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | GRNDMEAD-ER8 | 0.9119 | 0.8713 | -0.0406 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | GRNDMEAD-ER8 | 0.9125 | 0.8726 | -0.0399 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | GRNDMEAD-ER8 | 0.9125 | 0.8726 | -0.0399 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | GRNDMEAD-ER8 | 0.9125 | 0.8726 | -0.0399 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | GRNDMEAD-ER8 | 0.9125 | 0.8726 | -0.0399 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | GRNDMEAD-ER8 | 0.9125 | 0.8726 | -0.0399 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | GRNDMEAD-ER8 | 0.9125 | 0.8726 | -0.0399 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | GRNDMEAD-ER8 | 0.9131 | 0.8732 | -0.0399 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | GRNDMEAD-ER8 | 0.9131 | 0.8732 | -0.0399 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | GRNDMEAD-ER8 | 0.9131 | 0.8732 | -0.0399 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | GRNDMEAD-ER8 | 0.9131 | 0.8732 | -0.0399 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | GRNDMEAD-ER8 | 0.9131 | 0.8732 | -0.0399 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | GRNDMEAD-ER8 | 0.9131 | 0.8732 | -0.0399 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | GRNDMEAD-ER8 | 0.914 | 0.8749 | -0.0391 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | GRNDMEAD-ER8 | 0.914 | 0.8749 | -0.0391 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | GRNDMEAD-ER8 | 0.914 | 0.8749 | -0.0391 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | GRNDMEAD-ER8 | 0.914 | 0.8749 | -0.0391 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | GRNDMEAD-ER8 | 0.914 | 0.8749 | -0.0391 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | GRNDMEAD-ER8 | 0.914 | 0.8749 | -0.0391 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | GRNDMEAD-ER8 | 0.9143 | 0.8755 | -0.0388 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | GRNDMEAD-ER8 | 0.9143 | 0.8755 | -0.0388 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | GRNDMEAD-ER8 | 0.9143 | 0.8755 | -0.0388 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | GRNDMEAD-ER8 | 0.9143 | 0.8755 | -0.0388 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | GRNDMEAD-ER8 | 0.9143 | 0.8755 | -0.0388 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | GRNDMEAD-ER8 | 0.9143 | 0.8755 | -0.0388 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HANLON1-ER8 | 0.9179 | 0.8748 | -0.0431 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HANLON1-ER8 | 0.9179 | 0.8748 | -0.0431 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HANLON1-ER8 | 0.9179 | 0.8748 | -0.0431 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HANLON1-ER8 | 0.9179 | 0.8748 | -0.0431 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HANLON1-ER8 | 0.9179 | 0.8748 | -0.0431 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HANLON1-ER8 | 0.9179 | 0.8748 | -0.0431 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HANLON1-ER8 | 0.9177 | 0.875 | -0.0427 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HANLON1-ER8 | 0.9177 | 0.875 | -0.0427 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HANLON1-ER8 | 0.9177 | 0.875 | -0.0427 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HANLON1-ER8 | 0.9177 | 0.875 | -0.0427 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HANLON1-ER8 | 0.9177 | 0.875 | -0.0427 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HANLON1-ER8 | 0.9177 | 0.875 | -0.0427 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HANLON1-ER8 | 0.9194 | 0.8792 | -0.0402 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HANLON1-ER8 | 0.9194 | 0.8792 | -0.0402 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HANLON1-ER8 | 0.9194 | 0.8792 | -0.0402 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HANLON1-ER8 | 0.9194 | 0.8792 | -0.0402 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HANLON1-ER8 | 0.9194 | 0.8792 | -0.0402 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HANLON1-ER8 | 0.9194 | 0.8792 | -0.0402 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | HANLON1-ER8 | 0.9204 | 0.8793 | -0.0411 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | HANLON1-ER8 | 0.9204 | 0.8793 | -0.0411 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | HANLON1-ER8 | 0.9204 | 0.8793 | -0.0411 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | HANLON1-ER8 | 0.9204 | 0.8793 | -0.0411 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | HANLON1-ER8 | 0.9204 | 0.8793 | -0.0411 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | HANLON1-ER8 | 0.9204 | 0.8793 | -0.0411 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | INDMARIN-ER8 | 0.8713 | 0.8251 | -0.0462 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | INDMARIN-ER8 | 0.8713 | 0.8251 | -0.0462 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | INDMARIN-ER8 | 0.8713 | 0.8251 | -0.0462 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | INDMARIN-ER8 | 0.8713 | 0.8251 | -0.0462 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | INDMARIN-ER8 | 0.8713 | 0.8251 | -0.0462 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | INDMARIN-ER8 | 0.8713 | 0.8251 | -0.0462 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | INDMARIN-ER8 | 0.8732 | 0.8297 | -0.0435 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | INDMARIN-ER8 | 0.8732 | 0.8297 | -0.0435 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | INDMARIN-ER8 | 0.8732 | 0.8297 | -0.0435 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | INDMARIN-ER8 | 0.8732 | 0.8297 | -0.0435 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | INDMARIN-ER8 | 0.8732 | 0.8297 | -0.0435 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | INDMARIN-ER8 | 0.8732 | 0.8297 | -0.0435 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | INDMARIN-ER8 | 0.8739 | 0.8306 | -0.0433 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | INDMARIN-ER8 | 0.8739 | 0.8306 | -0.0433 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | INDMARIN-ER8 | 0.8739 | 0.8306 | -0.0433 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | INDMARIN-ER8 | 0.8739 | 0.8306 | -0.0433 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | INDMARIN-ER8 | 0.8739 | 0.8306 | -0.0433 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | INDMARIN-ER8 | 0.8739 | 0.8306 | -0.0433 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | INDMARIN-ER8 | 0.8758 | 0.8314 | -0.0444 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | INDMARIN-ER8 | 0.8758 | 0.8314 | -0.0444 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | INDMARIN-ER8 | 0.8758 | 0.8314 | -0.0444 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | INDMARIN-ER8 | 0.8758 | 0.8314 | -0.0444 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | INDMARIN-ER8 | 0.8758 | 0.8314 | -0.0444 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | INDMARIN-ER8 | 0.8758 | 0.8314 | -0.0444 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | HANLON1-ER8 | 0.9204 | 0.8798 | -0.0406 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | HANLON1-ER8 | 0.9204 | 0.8798 | -0.0406 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | HANLON1-ER8 | 0.9204 | 0.8798 | -0.0406 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | HANLON1-ER8 | 0.9204 | 0.8798 | -0.0406 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | HANLON1-ER8 | 0.9204 | 0.8798 | -0.0406 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | HANLON1-ER8 | 0.9204 | 0.8798 | -0.0406 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HANLON1-ER8 | 0.9201 | 0.8801 | -0.04 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HANLON1-ER8 | 0.9201 | 0.8801 | -0.04 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HANLON1-ER8 | 0.9201 | 0.8801 | -0.04 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HANLON1-ER8 | 0.9201 | 0.8801 | -0.04 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HANLON1-ER8 | 0.9201 | 0.8801 | -0.04 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HANLON1-ER8 | 0.9201 | 0.8801 | -0.04 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HANLON1-ER8 | 0.9208 | 0.8813 | -0.0395 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HANLON1-ER8 | 0.9208 | 0.8813 | -0.0395 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HANLON1-ER8 | 0.9208 | 0.8813 | -0.0395 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HANLON1-ER8 | 0.9208 | 0.8813 | -0.0395 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HANLON1-ER8 | 0.9208 | 0.8813 | -0.0395 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HANLON1-ER8 | 0.9208 | 0.8813 | -0.0395 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | HANLON1-ER8 | 0.9223 | 0.8829 | -0.0394 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | HANLON1-ER8 | 0.9223 | 0.8829 | -0.0394 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | HANLON1-ER8 | 0.9223 | 0.8829 | -0.0394 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | HANLON1-ER8 | 0.9223 | 0.8829 | -0.0394 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | HANLON1-ER8 | 0.9223 | 0.8829 | -0.0394 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | HANLON1-ER8 | 0.9223 | 0.8829 | -0.0394 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | HANLON1-ER8 | 0.9232 | 0.8846 | -0.0386 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | HANLON1-ER8 | 0.9232 | 0.8846 | -0.0386 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | HANLON1-ER8 | 0.9232 | 0.8846 | -0.0386 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | HANLON1-ER8 | 0.9232 | 0.8846 | -0.0386 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | HANLON1-ER8 | 0.9232 | 0.8846 | -0.0386 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | HANLON1-ER8 | 0.9232 | 0.8846 | -0.0386 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | INDMARIN-ER8 | 0.8746 | 0.832 | -0.0426 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | INDMARIN-ER8 | 0.8746 | 0.832 | -0.0426 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | INDMARIN-ER8 | 0.8746 | 0.832 | -0.0426 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | INDMARIN-ER8 | 0.8746 | 0.832 | -0.0426 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | INDMARIN-ER8 | 0.8746 | 0.832 | -0.0426 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | INDMARIN-ER8 | 0.8746 | 0.832 | -0.0426 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | INDMARIN-ER8 | 0.8758 | 0.832 | -0.0438 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | INDMARIN-ER8 | 0.8758 | 0.832 | -0.0438 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | INDMARIN-ER8 | 0.8758 | 0.832 | -0.0438 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | INDMARIN-ER8 | 0.8758 | 0.832 | -0.0438 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | INDMARIN-ER8 | 0.8758 | 0.832 | -0.0438 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | INDMARIN-ER8 | 0.8758 | 0.832 | -0.0438 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | HANLON1-ER8 | 0.9235 | 0.8851 | -0.0384 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | HANLON1-ER8 | 0.9235 | 0.8851 | -0.0384 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | HANLON1-ER8 | 0.9235 | 0.8851 | -0.0384 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | HANLON1-ER8 | 0.9235 | 0.8851 | -0.0384 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | HANLON1-ER8 | 0.9235 | 0.8851 | -0.0384 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | HANLON1-ER8 | 0.9235 | 0.8851 | -0.0384 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HANLON2-ER8 | 0.9179 | 0.8748 | -0.0431 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HANLON2-ER8 | 0.9179 | 0.8748 | -0.0431 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HANLON2-ER8 | 0.9179 | 0.8748 | -0.0431 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HANLON2-ER8 | 0.9179 | 0.8748 | -0.0431 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HANLON2-ER8 | 0.9179 | 0.8748 | -0.0431 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HANLON2-ER8 | 0.9179 | 0.8748 | -0.0431 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | INDMARIN-ER8 | 0.8778 | 0.8354 | -0.0424 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | INDMARIN-ER8 | 0.8778 | 0.8354 | -0.0424 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | INDMARIN-ER8 | 0.8778 | 0.8354 | -0.0424 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | INDMARIN-ER8 | 0.8778 | 0.8354 | -0.0424 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | INDMARIN-ER8 | 0.8778 | 0.8354 | -0.0424 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | INDMARIN-ER8 | 0.8778 | 0.8354 | -0.0424 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | INDMARIN-ER8 | 0.8788 | 0.8372 | -0.0416 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | INDMARIN-ER8 | 0.8788 | 0.8372 | -0.0416 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | INDMARIN-ER8 | 0.8788 | 0.8372 | -0.0416 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | INDMARIN-ER8 | 0.8788 | 0.8372 | -0.0416 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | INDMARIN-ER8 | 0.8788 | 0.8372 | -0.0416 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | INDMARIN-ER8 | 0.8788 | 0.8372 | -0.0416 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | INDMARIN-ER8 | 0.8791 | 0.8378 | -0.0413 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | INDMARIN-ER8 | 0.8791 | 0.8378 | -0.0413 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | INDMARIN-ER8 | 0.8791 | 0.8378 | -0.0413 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | INDMARIN-ER8 | 0.8791 | 0.8378 | -0.0413 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | INDMARIN-ER8 | 0.8791 | 0.8378 | -0.0413 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | INDMARIN-ER8 | 0.8791 | 0.8378 | -0.0413 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HANLON2-ER8 | 0.9177 | 0.875 | -0.0427 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HANLON2-ER8 | 0.9177 | 0.875 | -0.0427 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HANLON2-ER8 | 0.9177 | 0.875 | -0.0427 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HANLON2-ER8 | 0.9177 | 0.875 | -0.0427 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HANLON2-ER8 | 0.9177 | 0.875 | -0.0427 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HANLON2-ER8 | 0.9177 | 0.875 | -0.0427 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HANLON2-ER8 | 0.9194 | 0.8792 | -0.0402 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HANLON2-ER8 | 0.9194 | 0.8792 | -0.0402 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HANLON2-ER8 | 0.9194 | 0.8792 | -0.0402 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HANLON2-ER8 | 0.9194 | 0.8792 | -0.0402 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HANLON2-ER8 | 0.9194 | 0.8792 | -0.0402 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HANLON2-ER8 | 0.9194 | 0.8792 | -0.0402 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | INDMARIN-ER8 | 0.8997 | 0.8689 | -0.0308 |  | 0.9 | 1.05 | 0.10642 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | INDMARIN-ER8 | 0.8997 | 0.8689 | -0.0308 |  | 0.9 | 1.05 | 0.24279 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | INDMARIN-ER8 | 0.8997 | 0.8689 | -0.0308 |  | 0.9 | 1.05 | 0.09958 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | INDMARIN-ER8 | 0.8997 | 0.8689 | -0.0308 |  | 0.9 | 1.05 | 0.03529 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | INDMARIN-ER8 | 0.8997 | 0.8689 | -0.0308 |  | 0.9 | 1.05 | 0.0709 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | INDMARIN-ER8 | 0.8997 | 0.8689 | -0.0308 |  | 0.9 | 1.05 | 0.14646 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | INDMARIN-ER8 | 0.8997 | 0.8689 | -0.0308 |  | 0.9 | 1.05 | 0.10642 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | INDMARIN-ER8 | 0.8997 | 0.8689 | -0.0308 |  | 0.9 | 1.05 | 0.24279 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | INDMARIN-ER8 | 0.8997 | 0.8689 | -0.0308 |  | 0.9 | 1.05 | 0.09958 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | INDMARIN-ER8 | 0.8997 | 0.8689 | -0.0308 |  | 0.9 | 1.05 | 0.03529 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | INDMARIN-ER8 | 0.8997 | 0.8689 | -0.0308 |  | 0.9 | 1.05 | 0.0709 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | INDMARIN-ER8 | 0.8997 | 0.8689 | -0.0308 |  | 0.9 | 1.05 | 0.14646 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | INDMARIN-ER8 | 0.8997 | 0.8689 | -0.0308 |  | 0.9 | 1.05 | 0.10642 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | INDMARIN-ER8 | 0.8997 | 0.8689 | -0.0308 |  | 0.9 | 1.05 | 0.24279 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | INDMARIN-ER8 | 0.8997 | 0.8689 | -0.0308 |  | 0.9 | 1.05 | 0.09958 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | INDMARIN-ER8 | 0.8997 | 0.8689 | -0.0308 |  | 0.9 | 1.05 | 0.03529 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | INDMARIN-ER8 | 0.8997 | 0.8689 | -0.0308 |  | 0.9 | 1.05 | 0.0709 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | INDMARIN-ER8 | 0.8997 | 0.8689 | -0.0308 |  | 0.9 | 1.05 | 0.14646 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | HANLON2-ER8 | 0.9204 | 0.8793 | -0.0411 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | HANLON2-ER8 | 0.9204 | 0.8793 | -0.0411 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | HANLON2-ER8 | 0.9204 | 0.8793 | -0.0411 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | HANLON2-ER8 | 0.9204 | 0.8793 | -0.0411 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | HANLON2-ER8 | 0.9204 | 0.8793 | -0.0411 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | HANLON2-ER8 | 0.9204 | 0.8793 | -0.0411 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | HANLON2-ER8 | 0.9204 | 0.8798 | -0.0406 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | HANLON2-ER8 | 0.9204 | 0.8798 | -0.0406 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | HANLON2-ER8 | 0.9204 | 0.8798 | -0.0406 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | HANLON2-ER8 | 0.9204 | 0.8798 | -0.0406 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | HANLON2-ER8 | 0.9204 | 0.8798 | -0.0406 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | HANLON2-ER8 | 0.9204 | 0.8798 | -0.0406 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HANLON2-ER8 | 0.9202 | 0.8801 | -0.0401 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HANLON2-ER8 | 0.9202 | 0.8801 | -0.0401 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HANLON2-ER8 | 0.9202 | 0.8801 | -0.0401 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HANLON2-ER8 | 0.9202 | 0.8801 | -0.0401 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HANLON2-ER8 | 0.9202 | 0.8801 | -0.0401 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HANLON2-ER8 | 0.9202 | 0.8801 | -0.0401 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HANLON2-ER8 | 0.9208 | 0.8813 | -0.0395 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HANLON2-ER8 | 0.9208 | 0.8813 | -0.0395 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HANLON2-ER8 | 0.9208 | 0.8813 | -0.0395 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HANLON2-ER8 | 0.9208 | 0.8813 | -0.0395 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HANLON2-ER8 | 0.9208 | 0.8813 | -0.0395 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HANLON2-ER8 | 0.9208 | 0.8813 | -0.0395 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | HANLON2-ER8 | 0.9223 | 0.8829 | -0.0394 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | HANLON2-ER8 | 0.9223 | 0.8829 | -0.0394 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | HANLON2-ER8 | 0.9223 | 0.8829 | -0.0394 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | HANLON2-ER8 | 0.9223 | 0.8829 | -0.0394 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | HANLON2-ER8 | 0.9223 | 0.8829 | -0.0394 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | HANLON2-ER8 | 0.9223 | 0.8829 | -0.0394 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | HANLON2-ER8 | 0.9232 | 0.8846 | -0.0386 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | HANLON2-ER8 | 0.9232 | 0.8846 | -0.0386 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | HANLON2-ER8 | 0.9232 | 0.8846 | -0.0386 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | HANLON2-ER8 | 0.9232 | 0.8846 | -0.0386 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | HANLON2-ER8 | 0.9232 | 0.8846 | -0.0386 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | HANLON2-ER8 | 0.9232 | 0.8846 | -0.0386 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | HANLON2-ER8 | 0.9235 | 0.8851 | -0.0384 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | HANLON2-ER8 | 0.9235 | 0.8851 | -0.0384 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | HANLON2-ER8 | 0.9235 | 0.8851 | -0.0384 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | HANLON2-ER8 | 0.9235 | 0.8851 | -0.0384 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | HANLON2-ER8 | 0.9235 | 0.8851 | -0.0384 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | HANLON2-ER8 | 0.9235 | 0.8851 | -0.0384 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | INDMARIN-ER8 | 0.9026 | 0.8736 | -0.029 |  | 0.9 | 1.05 | 0.10623 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | INDMARIN-ER8 | 0.9026 | 0.8736 | -0.029 |  | 0.9 | 1.05 | 0.24261 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | INDMARIN-ER8 | 0.9026 | 0.8736 | -0.029 |  | 0.9 | 1.05 | 0.1005 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | INDMARIN-ER8 | 0.9026 | 0.8736 | -0.029 |  | 0.9 | 1.05 | 0.03506 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | INDMARIN-ER8 | 0.9026 | 0.8736 | -0.029 |  | 0.9 | 1.05 | 0.07067 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | INDMARIN-ER8 | 0.9026 | 0.8736 | -0.029 |  | 0.9 | 1.05 | 0.14607 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | INDMARIN-ER8 | 0.9026 | 0.8736 | -0.029 |  | 0.9 | 1.05 | 0.10623 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | INDMARIN-ER8 | 0.9026 | 0.8736 | -0.029 |  | 0.9 | 1.05 | 0.24261 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | INDMARIN-ER8 | 0.9026 | 0.8736 | -0.029 |  | 0.9 | 1.05 | 0.1005 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | INDMARIN-ER8 | 0.9026 | 0.8736 | -0.029 |  | 0.9 | 1.05 | 0.03506 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | INDMARIN-ER8 | 0.9026 | 0.8736 | -0.029 |  | 0.9 | 1.05 | 0.07067 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | INDMARIN-ER8 | 0.9026 | 0.8736 | -0.029 |  | 0.9 | 1.05 | 0.14607 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | INDMARIN-ER8 | 0.9026 | 0.8736 | -0.029 |  | 0.9 | 1.05 | 0.10623 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | INDMARIN-ER8 | 0.9026 | 0.8736 | -0.029 |  | 0.9 | 1.05 | 0.24261 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | INDMARIN-ER8 | 0.9026 | 0.8736 | -0.029 |  | 0.9 | 1.05 | 0.1005 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | INDMARIN-ER8 | 0.9026 | 0.8736 | -0.029 |  | 0.9 | 1.05 | 0.03506 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | INDMARIN-ER8 | 0.9026 | 0.8736 | -0.029 |  | 0.9 | 1.05 | 0.07067 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | INDMARIN-ER8 | 0.9026 | 0.8736 | -0.029 |  | 0.9 | 1.05 | 0.14607 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | INDMARIN-ER8 | 0.9053 | 0.8808 | -0.0245 |  | 0.9 | 1.05 | 0.10941 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | INDMARIN-ER8 | 0.9053 | 0.8808 | -0.0245 |  | 0.9 | 1.05 | 0.05493 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | INDMARIN-ER8 | 0.9096 | 0.8852 | -0.0244 |  | 0.9 | 1.05 | 0.03069 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | INDMARIN-ER8 | 0.9096 | 0.8852 | -0.0244 |  | 0.9 | 1.05 | 0.10922 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | INDMARIN-ER8 | 0.9096 | 0.8852 | -0.0244 |  | 0.9 | 1.05 | 0.05476 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | INDMARIN-ER8 | 0.9078 | 0.8853 | -0.0225 |  | 0.9 | 1.05 | 0.05765 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | INDMARIN-ER8 | 0.9078 | 0.8853 | -0.0225 |  | 0.9 | 1.05 | 0.04499 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | INDMARIN-ER8 | 0.9078 | 0.8853 | -0.0225 |  | 0.9 | 1.05 | 0.05213 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | INDMARIN-ER8 | 0.9078 | 0.8853 | -0.0225 |  | 0.9 | 1.05 | 0.07544 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | INDMARIN-ER8 | 0.9078 | 0.8853 | -0.0225 |  | 0.9 | 1.05 | 0.07656 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | INDMARIN-ER8 | 0.9078 | 0.8853 | -0.0225 |  | 0.9 | 1.05 | 0.05236 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | INDMARIN-ER8 | 0.9084 | 0.8857 | -0.0227 |  | 0.9 | 1.05 | 0.03199 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | INDMARIN-ER8 | 0.9084 | 0.8857 | -0.0227 |  | 0.9 | 1.05 | 0.04873 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | INDMARIN-ER8 | 0.9084 | 0.8857 | -0.0227 |  | 0.9 | 1.05 | 0.09554 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | INDMARIN-ER8 | 0.9084 | 0.8857 | -0.0227 |  | 0.9 | 1.05 | 0.08589 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | INDMARIN-ER8 | 0.9084 | 0.8857 | -0.0227 |  | 0.9 | 1.05 | 0.04498 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | INDMARIN-ER8 | 0.9084 | 0.8861 | -0.0223 |  | 0.9 | 1.05 | 0.03222 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | INDMARIN-ER8 | 0.9084 | 0.8861 | -0.0223 |  | 0.9 | 1.05 | 0.04909 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | INDMARIN-ER8 | 0.9084 | 0.8861 | -0.0223 |  | 0.9 | 1.05 | 0.09624 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | INDMARIN-ER8 | 0.9084 | 0.8861 | -0.0223 |  | 0.9 | 1.05 | 0.08652 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | INDMARIN-ER8 | 0.9084 | 0.8861 | -0.0223 |  | 0.9 | 1.05 | 0.04531 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HILLTOP-ER8 | 0.9284 | 0.8769 | -0.0515 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HILLTOP-ER8 | 0.9284 | 0.8769 | -0.0515 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HILLTOP-ER8 | 0.9284 | 0.8769 | -0.0515 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HILLTOP-ER8 | 0.9284 | 0.8769 | -0.0515 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HILLTOP-ER8 | 0.9284 | 0.8769 | -0.0515 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HILLTOP-ER8 | 0.9284 | 0.8769 | -0.0515 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HILLTOP-ER8 | 0.9281 | 0.8771 | -0.051 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HILLTOP-ER8 | 0.9281 | 0.8771 | -0.051 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HILLTOP-ER8 | 0.9281 | 0.8771 | -0.051 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HILLTOP-ER8 | 0.9281 | 0.8771 | -0.051 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HILLTOP-ER8 | 0.9281 | 0.8771 | -0.051 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HILLTOP-ER8 | 0.9281 | 0.8771 | -0.051 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | HILLTOP-ER8 | 0.9299 | 0.8826 | -0.0473 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | HILLTOP-ER8 | 0.9299 | 0.8826 | -0.0473 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | HILLTOP-ER8 | 0.9299 | 0.8826 | -0.0473 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | HILLTOP-ER8 | 0.9299 | 0.8826 | -0.0473 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | HILLTOP-ER8 | 0.9299 | 0.8826 | -0.0473 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | HILLTOP-ER8 | 0.9299 | 0.8826 | -0.0473 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | HILLTOP-ER8 | 0.9299 | 0.8832 | -0.0467 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | HILLTOP-ER8 | 0.9299 | 0.8832 | -0.0467 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | HILLTOP-ER8 | 0.9299 | 0.8832 | -0.0467 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | HILLTOP-ER8 | 0.9299 | 0.8832 | -0.0467 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | HILLTOP-ER8 | 0.9299 | 0.8832 | -0.0467 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | HILLTOP-ER8 | 0.9299 | 0.8832 | -0.0467 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HILLTOP-ER8 | 0.9311 | 0.8855 | -0.0456 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HILLTOP-ER8 | 0.9311 | 0.8855 | -0.0456 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HILLTOP-ER8 | 0.9311 | 0.8855 | -0.0456 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HILLTOP-ER8 | 0.9311 | 0.8855 | -0.0456 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HILLTOP-ER8 | 0.9311 | 0.8855 | -0.0456 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HILLTOP-ER8 | 0.9311 | 0.8855 | -0.0456 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HILLTOP-ER8 | 0.9327 | 0.8875 | -0.0452 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HILLTOP-ER8 | 0.9327 | 0.8875 | -0.0452 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HILLTOP-ER8 | 0.9327 | 0.8875 | -0.0452 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HILLTOP-ER8 | 0.9327 | 0.8875 | -0.0452 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HILLTOP-ER8 | 0.9327 | 0.8875 | -0.0452 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HILLTOP-ER8 | 0.9327 | 0.8875 | -0.0452 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HILLTOP-ER8 | 0.9334 | 0.8887 | -0.0447 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HILLTOP-ER8 | 0.9334 | 0.8887 | -0.0447 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HILLTOP-ER8 | 0.9334 | 0.8887 | -0.0447 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HILLTOP-ER8 | 0.9334 | 0.8887 | -0.0447 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HILLTOP-ER8 | 0.9334 | 0.8887 | -0.0447 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HILLTOP-ER8 | 0.9334 | 0.8887 | -0.0447 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | INDMARIN-ER8 | 0.9093 | 0.8866 | -0.0227 |  | 0.9 | 1.05 | 0.03222 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | INDMARIN-ER8 | 0.9093 | 0.8866 | -0.0227 |  | 0.9 | 1.05 | 0.04909 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | INDMARIN-ER8 | 0.9093 | 0.8866 | -0.0227 |  | 0.9 | 1.05 | 0.09624 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | INDMARIN-ER8 | 0.9093 | 0.8866 | -0.0227 |  | 0.9 | 1.05 | 0.08652 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | INDMARIN-ER8 | 0.9093 | 0.8866 | -0.0227 |  | 0.9 | 1.05 | 0.04531 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | HILLTOP-ER8 | 0.933 | 0.8887 | -0.0443 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | HILLTOP-ER8 | 0.933 | 0.8887 | -0.0443 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | HILLTOP-ER8 | 0.933 | 0.8887 | -0.0443 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | HILLTOP-ER8 | 0.933 | 0.8887 | -0.0443 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | HILLTOP-ER8 | 0.933 | 0.8887 | -0.0443 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | HILLTOP-ER8 | 0.933 | 0.8887 | -0.0443 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | HILLTOP-ER8 | 0.9348 | 0.8914 | -0.0434 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | HILLTOP-ER8 | 0.9348 | 0.8914 | -0.0434 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | HILLTOP-ER8 | 0.9348 | 0.8914 | -0.0434 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | HILLTOP-ER8 | 0.9348 | 0.8914 | -0.0434 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | HILLTOP-ER8 | 0.9348 | 0.8914 | -0.0434 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | HILLTOP-ER8 | 0.9348 | 0.8914 | -0.0434 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | INDMARIN-ER8 | 0.9102 | 0.8871 | -0.0231 |  | 0.9 | 1.05 | 0.05765 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | INDMARIN-ER8 | 0.9102 | 0.8871 | -0.0231 |  | 0.9 | 1.05 | 0.04499 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | INDMARIN-ER8 | 0.9102 | 0.8871 | -0.0231 |  | 0.9 | 1.05 | 0.05213 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | INDMARIN-ER8 | 0.9102 | 0.8871 | -0.0231 |  | 0.9 | 1.05 | 0.07544 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | INDMARIN-ER8 | 0.9102 | 0.8871 | -0.0231 |  | 0.9 | 1.05 | 0.07656 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | INDMARIN-ER8 | 0.9102 | 0.8871 | -0.0231 |  | 0.9 | 1.05 | 0.05236 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | HILLTOP-ER8 | 0.9351 | 0.892 | -0.0431 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | HILLTOP-ER8 | 0.9351 | 0.892 | -0.0431 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | HILLTOP-ER8 | 0.9351 | 0.892 | -0.0431 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | HILLTOP-ER8 | 0.9351 | 0.892 | -0.0431 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | HILLTOP-ER8 | 0.9351 | 0.892 | -0.0431 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | HILLTOP-ER8 | 0.9351 | 0.892 | -0.0431 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HRRISBRG-ER7 | 0.9267 | 0.8907 | -0.036 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HRRISBRG-ER7 | 0.9267 | 0.8907 | -0.036 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HRRISBRG-ER7 | 0.9267 | 0.8907 | -0.036 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HRRISBRG-ER7 | 0.9267 | 0.8907 | -0.036 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HRRISBRG-ER7 | 0.9267 | 0.8907 | -0.036 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HRRISBRG-ER7 | 0.9267 | 0.8907 | -0.036 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HRRISBRG-ER7 | 0.9265 | 0.8909 | -0.0356 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HRRISBRG-ER7 | 0.9265 | 0.8909 | -0.0356 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HRRISBRG-ER7 | 0.9265 | 0.8909 | -0.0356 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HRRISBRG-ER7 | 0.9265 | 0.8909 | -0.0356 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HRRISBRG-ER7 | 0.9265 | 0.8909 | -0.0356 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HRRISBRG-ER7 | 0.9265 | 0.8909 | -0.0356 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HRRISBRG-ER7 | 0.9274 | 0.8929 | -0.0345 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HRRISBRG-ER7 | 0.9274 | 0.8929 | -0.0345 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HRRISBRG-ER7 | 0.9274 | 0.8929 | -0.0345 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HRRISBRG-ER7 | 0.9274 | 0.8929 | -0.0345 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HRRISBRG-ER7 | 0.9274 | 0.8929 | -0.0345 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HRRISBRG-ER7 | 0.9274 | 0.8929 | -0.0345 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HRRISBRG-ER7 | 0.9281 | 0.8939 | -0.0342 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HRRISBRG-ER7 | 0.9281 | 0.8939 | -0.0342 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HRRISBRG-ER7 | 0.9281 | 0.8939 | -0.0342 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HRRISBRG-ER7 | 0.9281 | 0.8939 | -0.0342 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HRRISBRG-ER7 | 0.9281 | 0.8939 | -0.0342 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HRRISBRG-ER7 | 0.9281 | 0.8939 | -0.0342 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | INDMARIN-ER8 | 0.917 | 0.8903 | -0.0267 |  | 0.9 | 1.05 | 0.10782 | 601048 LYON CO 3 345 601077 HAWKSNEST 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | INDMARIN-ER8 | 0.917 | 0.8903 | -0.0267 |  | 0.9 | 1.05 | 0.2135 | 601048 LYON CO 3 345 601077 HAWKSNEST 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | INDMARIN-ER8 | 0.917 | 0.8903 | -0.0267 |  | 0.9 | 1.05 | 0.03689 | 601048 LYON CO 3 345 601077 HAWKSNEST 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | INDMARIN-ER8 | 0.917 | 0.8903 | -0.0267 |  | 0.9 | 1.05 | 0.04864 | 601048 LYON CO 3 345 601077 HAWKSNEST 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | INDMARIN-ER8 | 0.917 | 0.8903 | -0.0267 |  | 0.9 | 1.05 | 0.06643 | 601048 LYON CO 3 345 601077 HAWKSNEST 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | INDMARIN-ER8 | 0.917 | 0.8903 | -0.0267 |  | 0.9 | 1.05 | 0.08939 | 601048 LYON CO 3 345 601077 HAWKSNEST 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HRRISBRG-ER7 | 0.9288 | 0.8949 | -0.0339 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HRRISBRG-ER7 | 0.9288 | 0.8949 | -0.0339 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HRRISBRG-ER7 | 0.9288 | 0.8949 | -0.0339 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HRRISBRG-ER7 | 0.9288 | 0.8949 | -0.0339 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HRRISBRG-ER7 | 0.9288 | 0.8949 | -0.0339 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HRRISBRG-ER7 | 0.9288 | 0.8949 | -0.0339 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HUMBOLT-ER8 | 0.9146 | 0.8713 | -0.0433 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HUMBOLT-ER8 | 0.9146 | 0.8713 | -0.0433 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HUMBOLT-ER8 | 0.9146 | 0.8713 | -0.0433 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HUMBOLT-ER8 | 0.9146 | 0.8713 | -0.0433 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HUMBOLT-ER8 | 0.9146 | 0.8713 | -0.0433 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HUMBOLT-ER8 | 0.9146 | 0.8713 | -0.0433 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | INDMARIN-ER8 | 0.917 | 0.8906 | -0.0264 |  | 0.9 | 1.05 | 0.10782 | 601077 HAWKSNEST 3 345 601087 STEEP BK LK3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | INDMARIN-ER8 | 0.917 | 0.8906 | -0.0264 |  | 0.9 | 1.05 | 0.2135 | 601077 HAWKSNEST 3 345 601087 STEEP BK LK3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | INDMARIN-ER8 | 0.917 | 0.8906 | -0.0264 |  | 0.9 | 1.05 | 0.03689 | 601077 HAWKSNEST 3 345 601087 STEEP BK LK3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | INDMARIN-ER8 | 0.917 | 0.8906 | -0.0264 |  | 0.9 | 1.05 | 0.04864 | 601077 HAWKSNEST 3 345 601087 STEEP BK LK3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | INDMARIN-ER8 | 0.917 | 0.8906 | -0.0264 |  | 0.9 | 1.05 | 0.06643 | 601077 HAWKSNEST 3 345 601087 STEEP BK LK3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | INDMARIN-ER8 | 0.917 | 0.8906 | -0.0264 |  | 0.9 | 1.05 | 0.08939 | 601077 HAWKSNEST 3 345 601087 STEEP BK LK3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | INDMARIN-ER8 | 0.917 | 0.8907 | -0.0263 |  | 0.9 | 1.05 | 0.03163 | POI 763443_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | INDMARIN-ER8 | 0.917 | 0.8907 | -0.0263 |  | 0.9 | 1.05 | 0.10289 | POI 763443_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | INDMARIN-ER8 | 0.917 | 0.8907 | -0.0263 |  | 0.9 | 1.05 | 0.059 | POI 763443_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HUMBOLT-ER8 | 0.9144 | 0.8715 | -0.0429 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HUMBOLT-ER8 | 0.9144 | 0.8715 | -0.0429 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HUMBOLT-ER8 | 0.9144 | 0.8715 | -0.0429 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HUMBOLT-ER8 | 0.9144 | 0.8715 | -0.0429 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HUMBOLT-ER8 | 0.9144 | 0.8715 | -0.0429 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HUMBOLT-ER8 | 0.9144 | 0.8715 | -0.0429 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | HUMBOLT-ER8 | 0.9167 | 0.8754 | -0.0413 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | HUMBOLT-ER8 | 0.9167 | 0.8754 | -0.0413 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | HUMBOLT-ER8 | 0.9167 | 0.8754 | -0.0413 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | HUMBOLT-ER8 | 0.9167 | 0.8754 | -0.0413 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | HUMBOLT-ER8 | 0.9167 | 0.8754 | -0.0413 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | HUMBOLT-ER8 | 0.9167 | 0.8754 | -0.0413 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HUMBOLT-ER8 | 0.9161 | 0.8757 | -0.0404 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HUMBOLT-ER8 | 0.9161 | 0.8757 | -0.0404 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HUMBOLT-ER8 | 0.9161 | 0.8757 | -0.0404 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HUMBOLT-ER8 | 0.9161 | 0.8757 | -0.0404 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HUMBOLT-ER8 | 0.9161 | 0.8757 | -0.0404 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HUMBOLT-ER8 | 0.9161 | 0.8757 | -0.0404 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | HUMBOLT-ER8 | 0.9167 | 0.876 | -0.0407 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | HUMBOLT-ER8 | 0.9167 | 0.876 | -0.0407 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | HUMBOLT-ER8 | 0.9167 | 0.876 | -0.0407 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | HUMBOLT-ER8 | 0.9167 | 0.876 | -0.0407 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | HUMBOLT-ER8 | 0.9167 | 0.876 | -0.0407 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | HUMBOLT-ER8 | 0.9167 | 0.876 | -0.0407 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HUMBOLT-ER8 | 0.9169 | 0.8766 | -0.0403 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HUMBOLT-ER8 | 0.9169 | 0.8766 | -0.0403 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HUMBOLT-ER8 | 0.9169 | 0.8766 | -0.0403 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HUMBOLT-ER8 | 0.9169 | 0.8766 | -0.0403 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HUMBOLT-ER8 | 0.9169 | 0.8766 | -0.0403 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HUMBOLT-ER8 | 0.9169 | 0.8766 | -0.0403 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | HUMBOLT-ER8 | 0.9175 | 0.8778 | -0.0397 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | HUMBOLT-ER8 | 0.9175 | 0.8778 | -0.0397 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | HUMBOLT-ER8 | 0.9175 | 0.8778 | -0.0397 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | HUMBOLT-ER8 | 0.9175 | 0.8778 | -0.0397 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | HUMBOLT-ER8 | 0.9175 | 0.8778 | -0.0397 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | HUMBOLT-ER8 | 0.9175 | 0.8778 | -0.0397 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | INDMARIN-ER8 | 0.917 | 0.8907 | -0.0263 |  | 0.9 | 1.05 | 0.03163 | 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | INDMARIN-ER8 | 0.917 | 0.8907 | -0.0263 |  | 0.9 | 1.05 | 0.10289 | 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | INDMARIN-ER8 | 0.917 | 0.8907 | -0.0263 |  | 0.9 | 1.05 | 0.059 | 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | HUMBOLT-ER8 | 0.9186 | 0.879 | -0.0396 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | HUMBOLT-ER8 | 0.9186 | 0.879 | -0.0396 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | HUMBOLT-ER8 | 0.9186 | 0.879 | -0.0396 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | HUMBOLT-ER8 | 0.9186 | 0.879 | -0.0396 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | HUMBOLT-ER8 | 0.9186 | 0.879 | -0.0396 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | HUMBOLT-ER8 | 0.9186 | 0.879 | -0.0396 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | HUMBOLT-ER8 | 0.9196 | 0.8808 | -0.0388 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | HUMBOLT-ER8 | 0.9196 | 0.8808 | -0.0388 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | HUMBOLT-ER8 | 0.9196 | 0.8808 | -0.0388 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | HUMBOLT-ER8 | 0.9196 | 0.8808 | -0.0388 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | HUMBOLT-ER8 | 0.9196 | 0.8808 | -0.0388 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | HUMBOLT-ER8 | 0.9196 | 0.8808 | -0.0388 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | HUMBOLT-ER8 | 0.9199 | 0.8813 | -0.0386 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | HUMBOLT-ER8 | 0.9199 | 0.8813 | -0.0386 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | HUMBOLT-ER8 | 0.9199 | 0.8813 | -0.0386 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | HUMBOLT-ER8 | 0.9199 | 0.8813 | -0.0386 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | HUMBOLT-ER8 | 0.9199 | 0.8813 | -0.0386 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | HUMBOLT-ER8 | 0.9199 | 0.8813 | -0.0386 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | INDMARIN-ER8 | 0.9126 | 0.8908 | -0.0218 |  | 0.9 | 1.05 | 0.05737 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | INDMARIN-ER8 | 0.9126 | 0.8908 | -0.0218 |  | 0.9 | 1.05 | 0.04472 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | INDMARIN-ER8 | 0.9126 | 0.8908 | -0.0218 |  | 0.9 | 1.05 | 0.05275 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | INDMARIN-ER8 | 0.9126 | 0.8908 | -0.0218 |  | 0.9 | 1.05 | 0.07518 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | INDMARIN-ER8 | 0.9126 | 0.8908 | -0.0218 |  | 0.9 | 1.05 | 0.0763 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | INDMARIN-ER8 | 0.9126 | 0.8908 | -0.0218 |  | 0.9 | 1.05 | 0.05195 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | INDMARIN-ER8 | 0.917 | 0.8909 | -0.0261 |  | 0.9 | 1.05 | 0.0409 | POI 640374_5 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | INDMARIN-ER8 | 0.917 | 0.8909 | -0.0261 |  | 0.9 | 1.05 | 0.03631 | POI 640374_5 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | INDMARIN-ER8 | 0.917 | 0.8909 | -0.0261 |  | 0.9 | 1.05 | 0.04514 | POI 640374_5 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | INDMARIN-ER8 | 0.917 | 0.8909 | -0.0261 |  | 0.9 | 1.05 | 0.05706 | POI 640374_5 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | INDMARIN-ER8 | 0.917 | 0.8909 | -0.0261 |  | 0.9 | 1.05 | 0.05004 | POI 640374_5 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | INDMARIN-ER8 | 0.917 | 0.8909 | -0.0261 |  | 0.9 | 1.05 | 0.04219 | POI 640374_5 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | INDMARIN-ER8 | 0.9128 | 0.8909 | -0.0219 |  | 0.9 | 1.05 | 0.03187 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | INDMARIN-ER8 | 0.9128 | 0.8909 | -0.0219 |  | 0.9 | 1.05 | 0.04986 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | INDMARIN-ER8 | 0.9128 | 0.8909 | -0.0219 |  | 0.9 | 1.05 | 0.09536 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | INDMARIN-ER8 | 0.9128 | 0.8909 | -0.0219 |  | 0.9 | 1.05 | 0.08573 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | INDMARIN-ER8 | 0.9128 | 0.8909 | -0.0219 |  | 0.9 | 1.05 | 0.04463 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | INDMARIN-ER8 | 0.917 | 0.891 | -0.026 |  | 0.9 | 1.05 | 0.10782 | 157232 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | INDMARIN-ER8 | 0.917 | 0.891 | -0.026 |  | 0.9 | 1.05 | 0.2135 | 157232 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | INDMARIN-ER8 | 0.917 | 0.891 | -0.026 |  | 0.9 | 1.05 | 0.03689 | 157232 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | INDMARIN-ER8 | 0.917 | 0.891 | -0.026 |  | 0.9 | 1.05 | 0.04864 | 157232 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | INDMARIN-ER8 | 0.917 | 0.891 | -0.026 |  | 0.9 | 1.05 | 0.06643 | 157232 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | INDMARIN-ER8 | 0.917 | 0.891 | -0.026 |  | 0.9 | 1.05 | 0.08939 | 157232 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | INDMARIN-ER8 | 0.917 | 0.891 | -0.026 |  | 0.9 | 1.05 | 0.10782 | 152186 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | INDMARIN-ER8 | 0.917 | 0.891 | -0.026 |  | 0.9 | 1.05 | 0.2135 | 152186 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | INDMARIN-ER8 | 0.917 | 0.891 | -0.026 |  | 0.9 | 1.05 | 0.03689 | 152186 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | INDMARIN-ER8 | 0.917 | 0.891 | -0.026 |  | 0.9 | 1.05 | 0.04864 | 152186 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | INDMARIN-ER8 | 0.917 | 0.891 | -0.026 |  | 0.9 | 1.05 | 0.06643 | 152186 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | INDMARIN-ER8 | 0.917 | 0.891 | -0.026 |  | 0.9 | 1.05 | 0.08939 | 152186 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | INDMARIN-ER8 | 0.917 | 0.8911 | -0.0259 |  | 0.9 | 1.05 | 0.07189 | 154070 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | INDMARIN-ER8 | 0.917 | 0.8911 | -0.0259 |  | 0.9 | 1.05 | 0.05321 | 154070 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | INDMARIN-ER8 | 0.917 | 0.8911 | -0.0259 |  | 0.9 | 1.05 | 0.03163 | POI 640226_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | INDMARIN-ER8 | 0.917 | 0.8911 | -0.0259 |  | 0.9 | 1.05 | 0.10289 | POI 640226_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | INDMARIN-ER8 | 0.917 | 0.8911 | -0.0259 |  | 0.9 | 1.05 | 0.059 | POI 640226_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | INDMARIN-ER8 | 0.917 | 0.8913 | -0.0257 |  | 0.9 | 1.05 | 0.08163 | POI 620369_0 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | INDMARIN-ER8 | 0.917 | 0.8913 | -0.0257 |  | 0.9 | 1.05 | 0.04882 | POI 620369_0 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | INDMARIN-ER8 | 0.9127 | 0.8913 | -0.0214 |  | 0.9 | 1.05 | 0.03211 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | INDMARIN-ER8 | 0.9127 | 0.8913 | -0.0214 |  | 0.9 | 1.05 | 0.05023 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | INDMARIN-ER8 | 0.9127 | 0.8913 | -0.0214 |  | 0.9 | 1.05 | 0.09607 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | INDMARIN-ER8 | 0.9127 | 0.8913 | -0.0214 |  | 0.9 | 1.05 | 0.08636 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | INDMARIN-ER8 | 0.9127 | 0.8913 | -0.0214 |  | 0.9 | 1.05 | 0.04496 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | INDMARIN-ER8 | 0.917 | 0.8914 | -0.0256 |  | 0.9 | 1.05 | 0.07189 | 601067 BISON 3 345 658049 ALXLNRCTRT 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | INDMARIN-ER8 | 0.917 | 0.8914 | -0.0256 |  | 0.9 | 1.05 | 0.05321 | 601067 BISON 3 345 658049 ALXLNRCTRT 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | LAKPLAT-ER8 | 0.9426 | 0.8926 | -0.05 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | LAKPLAT-ER8 | 0.9426 | 0.8926 | -0.05 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | LAKPLAT-ER8 | 0.9426 | 0.8926 | -0.05 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | LAKPLAT-ER8 | 0.9426 | 0.8926 | -0.05 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | LAKPLAT-ER8 | 0.9426 | 0.8926 | -0.05 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | LAKPLAT-ER8 | 0.9426 | 0.8926 | -0.05 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | INDMARIN-ER8 | 0.917 | 0.8914 | -0.0256 |  | 0.9 | 1.05 | 0.0343 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | INDMARIN-ER8 | 0.917 | 0.8915 | -0.0255 |  | 0.9 | 1.05 | 0.07189 | 658047 ALEXMRES3 345 658049 ALXLNRCTRT 345 Z1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | INDMARIN-ER8 | 0.917 | 0.8915 | -0.0255 |  | 0.9 | 1.05 | 0.05321 | 658047 ALEXMRES3 345 658049 ALXLNRCTRT 345 Z1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | LAKPLAT-ER8 | 0.9423 | 0.8928 | -0.0495 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | LAKPLAT-ER8 | 0.9423 | 0.8928 | -0.0495 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | LAKPLAT-ER8 | 0.9423 | 0.8928 | -0.0495 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | LAKPLAT-ER8 | 0.9423 | 0.8928 | -0.0495 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | LAKPLAT-ER8 | 0.9423 | 0.8928 | -0.0495 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | LAKPLAT-ER8 | 0.9423 | 0.8928 | -0.0495 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | LAKPLAT-ER8 | 0.9444 | 0.8985 | -0.0459 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | LAKPLAT-ER8 | 0.9444 | 0.8985 | -0.0459 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | LAKPLAT-ER8 | 0.9444 | 0.8985 | -0.0459 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | LAKPLAT-ER8 | 0.9444 | 0.8985 | -0.0459 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | LAKPLAT-ER8 | 0.9444 | 0.8985 | -0.0459 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | LAKPLAT-ER8 | 0.9444 | 0.8985 | -0.0459 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | LAKPLAT-ER8 | 0.9444 | 0.8991 | -0.0453 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | LAKPLAT-ER8 | 0.9444 | 0.8991 | -0.0453 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | LAKPLAT-ER8 | 0.9444 | 0.8991 | -0.0453 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | LAKPLAT-ER8 | 0.9444 | 0.8991 | -0.0453 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | LAKPLAT-ER8 | 0.9444 | 0.8991 | -0.0453 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | LAKPLAT-ER8 | 0.9444 | 0.8991 | -0.0453 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | INDMARIN-ER8 | 0.917 | 0.8915 | -0.0255 |  | 0.9 | 1.05 | 0.06985 | P42:345:NPPD:BKR-HOS-3308:::: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | INDMARIN-ER8 | 0.917 | 0.8915 | -0.0255 |  | 0.9 | 1.05 | 0.06933 | P42:345:NPPD:BKR-HOS-3308:::: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | INDMARIN-ER8 | 0.917 | 0.8915 | -0.0255 |  | 0.9 | 1.05 | 0.0608 | P42:345:NPPD:BKR-HOS-3308:::: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | INDMARIN-ER8 | 0.917 | 0.8915 | -0.0255 |  | 0.9 | 1.05 | 0.06888 | P42:345:NPPD:BKR-HOS-3308:::: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | INDMARIN-ER8 | 0.917 | 0.8915 | -0.0255 |  | 0.9 | 1.05 | 0.06404 | P42:345:NPPD:BKR-HOS-3308:::: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | INDMARIN-ER8 | 0.917 | 0.8915 | -0.0255 |  | 0.9 | 1.05 | 0.06419 | P42:345:NPPD:BKR-HOS-3308:::: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | INDMARIN-ER8 | 0.917 | 0.8915 | -0.0255 |  | 0.9 | 1.05 | 0.06985 | POI 640226_5 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | INDMARIN-ER8 | 0.917 | 0.8915 | -0.0255 |  | 0.9 | 1.05 | 0.06933 | POI 640226_5 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | INDMARIN-ER8 | 0.917 | 0.8915 | -0.0255 |  | 0.9 | 1.05 | 0.0608 | POI 640226_5 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | INDMARIN-ER8 | 0.917 | 0.8915 | -0.0255 |  | 0.9 | 1.05 | 0.06888 | POI 640226_5 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | INDMARIN-ER8 | 0.917 | 0.8915 | -0.0255 |  | 0.9 | 1.05 | 0.06404 | POI 640226_5 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | INDMARIN-ER8 | 0.917 | 0.8915 | -0.0255 |  | 0.9 | 1.05 | 0.06419 | POI 640226_5 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | INDMARIN-ER8 | 0.9136 | 0.8918 | -0.0218 |  | 0.9 | 1.05 | 0.03211 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | INDMARIN-ER8 | 0.9136 | 0.8918 | -0.0218 |  | 0.9 | 1.05 | 0.05023 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | INDMARIN-ER8 | 0.9136 | 0.8918 | -0.0218 |  | 0.9 | 1.05 | 0.09607 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | INDMARIN-ER8 | 0.9136 | 0.8918 | -0.0218 |  | 0.9 | 1.05 | 0.08636 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | INDMARIN-ER8 | 0.9136 | 0.8918 | -0.0218 |  | 0.9 | 1.05 | 0.04496 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | LINCOLN-ER7 | 0.9267 | 0.8906 | -0.0361 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | LINCOLN-ER7 | 0.9267 | 0.8906 | -0.0361 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | LINCOLN-ER7 | 0.9267 | 0.8906 | -0.0361 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | LINCOLN-ER7 | 0.9267 | 0.8906 | -0.0361 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | LINCOLN-ER7 | 0.9267 | 0.8906 | -0.0361 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | LINCOLN-ER7 | 0.9267 | 0.8906 | -0.0361 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | LINCOLN-ER7 | 0.9265 | 0.8908 | -0.0357 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | LINCOLN-ER7 | 0.9265 | 0.8908 | -0.0357 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | LINCOLN-ER7 | 0.9265 | 0.8908 | -0.0357 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | LINCOLN-ER7 | 0.9265 | 0.8908 | -0.0357 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | LINCOLN-ER7 | 0.9265 | 0.8908 | -0.0357 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | LINCOLN-ER7 | 0.9265 | 0.8908 | -0.0357 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | LINCOLN-ER7 | 0.9274 | 0.8929 | -0.0345 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | LINCOLN-ER7 | 0.9274 | 0.8929 | -0.0345 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | LINCOLN-ER7 | 0.9274 | 0.8929 | -0.0345 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | LINCOLN-ER7 | 0.9274 | 0.8929 | -0.0345 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | LINCOLN-ER7 | 0.9274 | 0.8929 | -0.0345 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | LINCOLN-ER7 | 0.9274 | 0.8929 | -0.0345 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | INDMARIN-ER8 | 0.9199 | 0.8967 | -0.0232 |  | 0.9 | 1.05 | 0.10739 | 157232 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | INDMARIN-ER8 | 0.9199 | 0.8967 | -0.0232 |  | 0.9 | 1.05 | 0.21314 | 157232 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | INDMARIN-ER8 | 0.9199 | 0.8967 | -0.0232 |  | 0.9 | 1.05 | 0.04006 | 157232 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | INDMARIN-ER8 | 0.9199 | 0.8967 | -0.0232 |  | 0.9 | 1.05 | 0.04806 | 157232 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | INDMARIN-ER8 | 0.9199 | 0.8967 | -0.0232 |  | 0.9 | 1.05 | 0.06592 | 157232 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | INDMARIN-ER8 | 0.9199 | 0.8967 | -0.0232 |  | 0.9 | 1.05 | 0.08838 | 157232 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | LINCOLN-ER7 | 0.9281 | 0.8938 | -0.0343 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | LINCOLN-ER7 | 0.9281 | 0.8938 | -0.0343 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | LINCOLN-ER7 | 0.9281 | 0.8938 | -0.0343 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | LINCOLN-ER7 | 0.9281 | 0.8938 | -0.0343 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | LINCOLN-ER7 | 0.9281 | 0.8938 | -0.0343 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | LINCOLN-ER7 | 0.9281 | 0.8938 | -0.0343 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | LINCOLN-ER7 | 0.9287 | 0.8948 | -0.0339 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | LINCOLN-ER7 | 0.9287 | 0.8948 | -0.0339 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | LINCOLN-ER7 | 0.9287 | 0.8948 | -0.0339 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | LINCOLN-ER7 | 0.9287 | 0.8948 | -0.0339 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | LINCOLN-ER7 | 0.9287 | 0.8948 | -0.0339 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | LINCOLN-ER7 | 0.9287 | 0.8948 | -0.0339 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | INDMARIN-ER8 | 0.9199 | 0.8967 | -0.0232 |  | 0.9 | 1.05 | 0.10739 | 152186 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | INDMARIN-ER8 | 0.9199 | 0.8967 | -0.0232 |  | 0.9 | 1.05 | 0.21314 | 152186 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | INDMARIN-ER8 | 0.9199 | 0.8967 | -0.0232 |  | 0.9 | 1.05 | 0.04006 | 152186 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | INDMARIN-ER8 | 0.9199 | 0.8967 | -0.0232 |  | 0.9 | 1.05 | 0.04806 | 152186 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | INDMARIN-ER8 | 0.9199 | 0.8967 | -0.0232 |  | 0.9 | 1.05 | 0.06592 | 152186 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | INDMARIN-ER8 | 0.9199 | 0.8967 | -0.0232 |  | 0.9 | 1.05 | 0.08838 | 152186 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | INDMARIN-ER8 | 0.9199 | 0.8969 | -0.023 |  | 0.9 | 1.05 | 0.11733 | 659423 GR.LS-LO-BE3 345 762544 G23-182-TAP 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | INDMARIN-ER8 | 0.9199 | 0.8969 | -0.023 |  | 0.9 | 1.05 | 0.49292 | 659423 GR.LS-LO-BE3 345 762544 G23-182-TAP 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | INDMARIN-ER8 | 0.9199 | 0.8969 | -0.023 |  | 0.9 | 1.05 | 0.0725 | 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | INDMARIN-ER8 | 0.9199 | 0.8969 | -0.023 |  | 0.9 | 1.05 | 0.0508 | 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | INDMARIN-ER8 | 0.9199 | 0.8969 | -0.023 |  | 0.9 | 1.05 | 0.0336 | 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | INDMARIN-ER8 | 0.9199 | 0.8969 | -0.023 |  | 0.9 | 1.05 | 0.03699 | 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | INDMARIN-ER8 | 0.9199 | 0.8969 | -0.023 |  | 0.9 | 1.05 | 0.04366 | 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | INDMARIN-ER8 | 0.9199 | 0.8969 | -0.023 |  | 0.9 | 1.05 | 0.03713 | 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | INDMARIN-ER8 | 0.9199 | 0.8974 | -0.0225 |  | 0.9 | 1.05 | 0.11188 | POI 640510_8 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | INDMARIN-ER8 | 0.9199 | 0.8974 | -0.0225 |  | 0.9 | 1.05 | 0.09831 | POI 640510_8 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | INDMARIN-ER8 | 0.9199 | 0.8974 | -0.0225 |  | 0.9 | 1.05 | 0.1114 | POI 640510_8 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | INDMARIN-ER8 | 0.9199 | 0.8974 | -0.0225 |  | 0.9 | 1.05 | 0.18217 | POI 640510_8 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | INDMARIN-ER8 | 0.9199 | 0.8974 | -0.0225 |  | 0.9 | 1.05 | 0.14157 | POI 640510_8 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | INDMARIN-ER8 | 0.9199 | 0.8974 | -0.0225 |  | 0.9 | 1.05 | 0.1112 | POI 640510_8 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | INDMARIN-ER8 | 0.9199 | 0.8974 | -0.0225 |  | 0.9 | 1.05 | 0.11188 | POI 640510_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | INDMARIN-ER8 | 0.9199 | 0.8974 | -0.0225 |  | 0.9 | 1.05 | 0.09831 | POI 640510_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | INDMARIN-ER8 | 0.9199 | 0.8974 | -0.0225 |  | 0.9 | 1.05 | 0.1114 | POI 640510_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | INDMARIN-ER8 | 0.9199 | 0.8974 | -0.0225 |  | 0.9 | 1.05 | 0.18217 | POI 640510_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | INDMARIN-ER8 | 0.9199 | 0.8974 | -0.0225 |  | 0.9 | 1.05 | 0.14157 | POI 640510_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | INDMARIN-ER8 | 0.9199 | 0.8974 | -0.0225 |  | 0.9 | 1.05 | 0.1112 | POI 640510_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | INDMARIN-ER8 | 0.9199 | 0.8974 | -0.0225 |  | 0.9 | 1.05 | 0.11188 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | INDMARIN-ER8 | 0.9199 | 0.8974 | -0.0225 |  | 0.9 | 1.05 | 0.09831 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | INDMARIN-ER8 | 0.9199 | 0.8974 | -0.0225 |  | 0.9 | 1.05 | 0.1114 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | INDMARIN-ER8 | 0.9199 | 0.8974 | -0.0225 |  | 0.9 | 1.05 | 0.18217 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | INDMARIN-ER8 | 0.9199 | 0.8974 | -0.0225 |  | 0.9 | 1.05 | 0.14157 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | INDMARIN-ER8 | 0.9199 | 0.8974 | -0.0225 |  | 0.9 | 1.05 | 0.1112 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | INDMARIN-ER8 | 0.9199 | 0.8975 | -0.0224 |  | 0.9 | 1.05 | 0.11188 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | INDMARIN-ER8 | 0.9199 | 0.8975 | -0.0224 |  | 0.9 | 1.05 | 0.09831 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | INDMARIN-ER8 | 0.9199 | 0.8975 | -0.0224 |  | 0.9 | 1.05 | 0.1114 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | INDMARIN-ER8 | 0.9199 | 0.8975 | -0.0224 |  | 0.9 | 1.05 | 0.18217 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | INDMARIN-ER8 | 0.9199 | 0.8975 | -0.0224 |  | 0.9 | 1.05 | 0.14157 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | INDMARIN-ER8 | 0.9199 | 0.8975 | -0.0224 |  | 0.9 | 1.05 | 0.1112 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | INDMARIN-ER8 | 0.9199 | 0.899 | -0.0209 |  | 0.9 | 1.05 | 0.03452 | 659133 SIDNEY__-MB3 345 659135 STEGALL_-MB3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | INDMARIN-ER8 | 0.9199 | 0.8996 | -0.0203 |  | 0.9 | 1.05 | 0.04698 | 155360 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | INDMARIN-ER8 | 0.9199 | 0.8996 | -0.0203 |  | 0.9 | 1.05 | 0.0312 | 155360 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | LYONS-ER8 | 0.907 | 0.8633 | -0.0437 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | LYONS-ER8 | 0.907 | 0.8633 | -0.0437 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | LYONS-ER8 | 0.907 | 0.8633 | -0.0437 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | LYONS-ER8 | 0.907 | 0.8633 | -0.0437 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | LYONS-ER8 | 0.907 | 0.8633 | -0.0437 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | LYONS-ER8 | 0.907 | 0.8633 | -0.0437 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | LYONS-ER8 | 0.9069 | 0.8635 | -0.0434 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | LYONS-ER8 | 0.9069 | 0.8635 | -0.0434 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | LYONS-ER8 | 0.9069 | 0.8635 | -0.0434 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | LYONS-ER8 | 0.9069 | 0.8635 | -0.0434 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | LYONS-ER8 | 0.9069 | 0.8635 | -0.0434 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | LYONS-ER8 | 0.9069 | 0.8635 | -0.0434 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | LYONS-ER8 | 0.9084 | 0.8666 | -0.0418 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | LYONS-ER8 | 0.9084 | 0.8666 | -0.0418 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | LYONS-ER8 | 0.9084 | 0.8666 | -0.0418 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | LYONS-ER8 | 0.9084 | 0.8666 | -0.0418 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | LYONS-ER8 | 0.9084 | 0.8666 | -0.0418 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | LYONS-ER8 | 0.9084 | 0.8666 | -0.0418 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | LYONS-ER8 | 0.9084 | 0.8671 | -0.0413 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | LYONS-ER8 | 0.9084 | 0.8671 | -0.0413 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | LYONS-ER8 | 0.9084 | 0.8671 | -0.0413 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | LYONS-ER8 | 0.9084 | 0.8671 | -0.0413 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | LYONS-ER8 | 0.9084 | 0.8671 | -0.0413 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | LYONS-ER8 | 0.9084 | 0.8671 | -0.0413 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | LYONS-ER8 | 0.9086 | 0.8678 | -0.0408 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | LYONS-ER8 | 0.9086 | 0.8678 | -0.0408 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | LYONS-ER8 | 0.9086 | 0.8678 | -0.0408 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | LYONS-ER8 | 0.9086 | 0.8678 | -0.0408 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | LYONS-ER8 | 0.9086 | 0.8678 | -0.0408 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | LYONS-ER8 | 0.9086 | 0.8678 | -0.0408 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MARION-ER8 | 0.8757 | 0.8293 | -0.0464 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MARION-ER8 | 0.8757 | 0.8293 | -0.0464 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MARION-ER8 | 0.8757 | 0.8293 | -0.0464 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MARION-ER8 | 0.8757 | 0.8293 | -0.0464 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MARION-ER8 | 0.8757 | 0.8293 | -0.0464 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MARION-ER8 | 0.8757 | 0.8293 | -0.0464 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MARION-ER8 | 0.8755 | 0.8295 | -0.046 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MARION-ER8 | 0.8755 | 0.8295 | -0.046 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MARION-ER8 | 0.8755 | 0.8295 | -0.046 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MARION-ER8 | 0.8755 | 0.8295 | -0.046 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MARION-ER8 | 0.8755 | 0.8295 | -0.046 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MARION-ER8 | 0.8755 | 0.8295 | -0.046 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | LYONS-ER8 | 0.9093 | 0.8687 | -0.0406 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | LYONS-ER8 | 0.9093 | 0.8687 | -0.0406 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | LYONS-ER8 | 0.9093 | 0.8687 | -0.0406 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | LYONS-ER8 | 0.9093 | 0.8687 | -0.0406 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | LYONS-ER8 | 0.9093 | 0.8687 | -0.0406 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | LYONS-ER8 | 0.9093 | 0.8687 | -0.0406 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | LYONS-ER8 | 0.91 | 0.8699 | -0.0401 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | LYONS-ER8 | 0.91 | 0.8699 | -0.0401 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | LYONS-ER8 | 0.91 | 0.8699 | -0.0401 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | LYONS-ER8 | 0.91 | 0.8699 | -0.0401 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | LYONS-ER8 | 0.91 | 0.8699 | -0.0401 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | LYONS-ER8 | 0.91 | 0.8699 | -0.0401 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | LYONS-ER8 | 0.9103 | 0.8702 | -0.0401 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | LYONS-ER8 | 0.9103 | 0.8702 | -0.0401 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | LYONS-ER8 | 0.9103 | 0.8702 | -0.0401 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | LYONS-ER8 | 0.9103 | 0.8702 | -0.0401 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | LYONS-ER8 | 0.9103 | 0.8702 | -0.0401 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | LYONS-ER8 | 0.9103 | 0.8702 | -0.0401 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | LYONS-ER8 | 0.9112 | 0.872 | -0.0392 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | LYONS-ER8 | 0.9112 | 0.872 | -0.0392 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | LYONS-ER8 | 0.9112 | 0.872 | -0.0392 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | LYONS-ER8 | 0.9112 | 0.872 | -0.0392 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | LYONS-ER8 | 0.9112 | 0.872 | -0.0392 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | LYONS-ER8 | 0.9112 | 0.872 | -0.0392 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | LYONS-ER8 | 0.9115 | 0.8726 | -0.0389 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | LYONS-ER8 | 0.9115 | 0.8726 | -0.0389 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | LYONS-ER8 | 0.9115 | 0.8726 | -0.0389 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | LYONS-ER8 | 0.9115 | 0.8726 | -0.0389 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | LYONS-ER8 | 0.9115 | 0.8726 | -0.0389 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | LYONS-ER8 | 0.9115 | 0.8726 | -0.0389 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MARION-ER8 | 0.8773 | 0.834 | -0.0433 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MARION-ER8 | 0.8773 | 0.834 | -0.0433 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MARION-ER8 | 0.8773 | 0.834 | -0.0433 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MARION-ER8 | 0.8773 | 0.834 | -0.0433 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MARION-ER8 | 0.8773 | 0.834 | -0.0433 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MARION-ER8 | 0.8773 | 0.834 | -0.0433 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MARION-ER8 | 0.8781 | 0.835 | -0.0431 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MARION-ER8 | 0.8781 | 0.835 | -0.0431 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MARION-ER8 | 0.8781 | 0.835 | -0.0431 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MARION-ER8 | 0.8781 | 0.835 | -0.0431 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MARION-ER8 | 0.8781 | 0.835 | -0.0431 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MARION-ER8 | 0.8781 | 0.835 | -0.0431 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MARION-ER8 | 0.8798 | 0.8357 | -0.0441 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MARION-ER8 | 0.8798 | 0.8357 | -0.0441 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MARION-ER8 | 0.8798 | 0.8357 | -0.0441 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MARION-ER8 | 0.8798 | 0.8357 | -0.0441 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MARION-ER8 | 0.8798 | 0.8357 | -0.0441 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MARION-ER8 | 0.8798 | 0.8357 | -0.0441 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MARION-ER8 | 0.8798 | 0.8362 | -0.0436 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MARION-ER8 | 0.8798 | 0.8362 | -0.0436 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MARION-ER8 | 0.8798 | 0.8362 | -0.0436 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MARION-ER8 | 0.8798 | 0.8362 | -0.0436 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MARION-ER8 | 0.8798 | 0.8362 | -0.0436 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MARION-ER8 | 0.8798 | 0.8362 | -0.0436 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MARION-ER8 | 0.8788 | 0.8363 | -0.0425 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MARION-ER8 | 0.8788 | 0.8363 | -0.0425 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MARION-ER8 | 0.8788 | 0.8363 | -0.0425 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MARION-ER8 | 0.8788 | 0.8363 | -0.0425 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MARION-ER8 | 0.8788 | 0.8363 | -0.0425 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MARION-ER8 | 0.8788 | 0.8363 | -0.0425 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MARION-ER8 | 0.8818 | 0.8395 | -0.0423 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MARION-ER8 | 0.8818 | 0.8395 | -0.0423 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MARION-ER8 | 0.8818 | 0.8395 | -0.0423 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MARION-ER8 | 0.8818 | 0.8395 | -0.0423 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MARION-ER8 | 0.8818 | 0.8395 | -0.0423 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MARION-ER8 | 0.8818 | 0.8395 | -0.0423 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MARION-ER8 | 0.8828 | 0.8414 | -0.0414 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MARION-ER8 | 0.8828 | 0.8414 | -0.0414 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MARION-ER8 | 0.8828 | 0.8414 | -0.0414 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MARION-ER8 | 0.8828 | 0.8414 | -0.0414 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MARION-ER8 | 0.8828 | 0.8414 | -0.0414 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MARION-ER8 | 0.8828 | 0.8414 | -0.0414 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MARION-ER8 | 0.8831 | 0.842 | -0.0411 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MARION-ER8 | 0.8831 | 0.842 | -0.0411 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MARION-ER8 | 0.8831 | 0.842 | -0.0411 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MARION-ER8 | 0.8831 | 0.842 | -0.0411 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MARION-ER8 | 0.8831 | 0.842 | -0.0411 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MARION-ER8 | 0.8831 | 0.842 | -0.0411 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MARION-ER8 | 0.9037 | 0.873 | -0.0307 |  | 0.9 | 1.05 | 0.10642 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MARION-ER8 | 0.9037 | 0.873 | -0.0307 |  | 0.9 | 1.05 | 0.24279 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MARION-ER8 | 0.9037 | 0.873 | -0.0307 |  | 0.9 | 1.05 | 0.09958 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MARION-ER8 | 0.9037 | 0.873 | -0.0307 |  | 0.9 | 1.05 | 0.03529 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MARION-ER8 | 0.9037 | 0.873 | -0.0307 |  | 0.9 | 1.05 | 0.0709 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MARION-ER8 | 0.9037 | 0.873 | -0.0307 |  | 0.9 | 1.05 | 0.14646 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MARION-ER8 | 0.9037 | 0.8731 | -0.0306 |  | 0.9 | 1.05 | 0.10642 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MARION-ER8 | 0.9037 | 0.8731 | -0.0306 |  | 0.9 | 1.05 | 0.24279 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MARION-ER8 | 0.9037 | 0.8731 | -0.0306 |  | 0.9 | 1.05 | 0.09958 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MARION-ER8 | 0.9037 | 0.8731 | -0.0306 |  | 0.9 | 1.05 | 0.03529 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MARION-ER8 | 0.9037 | 0.8731 | -0.0306 |  | 0.9 | 1.05 | 0.0709 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MARION-ER8 | 0.9037 | 0.8731 | -0.0306 |  | 0.9 | 1.05 | 0.14646 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-CLTN-ER8 | 0.9072 | 0.8635 | -0.0437 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-CLTN-ER8 | 0.9072 | 0.8635 | -0.0437 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-CLTN-ER8 | 0.9072 | 0.8635 | -0.0437 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-CLTN-ER8 | 0.9072 | 0.8635 | -0.0437 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-CLTN-ER8 | 0.9072 | 0.8635 | -0.0437 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-CLTN-ER8 | 0.9072 | 0.8635 | -0.0437 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MARION-ER8 | 0.9037 | 0.8731 | -0.0306 |  | 0.9 | 1.05 | 0.10642 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MARION-ER8 | 0.9037 | 0.8731 | -0.0306 |  | 0.9 | 1.05 | 0.24279 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MARION-ER8 | 0.9037 | 0.8731 | -0.0306 |  | 0.9 | 1.05 | 0.09958 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MARION-ER8 | 0.9037 | 0.8731 | -0.0306 |  | 0.9 | 1.05 | 0.03529 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MARION-ER8 | 0.9037 | 0.8731 | -0.0306 |  | 0.9 | 1.05 | 0.0709 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MARION-ER8 | 0.9037 | 0.8731 | -0.0306 |  | 0.9 | 1.05 | 0.14646 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-CLTN-ER8 | 0.907 | 0.8637 | -0.0433 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-CLTN-ER8 | 0.907 | 0.8637 | -0.0433 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-CLTN-ER8 | 0.907 | 0.8637 | -0.0433 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-CLTN-ER8 | 0.907 | 0.8637 | -0.0433 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-CLTN-ER8 | 0.907 | 0.8637 | -0.0433 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-CLTN-ER8 | 0.907 | 0.8637 | -0.0433 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-CLTN-ER8 | 0.9086 | 0.8668 | -0.0418 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-CLTN-ER8 | 0.9086 | 0.8668 | -0.0418 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-CLTN-ER8 | 0.9086 | 0.8668 | -0.0418 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-CLTN-ER8 | 0.9086 | 0.8668 | -0.0418 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-CLTN-ER8 | 0.9086 | 0.8668 | -0.0418 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-CLTN-ER8 | 0.9086 | 0.8668 | -0.0418 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-CLTN-ER8 | 0.9086 | 0.8673 | -0.0413 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-CLTN-ER8 | 0.9086 | 0.8673 | -0.0413 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-CLTN-ER8 | 0.9086 | 0.8673 | -0.0413 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-CLTN-ER8 | 0.9086 | 0.8673 | -0.0413 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-CLTN-ER8 | 0.9086 | 0.8673 | -0.0413 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-CLTN-ER8 | 0.9086 | 0.8673 | -0.0413 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-CLTN-ER8 | 0.9088 | 0.868 | -0.0408 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-CLTN-ER8 | 0.9088 | 0.868 | -0.0408 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-CLTN-ER8 | 0.9088 | 0.868 | -0.0408 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-CLTN-ER8 | 0.9088 | 0.868 | -0.0408 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-CLTN-ER8 | 0.9088 | 0.868 | -0.0408 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-CLTN-ER8 | 0.9088 | 0.868 | -0.0408 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MARION-ER8 | 0.9064 | 0.8776 | -0.0288 |  | 0.9 | 1.05 | 0.10623 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MARION-ER8 | 0.9064 | 0.8776 | -0.0288 |  | 0.9 | 1.05 | 0.24261 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MARION-ER8 | 0.9064 | 0.8776 | -0.0288 |  | 0.9 | 1.05 | 0.1005 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MARION-ER8 | 0.9064 | 0.8776 | -0.0288 |  | 0.9 | 1.05 | 0.03506 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MARION-ER8 | 0.9064 | 0.8776 | -0.0288 |  | 0.9 | 1.05 | 0.07067 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MARION-ER8 | 0.9064 | 0.8776 | -0.0288 |  | 0.9 | 1.05 | 0.14607 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-CLTN-ER8 | 0.9095 | 0.8689 | -0.0406 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-CLTN-ER8 | 0.9095 | 0.8689 | -0.0406 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-CLTN-ER8 | 0.9095 | 0.8689 | -0.0406 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-CLTN-ER8 | 0.9095 | 0.8689 | -0.0406 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-CLTN-ER8 | 0.9095 | 0.8689 | -0.0406 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-CLTN-ER8 | 0.9095 | 0.8689 | -0.0406 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MARION-ER8 | 0.9064 | 0.8776 | -0.0288 |  | 0.9 | 1.05 | 0.10623 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MARION-ER8 | 0.9064 | 0.8776 | -0.0288 |  | 0.9 | 1.05 | 0.24261 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MARION-ER8 | 0.9064 | 0.8776 | -0.0288 |  | 0.9 | 1.05 | 0.1005 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MARION-ER8 | 0.9064 | 0.8776 | -0.0288 |  | 0.9 | 1.05 | 0.03506 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MARION-ER8 | 0.9064 | 0.8776 | -0.0288 |  | 0.9 | 1.05 | 0.07067 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MARION-ER8 | 0.9064 | 0.8776 | -0.0288 |  | 0.9 | 1.05 | 0.14607 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-CLTN-ER8 | 0.9102 | 0.8701 | -0.0401 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-CLTN-ER8 | 0.9102 | 0.8701 | -0.0401 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-CLTN-ER8 | 0.9102 | 0.8701 | -0.0401 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-CLTN-ER8 | 0.9102 | 0.8701 | -0.0401 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-CLTN-ER8 | 0.9102 | 0.8701 | -0.0401 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-CLTN-ER8 | 0.9102 | 0.8701 | -0.0401 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MARION-ER8 | 0.9064 | 0.8776 | -0.0288 |  | 0.9 | 1.05 | 0.10623 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MARION-ER8 | 0.9064 | 0.8776 | -0.0288 |  | 0.9 | 1.05 | 0.24261 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MARION-ER8 | 0.9064 | 0.8776 | -0.0288 |  | 0.9 | 1.05 | 0.1005 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MARION-ER8 | 0.9064 | 0.8776 | -0.0288 |  | 0.9 | 1.05 | 0.03506 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MARION-ER8 | 0.9064 | 0.8776 | -0.0288 |  | 0.9 | 1.05 | 0.07067 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MARION-ER8 | 0.9064 | 0.8776 | -0.0288 |  | 0.9 | 1.05 | 0.14607 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-CLTN-ER8 | 0.9105 | 0.8704 | -0.0401 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-CLTN-ER8 | 0.9105 | 0.8704 | -0.0401 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-CLTN-ER8 | 0.9105 | 0.8704 | -0.0401 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-CLTN-ER8 | 0.9105 | 0.8704 | -0.0401 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-CLTN-ER8 | 0.9105 | 0.8704 | -0.0401 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-CLTN-ER8 | 0.9105 | 0.8704 | -0.0401 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-CLTN-ER8 | 0.9114 | 0.8722 | -0.0392 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-CLTN-ER8 | 0.9114 | 0.8722 | -0.0392 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-CLTN-ER8 | 0.9114 | 0.8722 | -0.0392 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-CLTN-ER8 | 0.9114 | 0.8722 | -0.0392 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-CLTN-ER8 | 0.9114 | 0.8722 | -0.0392 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-CLTN-ER8 | 0.9114 | 0.8722 | -0.0392 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-CLTN-ER8 | 0.9117 | 0.8728 | -0.0389 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-CLTN-ER8 | 0.9117 | 0.8728 | -0.0389 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-CLTN-ER8 | 0.9117 | 0.8728 | -0.0389 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-CLTN-ER8 | 0.9117 | 0.8728 | -0.0389 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-CLTN-ER8 | 0.9117 | 0.8728 | -0.0389 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-CLTN-ER8 | 0.9117 | 0.8728 | -0.0389 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-HLTP-ER8 | 0.9283 | 0.8768 | -0.0515 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-HLTP-ER8 | 0.9283 | 0.8768 | -0.0515 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-HLTP-ER8 | 0.9283 | 0.8768 | -0.0515 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-HLTP-ER8 | 0.9283 | 0.8768 | -0.0515 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-HLTP-ER8 | 0.9283 | 0.8768 | -0.0515 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-HLTP-ER8 | 0.9283 | 0.8768 | -0.0515 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-HLTP-ER8 | 0.928 | 0.877 | -0.051 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-HLTP-ER8 | 0.928 | 0.877 | -0.051 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-HLTP-ER8 | 0.928 | 0.877 | -0.051 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-HLTP-ER8 | 0.928 | 0.877 | -0.051 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-HLTP-ER8 | 0.928 | 0.877 | -0.051 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-HLTP-ER8 | 0.928 | 0.877 | -0.051 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-HLTP-ER8 | 0.9298 | 0.8825 | -0.0473 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-HLTP-ER8 | 0.9298 | 0.8825 | -0.0473 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-HLTP-ER8 | 0.9298 | 0.8825 | -0.0473 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-HLTP-ER8 | 0.9298 | 0.8825 | -0.0473 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-HLTP-ER8 | 0.9298 | 0.8825 | -0.0473 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-HLTP-ER8 | 0.9298 | 0.8825 | -0.0473 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-HLTP-ER8 | 0.9298 | 0.8831 | -0.0467 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-HLTP-ER8 | 0.9298 | 0.8831 | -0.0467 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-HLTP-ER8 | 0.9298 | 0.8831 | -0.0467 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-HLTP-ER8 | 0.9298 | 0.8831 | -0.0467 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-HLTP-ER8 | 0.9298 | 0.8831 | -0.0467 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-HLTP-ER8 | 0.9298 | 0.8831 | -0.0467 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-HLTP-ER8 | 0.931 | 0.8854 | -0.0456 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-HLTP-ER8 | 0.931 | 0.8854 | -0.0456 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-HLTP-ER8 | 0.931 | 0.8854 | -0.0456 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-HLTP-ER8 | 0.931 | 0.8854 | -0.0456 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-HLTP-ER8 | 0.931 | 0.8854 | -0.0456 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-HLTP-ER8 | 0.931 | 0.8854 | -0.0456 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-HLTP-ER8 | 0.9326 | 0.8874 | -0.0452 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-HLTP-ER8 | 0.9326 | 0.8874 | -0.0452 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-HLTP-ER8 | 0.9326 | 0.8874 | -0.0452 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-HLTP-ER8 | 0.9326 | 0.8874 | -0.0452 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-HLTP-ER8 | 0.9326 | 0.8874 | -0.0452 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-HLTP-ER8 | 0.9326 | 0.8874 | -0.0452 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-HLTP-ER8 | 0.9334 | 0.8887 | -0.0447 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-HLTP-ER8 | 0.9334 | 0.8887 | -0.0447 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-HLTP-ER8 | 0.9334 | 0.8887 | -0.0447 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-HLTP-ER8 | 0.9334 | 0.8887 | -0.0447 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-HLTP-ER8 | 0.9334 | 0.8887 | -0.0447 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-HLTP-ER8 | 0.9334 | 0.8887 | -0.0447 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-HLTP-ER8 | 0.9329 | 0.8887 | -0.0442 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-HLTP-ER8 | 0.9329 | 0.8887 | -0.0442 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-HLTP-ER8 | 0.9329 | 0.8887 | -0.0442 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-HLTP-ER8 | 0.9329 | 0.8887 | -0.0442 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-HLTP-ER8 | 0.9329 | 0.8887 | -0.0442 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-HLTP-ER8 | 0.9329 | 0.8887 | -0.0442 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-HLTP-ER8 | 0.9347 | 0.8914 | -0.0433 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-HLTP-ER8 | 0.9347 | 0.8914 | -0.0433 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-HLTP-ER8 | 0.9347 | 0.8914 | -0.0433 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-HLTP-ER8 | 0.9347 | 0.8914 | -0.0433 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-HLTP-ER8 | 0.9347 | 0.8914 | -0.0433 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-HLTP-ER8 | 0.9347 | 0.8914 | -0.0433 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-HLTP-ER8 | 0.935 | 0.8919 | -0.0431 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-HLTP-ER8 | 0.935 | 0.8919 | -0.0431 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-HLTP-ER8 | 0.935 | 0.8919 | -0.0431 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-HLTP-ER8 | 0.935 | 0.8919 | -0.0431 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-HLTP-ER8 | 0.935 | 0.8919 | -0.0431 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-HLTP-ER8 | 0.935 | 0.8919 | -0.0431 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-KLKP-ER8 | 0.9181 | 0.8659 | -0.0522 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-KLKP-ER8 | 0.9181 | 0.8659 | -0.0522 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-KLKP-ER8 | 0.9181 | 0.8659 | -0.0522 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-KLKP-ER8 | 0.9181 | 0.8659 | -0.0522 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-KLKP-ER8 | 0.9181 | 0.8659 | -0.0522 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-KLKP-ER8 | 0.9181 | 0.8659 | -0.0522 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-KLKP-ER8 | 0.9178 | 0.8661 | -0.0517 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-KLKP-ER8 | 0.9178 | 0.8661 | -0.0517 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-KLKP-ER8 | 0.9178 | 0.8661 | -0.0517 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-KLKP-ER8 | 0.9178 | 0.8661 | -0.0517 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-KLKP-ER8 | 0.9178 | 0.8661 | -0.0517 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-KLKP-ER8 | 0.9178 | 0.8661 | -0.0517 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-KLKP-ER8 | 0.9195 | 0.8715 | -0.048 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-KLKP-ER8 | 0.9195 | 0.8715 | -0.048 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-KLKP-ER8 | 0.9195 | 0.8715 | -0.048 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-KLKP-ER8 | 0.9195 | 0.8715 | -0.048 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-KLKP-ER8 | 0.9195 | 0.8715 | -0.048 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-KLKP-ER8 | 0.9195 | 0.8715 | -0.048 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-KLKP-ER8 | 0.9195 | 0.8721 | -0.0474 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-KLKP-ER8 | 0.9195 | 0.8721 | -0.0474 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-KLKP-ER8 | 0.9195 | 0.8721 | -0.0474 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-KLKP-ER8 | 0.9195 | 0.8721 | -0.0474 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-KLKP-ER8 | 0.9195 | 0.8721 | -0.0474 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-KLKP-ER8 | 0.9195 | 0.8721 | -0.0474 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MARION-ER8 | 0.9093 | 0.8849 | -0.0244 |  | 0.9 | 1.05 | 0.10941 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MARION-ER8 | 0.9093 | 0.8849 | -0.0244 |  | 0.9 | 1.05 | 0.05493 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MARION-ER8 | 0.9135 | 0.8892 | -0.0243 |  | 0.9 | 1.05 | 0.03069 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MARION-ER8 | 0.9135 | 0.8892 | -0.0243 |  | 0.9 | 1.05 | 0.10922 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MARION-ER8 | 0.9135 | 0.8892 | -0.0243 |  | 0.9 | 1.05 | 0.05476 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-KLKP-ER8 | 0.9209 | 0.8746 | -0.0463 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-KLKP-ER8 | 0.9209 | 0.8746 | -0.0463 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-KLKP-ER8 | 0.9209 | 0.8746 | -0.0463 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-KLKP-ER8 | 0.9209 | 0.8746 | -0.0463 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-KLKP-ER8 | 0.9209 | 0.8746 | -0.0463 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-KLKP-ER8 | 0.9209 | 0.8746 | -0.0463 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-KLKP-ER8 | 0.9225 | 0.8766 | -0.0459 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-KLKP-ER8 | 0.9225 | 0.8766 | -0.0459 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-KLKP-ER8 | 0.9225 | 0.8766 | -0.0459 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-KLKP-ER8 | 0.9225 | 0.8766 | -0.0459 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-KLKP-ER8 | 0.9225 | 0.8766 | -0.0459 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-KLKP-ER8 | 0.9225 | 0.8766 | -0.0459 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-KLKP-ER8 | 0.9226 | 0.8777 | -0.0449 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-KLKP-ER8 | 0.9226 | 0.8777 | -0.0449 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-KLKP-ER8 | 0.9226 | 0.8777 | -0.0449 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-KLKP-ER8 | 0.9226 | 0.8777 | -0.0449 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-KLKP-ER8 | 0.9226 | 0.8777 | -0.0449 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-KLKP-ER8 | 0.9226 | 0.8777 | -0.0449 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-KLKP-ER8 | 0.9233 | 0.8779 | -0.0454 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-KLKP-ER8 | 0.9233 | 0.8779 | -0.0454 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-KLKP-ER8 | 0.9233 | 0.8779 | -0.0454 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-KLKP-ER8 | 0.9233 | 0.8779 | -0.0454 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-KLKP-ER8 | 0.9233 | 0.8779 | -0.0454 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-KLKP-ER8 | 0.9233 | 0.8779 | -0.0454 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MARION-ER8 | 0.9118 | 0.8894 | -0.0224 |  | 0.9 | 1.05 | 0.05765 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MARION-ER8 | 0.9118 | 0.8894 | -0.0224 |  | 0.9 | 1.05 | 0.04499 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MARION-ER8 | 0.9118 | 0.8894 | -0.0224 |  | 0.9 | 1.05 | 0.05213 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MARION-ER8 | 0.9118 | 0.8894 | -0.0224 |  | 0.9 | 1.05 | 0.07544 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MARION-ER8 | 0.9118 | 0.8894 | -0.0224 |  | 0.9 | 1.05 | 0.07656 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MARION-ER8 | 0.9118 | 0.8894 | -0.0224 |  | 0.9 | 1.05 | 0.05236 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MARION-ER8 | 0.9124 | 0.8898 | -0.0226 |  | 0.9 | 1.05 | 0.03199 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MARION-ER8 | 0.9124 | 0.8898 | -0.0226 |  | 0.9 | 1.05 | 0.04873 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MARION-ER8 | 0.9124 | 0.8898 | -0.0226 |  | 0.9 | 1.05 | 0.09554 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MARION-ER8 | 0.9124 | 0.8898 | -0.0226 |  | 0.9 | 1.05 | 0.08589 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MARION-ER8 | 0.9124 | 0.8898 | -0.0226 |  | 0.9 | 1.05 | 0.04498 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MARION-ER8 | 0.9124 | 0.8902 | -0.0222 |  | 0.9 | 1.05 | 0.03222 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MARION-ER8 | 0.9124 | 0.8902 | -0.0222 |  | 0.9 | 1.05 | 0.04909 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MARION-ER8 | 0.9124 | 0.8902 | -0.0222 |  | 0.9 | 1.05 | 0.09624 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MARION-ER8 | 0.9124 | 0.8902 | -0.0222 |  | 0.9 | 1.05 | 0.08652 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MARION-ER8 | 0.9124 | 0.8902 | -0.0222 |  | 0.9 | 1.05 | 0.04531 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-KLKP-ER8 | 0.9245 | 0.8805 | -0.044 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-KLKP-ER8 | 0.9245 | 0.8805 | -0.044 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-KLKP-ER8 | 0.9245 | 0.8805 | -0.044 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-KLKP-ER8 | 0.9245 | 0.8805 | -0.044 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-KLKP-ER8 | 0.9245 | 0.8805 | -0.044 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-KLKP-ER8 | 0.9245 | 0.8805 | -0.044 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-KLKP-ER8 | 0.9247 | 0.881 | -0.0437 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-KLKP-ER8 | 0.9247 | 0.881 | -0.0437 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-KLKP-ER8 | 0.9247 | 0.881 | -0.0437 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-KLKP-ER8 | 0.9247 | 0.881 | -0.0437 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-KLKP-ER8 | 0.9247 | 0.881 | -0.0437 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-KLKP-ER8 | 0.9247 | 0.881 | -0.0437 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MARION-ER8 | 0.9133 | 0.8907 | -0.0226 |  | 0.9 | 1.05 | 0.03222 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MARION-ER8 | 0.9133 | 0.8907 | -0.0226 |  | 0.9 | 1.05 | 0.04909 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MARION-ER8 | 0.9133 | 0.8907 | -0.0226 |  | 0.9 | 1.05 | 0.09624 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MARION-ER8 | 0.9133 | 0.8907 | -0.0226 |  | 0.9 | 1.05 | 0.08652 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MARION-ER8 | 0.9133 | 0.8907 | -0.0226 |  | 0.9 | 1.05 | 0.04531 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MARION-ER8 | 0.9165 | 0.8948 | -0.0217 |  | 0.9 | 1.05 | 0.05737 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MARION-ER8 | 0.9165 | 0.8948 | -0.0217 |  | 0.9 | 1.05 | 0.04472 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MARION-ER8 | 0.9165 | 0.8948 | -0.0217 |  | 0.9 | 1.05 | 0.05275 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MARION-ER8 | 0.9165 | 0.8948 | -0.0217 |  | 0.9 | 1.05 | 0.07518 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MARION-ER8 | 0.9165 | 0.8948 | -0.0217 |  | 0.9 | 1.05 | 0.0763 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MARION-ER8 | 0.9165 | 0.8948 | -0.0217 |  | 0.9 | 1.05 | 0.05195 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MARION-ER8 | 0.9166 | 0.8948 | -0.0218 |  | 0.9 | 1.05 | 0.03187 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MARION-ER8 | 0.9166 | 0.8948 | -0.0218 |  | 0.9 | 1.05 | 0.04986 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MARION-ER8 | 0.9166 | 0.8948 | -0.0218 |  | 0.9 | 1.05 | 0.09536 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MARION-ER8 | 0.9166 | 0.8948 | -0.0218 |  | 0.9 | 1.05 | 0.08573 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MARION-ER8 | 0.9166 | 0.8948 | -0.0218 |  | 0.9 | 1.05 | 0.04463 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MARION-ER8 | 0.9166 | 0.8952 | -0.0214 |  | 0.9 | 1.05 | 0.03211 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MARION-ER8 | 0.9166 | 0.8952 | -0.0214 |  | 0.9 | 1.05 | 0.05023 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MARION-ER8 | 0.9166 | 0.8952 | -0.0214 |  | 0.9 | 1.05 | 0.09607 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MARION-ER8 | 0.9166 | 0.8952 | -0.0214 |  | 0.9 | 1.05 | 0.08636 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MARION-ER8 | 0.9166 | 0.8952 | -0.0214 |  | 0.9 | 1.05 | 0.04496 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MARION-ER8 | 0.9174 | 0.8957 | -0.0217 |  | 0.9 | 1.05 | 0.03211 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MARION-ER8 | 0.9174 | 0.8957 | -0.0217 |  | 0.9 | 1.05 | 0.05023 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MARION-ER8 | 0.9174 | 0.8957 | -0.0217 |  | 0.9 | 1.05 | 0.09607 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MARION-ER8 | 0.9174 | 0.8957 | -0.0217 |  | 0.9 | 1.05 | 0.08636 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MARION-ER8 | 0.9174 | 0.8957 | -0.0217 |  | 0.9 | 1.05 | 0.04496 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MARION-ER8 | 0.9209 | 0.896 | -0.0249 |  | 0.9 | 1.05 | 0.10866 | 659423 GR.LS-LO-BE3 345 762544 G23-182-TAP 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MARION-ER8 | 0.9209 | 0.896 | -0.0249 |  | 0.9 | 1.05 | 0.49551 | 659423 GR.LS-LO-BE3 345 762544 G23-182-TAP 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MARION-ER8 | 0.9209 | 0.8963 | -0.0246 |  | 0.9 | 1.05 | 0.03387 | POI 640252_0 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MARION-ER8 | 0.9182 | 0.8963 | -0.0219 |  | 0.9 | 1.05 | 0.05737 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MARION-ER8 | 0.9182 | 0.8963 | -0.0219 |  | 0.9 | 1.05 | 0.04472 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MARION-ER8 | 0.9182 | 0.8963 | -0.0219 |  | 0.9 | 1.05 | 0.05275 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MARION-ER8 | 0.9182 | 0.8963 | -0.0219 |  | 0.9 | 1.05 | 0.07518 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MARION-ER8 | 0.9182 | 0.8963 | -0.0219 |  | 0.9 | 1.05 | 0.0763 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MARION-ER8 | 0.9182 | 0.8963 | -0.0219 |  | 0.9 | 1.05 | 0.05195 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MARION-ER8 | 0.9209 | 0.8966 | -0.0243 |  | 0.9 | 1.05 | 0.07277 | 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MARION-ER8 | 0.9209 | 0.8966 | -0.0243 |  | 0.9 | 1.05 | 0.05101 | 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MARION-ER8 | 0.9209 | 0.8966 | -0.0243 |  | 0.9 | 1.05 | 0.03331 | 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MARION-ER8 | 0.9209 | 0.8966 | -0.0243 |  | 0.9 | 1.05 | 0.03727 | 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MARION-ER8 | 0.9209 | 0.8966 | -0.0243 |  | 0.9 | 1.05 | 0.04392 | 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MARION-ER8 | 0.9209 | 0.8966 | -0.0243 |  | 0.9 | 1.05 | 0.03744 | 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MARION-ER8 | 0.9209 | 0.8967 | -0.0242 |  | 0.9 | 1.05 | 0.11223 | POI 640510_8 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MARION-ER8 | 0.9209 | 0.8967 | -0.0242 |  | 0.9 | 1.05 | 0.09867 | POI 640510_8 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MARION-ER8 | 0.9209 | 0.8967 | -0.0242 |  | 0.9 | 1.05 | 0.10969 | POI 640510_8 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MARION-ER8 | 0.9209 | 0.8967 | -0.0242 |  | 0.9 | 1.05 | 0.18255 | POI 640510_8 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MARION-ER8 | 0.9209 | 0.8967 | -0.0242 |  | 0.9 | 1.05 | 0.14194 | POI 640510_8 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MARION-ER8 | 0.9209 | 0.8967 | -0.0242 |  | 0.9 | 1.05 | 0.1119 | POI 640510_8 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MARION-ER8 | 0.9209 | 0.8967 | -0.0242 |  | 0.9 | 1.05 | 0.11223 | POI 640510_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MARION-ER8 | 0.9209 | 0.8967 | -0.0242 |  | 0.9 | 1.05 | 0.09867 | POI 640510_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MARION-ER8 | 0.9209 | 0.8967 | -0.0242 |  | 0.9 | 1.05 | 0.10969 | POI 640510_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MARION-ER8 | 0.9209 | 0.8967 | -0.0242 |  | 0.9 | 1.05 | 0.18255 | POI 640510_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MARION-ER8 | 0.9209 | 0.8967 | -0.0242 |  | 0.9 | 1.05 | 0.14194 | POI 640510_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MARION-ER8 | 0.9209 | 0.8967 | -0.0242 |  | 0.9 | 1.05 | 0.1119 | POI 640510_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MARION-ER8 | 0.9209 | 0.8967 | -0.0242 |  | 0.9 | 1.05 | 0.11223 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MARION-ER8 | 0.9209 | 0.8967 | -0.0242 |  | 0.9 | 1.05 | 0.09867 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MARION-ER8 | 0.9209 | 0.8967 | -0.0242 |  | 0.9 | 1.05 | 0.10969 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MARION-ER8 | 0.9209 | 0.8967 | -0.0242 |  | 0.9 | 1.05 | 0.18255 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MARION-ER8 | 0.9209 | 0.8967 | -0.0242 |  | 0.9 | 1.05 | 0.14194 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MARION-ER8 | 0.9209 | 0.8967 | -0.0242 |  | 0.9 | 1.05 | 0.1119 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MARION-ER8 | 0.9209 | 0.8967 | -0.0242 |  | 0.9 | 1.05 | 0.11223 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MARION-ER8 | 0.9209 | 0.8967 | -0.0242 |  | 0.9 | 1.05 | 0.09867 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MARION-ER8 | 0.9209 | 0.8967 | -0.0242 |  | 0.9 | 1.05 | 0.10969 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MARION-ER8 | 0.9209 | 0.8967 | -0.0242 |  | 0.9 | 1.05 | 0.18255 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MARION-ER8 | 0.9209 | 0.8967 | -0.0242 |  | 0.9 | 1.05 | 0.14194 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MARION-ER8 | 0.9209 | 0.8967 | -0.0242 |  | 0.9 | 1.05 | 0.1119 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-LKPL-ER8 | 0.9426 | 0.8926 | -0.05 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-LKPL-ER8 | 0.9426 | 0.8926 | -0.05 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-LKPL-ER8 | 0.9426 | 0.8926 | -0.05 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-LKPL-ER8 | 0.9426 | 0.8926 | -0.05 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-LKPL-ER8 | 0.9426 | 0.8926 | -0.05 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-LKPL-ER8 | 0.9426 | 0.8926 | -0.05 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-LKPL-ER8 | 0.9423 | 0.8928 | -0.0495 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-LKPL-ER8 | 0.9423 | 0.8928 | -0.0495 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-LKPL-ER8 | 0.9423 | 0.8928 | -0.0495 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-LKPL-ER8 | 0.9423 | 0.8928 | -0.0495 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-LKPL-ER8 | 0.9423 | 0.8928 | -0.0495 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-LKPL-ER8 | 0.9423 | 0.8928 | -0.0495 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-LKPL-ER8 | 0.9444 | 0.8985 | -0.0459 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-LKPL-ER8 | 0.9444 | 0.8985 | -0.0459 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-LKPL-ER8 | 0.9444 | 0.8985 | -0.0459 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-LKPL-ER8 | 0.9444 | 0.8985 | -0.0459 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-LKPL-ER8 | 0.9444 | 0.8985 | -0.0459 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-LKPL-ER8 | 0.9444 | 0.8985 | -0.0459 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-LKPL-ER8 | 0.9444 | 0.8991 | -0.0453 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-LKPL-ER8 | 0.9444 | 0.8991 | -0.0453 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-LKPL-ER8 | 0.9444 | 0.8991 | -0.0453 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-LKPL-ER8 | 0.9444 | 0.8991 | -0.0453 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-LKPL-ER8 | 0.9444 | 0.8991 | -0.0453 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-LKPL-ER8 | 0.9444 | 0.8991 | -0.0453 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MARION-ER8 | 0.9209 | 0.8985 | -0.0224 |  | 0.9 | 1.05 | 0.03541 | 659133 SIDNEY__-MB3 345 659135 STEGALL_-MB3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MARION-ER8 | 0.9209 | 0.8985 | -0.0224 |  | 0.9 | 1.05 | 0.04707 | 155360 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MARION-ER8 | 0.9209 | 0.8985 | -0.0224 |  | 0.9 | 1.05 | 0.03131 | 155360 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MARION-ER8 | 0.9237 | 0.8995 | -0.0242 |  | 0.9 | 1.05 | 0.04049 | POI 640374_5 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MARION-ER8 | 0.9237 | 0.8995 | -0.0242 |  | 0.9 | 1.05 | 0.0359 | POI 640374_5 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MARION-ER8 | 0.9237 | 0.8995 | -0.0242 |  | 0.9 | 1.05 | 0.04491 | POI 640374_5 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MARION-ER8 | 0.9237 | 0.8995 | -0.0242 |  | 0.9 | 1.05 | 0.05666 | POI 640374_5 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MARION-ER8 | 0.9237 | 0.8995 | -0.0242 |  | 0.9 | 1.05 | 0.04963 | POI 640374_5 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MARION-ER8 | 0.9237 | 0.8995 | -0.0242 |  | 0.9 | 1.05 | 0.04174 | POI 640374_5 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MARION-ER8 | 0.9237 | 0.8997 | -0.024 |  | 0.9 | 1.05 | 0.03329 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MARION-ER8 | 0.9237 | 0.8997 | -0.024 |  | 0.9 | 1.05 | 0.03286 | POI 763443_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MARION-ER8 | 0.9237 | 0.8997 | -0.024 |  | 0.9 | 1.05 | 0.10258 | POI 763443_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MARION-ER8 | 0.9237 | 0.8997 | -0.024 |  | 0.9 | 1.05 | 0.05872 | POI 763443_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MARION-ER8 | 0.9237 | 0.8997 | -0.024 |  | 0.9 | 1.05 | 0.03286 | 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MARION-ER8 | 0.9237 | 0.8997 | -0.024 |  | 0.9 | 1.05 | 0.10258 | 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MARION-ER8 | 0.9237 | 0.8997 | -0.024 |  | 0.9 | 1.05 | 0.05872 | 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MARION-ER8 | 0.9237 | 0.8998 | -0.0239 |  | 0.9 | 1.05 | 0.10739 | 601048 LYON CO 3 345 601077 HAWKSNEST 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MARION-ER8 | 0.9237 | 0.8998 | -0.0239 |  | 0.9 | 1.05 | 0.21314 | 601048 LYON CO 3 345 601077 HAWKSNEST 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MARION-ER8 | 0.9237 | 0.8998 | -0.0239 |  | 0.9 | 1.05 | 0.04006 | 601048 LYON CO 3 345 601077 HAWKSNEST 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MARION-ER8 | 0.9237 | 0.8998 | -0.0239 |  | 0.9 | 1.05 | 0.04806 | 601048 LYON CO 3 345 601077 HAWKSNEST 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MARION-ER8 | 0.9237 | 0.8998 | -0.0239 |  | 0.9 | 1.05 | 0.06592 | 601048 LYON CO 3 345 601077 HAWKSNEST 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MARION-ER8 | 0.9237 | 0.8998 | -0.0239 |  | 0.9 | 1.05 | 0.08838 | 601048 LYON CO 3 345 601077 HAWKSNEST 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MARIONRD-ER7 | 0.9319 | 0.8961 | -0.0358 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MARIONRD-ER7 | 0.9319 | 0.8961 | -0.0358 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MARIONRD-ER7 | 0.9319 | 0.8961 | -0.0358 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MARIONRD-ER7 | 0.9319 | 0.8961 | -0.0358 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MARIONRD-ER7 | 0.9319 | 0.8961 | -0.0358 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MARIONRD-ER7 | 0.9319 | 0.8961 | -0.0358 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MARIONRD-ER7 | 0.9317 | 0.8962 | -0.0355 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MARIONRD-ER7 | 0.9317 | 0.8962 | -0.0355 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MARIONRD-ER7 | 0.9317 | 0.8962 | -0.0355 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MARIONRD-ER7 | 0.9317 | 0.8962 | -0.0355 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MARIONRD-ER7 | 0.9317 | 0.8962 | -0.0355 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MARIONRD-ER7 | 0.9317 | 0.8962 | -0.0355 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MARIONRD-ER7 | 0.9326 | 0.8983 | -0.0343 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MARIONRD-ER7 | 0.9326 | 0.8983 | -0.0343 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MARIONRD-ER7 | 0.9326 | 0.8983 | -0.0343 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MARIONRD-ER7 | 0.9326 | 0.8983 | -0.0343 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MARIONRD-ER7 | 0.9326 | 0.8983 | -0.0343 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MARIONRD-ER7 | 0.9326 | 0.8983 | -0.0343 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MARIONRD-ER7 | 0.9333 | 0.8992 | -0.0341 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MARIONRD-ER7 | 0.9333 | 0.8992 | -0.0341 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MARIONRD-ER7 | 0.9333 | 0.8992 | -0.0341 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MARIONRD-ER7 | 0.9333 | 0.8992 | -0.0341 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MARIONRD-ER7 | 0.9333 | 0.8992 | -0.0341 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MARIONRD-ER7 | 0.9333 | 0.8992 | -0.0341 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MENNO-ER8 | 0.9261 | 0.8872 | -0.0389 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MENNO-ER8 | 0.9261 | 0.8872 | -0.0389 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MENNO-ER8 | 0.9261 | 0.8872 | -0.0389 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MENNO-ER8 | 0.9261 | 0.8872 | -0.0389 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MENNO-ER8 | 0.9261 | 0.8872 | -0.0389 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MENNO-ER8 | 0.9261 | 0.8872 | -0.0389 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MENNO-ER8 | 0.9255 | 0.8875 | -0.038 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MENNO-ER8 | 0.9255 | 0.8875 | -0.038 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MENNO-ER8 | 0.9255 | 0.8875 | -0.038 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MENNO-ER8 | 0.9255 | 0.8875 | -0.038 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MENNO-ER8 | 0.9255 | 0.8875 | -0.038 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MENNO-ER8 | 0.9255 | 0.8875 | -0.038 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MENNO-ER8 | 0.926 | 0.888 | -0.038 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MENNO-ER8 | 0.926 | 0.888 | -0.038 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MENNO-ER8 | 0.926 | 0.888 | -0.038 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MENNO-ER8 | 0.926 | 0.888 | -0.038 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MENNO-ER8 | 0.926 | 0.888 | -0.038 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MENNO-ER8 | 0.926 | 0.888 | -0.038 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MENNO-ER8 | 0.9293 | 0.8895 | -0.0398 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MENNO-ER8 | 0.9293 | 0.8895 | -0.0398 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MENNO-ER8 | 0.9293 | 0.8895 | -0.0398 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MENNO-ER8 | 0.9293 | 0.8895 | -0.0398 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MENNO-ER8 | 0.9293 | 0.8895 | -0.0398 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MENNO-ER8 | 0.9293 | 0.8895 | -0.0398 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MENNO-ER8 | 0.9287 | 0.8901 | -0.0386 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MENNO-ER8 | 0.9287 | 0.8901 | -0.0386 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MENNO-ER8 | 0.9287 | 0.8901 | -0.0386 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MENNO-ER8 | 0.9287 | 0.8901 | -0.0386 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MENNO-ER8 | 0.9287 | 0.8901 | -0.0386 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MENNO-ER8 | 0.9287 | 0.8901 | -0.0386 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MENNO-ER8 | 0.9289 | 0.8906 | -0.0383 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MENNO-ER8 | 0.9289 | 0.8906 | -0.0383 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MENNO-ER8 | 0.9289 | 0.8906 | -0.0383 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MENNO-ER8 | 0.9289 | 0.8906 | -0.0383 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MENNO-ER8 | 0.9289 | 0.8906 | -0.0383 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MENNO-ER8 | 0.9289 | 0.8906 | -0.0383 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MENNO-ER8 | 0.9279 | 0.8912 | -0.0367 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MENNO-ER8 | 0.9279 | 0.8912 | -0.0367 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MENNO-ER8 | 0.9279 | 0.8912 | -0.0367 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MENNO-ER8 | 0.9279 | 0.8912 | -0.0367 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MENNO-ER8 | 0.9279 | 0.8912 | -0.0367 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MENNO-ER8 | 0.9279 | 0.8912 | -0.0367 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MENNO-ER8 | 0.9286 | 0.8926 | -0.036 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MENNO-ER8 | 0.9286 | 0.8926 | -0.036 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MENNO-ER8 | 0.9286 | 0.8926 | -0.036 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MENNO-ER8 | 0.9286 | 0.8926 | -0.036 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MENNO-ER8 | 0.9286 | 0.8926 | -0.036 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MENNO-ER8 | 0.9286 | 0.8926 | -0.036 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MENNO-ER8 | 0.9304 | 0.893 | -0.0374 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MENNO-ER8 | 0.9304 | 0.893 | -0.0374 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MENNO-ER8 | 0.9304 | 0.893 | -0.0374 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MENNO-ER8 | 0.9304 | 0.893 | -0.0374 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MENNO-ER8 | 0.9304 | 0.893 | -0.0374 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MENNO-ER8 | 0.9304 | 0.893 | -0.0374 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MENNO-ER8 | 0.9322 | 0.8951 | -0.0371 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MENNO-ER8 | 0.9322 | 0.8951 | -0.0371 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MENNO-ER8 | 0.9322 | 0.8951 | -0.0371 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MENNO-ER8 | 0.9322 | 0.8951 | -0.0371 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MENNO-ER8 | 0.9322 | 0.8951 | -0.0371 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MENNO-ER8 | 0.9322 | 0.8951 | -0.0371 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MITCHELL-ER8 | 0.9309 | 0.8849 | -0.046 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MITCHELL-ER8 | 0.9309 | 0.8849 | -0.046 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MITCHELL-ER8 | 0.9309 | 0.8849 | -0.046 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MITCHELL-ER8 | 0.9309 | 0.8849 | -0.046 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MITCHELL-ER8 | 0.9309 | 0.8849 | -0.046 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MITCHELL-ER8 | 0.9309 | 0.8849 | -0.046 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MITCHELL-ER8 | 0.9305 | 0.8851 | -0.0454 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MITCHELL-ER8 | 0.9305 | 0.8851 | -0.0454 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MITCHELL-ER8 | 0.9305 | 0.8851 | -0.0454 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MITCHELL-ER8 | 0.9305 | 0.8851 | -0.0454 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MITCHELL-ER8 | 0.9305 | 0.8851 | -0.0454 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MITCHELL-ER8 | 0.9305 | 0.8851 | -0.0454 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MITCHELL-ER8 | 0.9319 | 0.8871 | -0.0448 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MITCHELL-ER8 | 0.9319 | 0.8871 | -0.0448 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MITCHELL-ER8 | 0.9319 | 0.8871 | -0.0448 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MITCHELL-ER8 | 0.9319 | 0.8871 | -0.0448 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MITCHELL-ER8 | 0.9319 | 0.8871 | -0.0448 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MITCHELL-ER8 | 0.9319 | 0.8871 | -0.0448 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MITCHELL-ER8 | 0.9318 | 0.89 | -0.0418 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MITCHELL-ER8 | 0.9318 | 0.89 | -0.0418 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MITCHELL-ER8 | 0.9318 | 0.89 | -0.0418 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MITCHELL-ER8 | 0.9318 | 0.89 | -0.0418 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MITCHELL-ER8 | 0.9318 | 0.89 | -0.0418 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MITCHELL-ER8 | 0.9318 | 0.89 | -0.0418 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MITCHELL-ER8 | 0.9338 | 0.8906 | -0.0432 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MITCHELL-ER8 | 0.9338 | 0.8906 | -0.0432 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MITCHELL-ER8 | 0.9338 | 0.8906 | -0.0432 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MITCHELL-ER8 | 0.9338 | 0.8906 | -0.0432 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MITCHELL-ER8 | 0.9338 | 0.8906 | -0.0432 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MITCHELL-ER8 | 0.9338 | 0.8906 | -0.0432 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MITCHELL-ER8 | 0.9324 | 0.891 | -0.0414 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MITCHELL-ER8 | 0.9324 | 0.891 | -0.0414 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MITCHELL-ER8 | 0.9324 | 0.891 | -0.0414 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MITCHELL-ER8 | 0.9324 | 0.891 | -0.0414 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MITCHELL-ER8 | 0.9324 | 0.891 | -0.0414 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MITCHELL-ER8 | 0.9324 | 0.891 | -0.0414 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MITCHELL-ER8 | 0.9339 | 0.8914 | -0.0425 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MITCHELL-ER8 | 0.9339 | 0.8914 | -0.0425 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MITCHELL-ER8 | 0.9339 | 0.8914 | -0.0425 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MITCHELL-ER8 | 0.9339 | 0.8914 | -0.0425 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MITCHELL-ER8 | 0.9339 | 0.8914 | -0.0425 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MITCHELL-ER8 | 0.9339 | 0.8914 | -0.0425 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MITCHELL-ER8 | 0.9348 | 0.8942 | -0.0406 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MITCHELL-ER8 | 0.9348 | 0.8942 | -0.0406 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MITCHELL-ER8 | 0.9348 | 0.8942 | -0.0406 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MITCHELL-ER8 | 0.9348 | 0.8942 | -0.0406 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MITCHELL-ER8 | 0.9348 | 0.8942 | -0.0406 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MITCHELL-ER8 | 0.9348 | 0.8942 | -0.0406 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MITCHELL-ER8 | 0.9363 | 0.8964 | -0.0399 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MITCHELL-ER8 | 0.9363 | 0.8964 | -0.0399 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MITCHELL-ER8 | 0.9363 | 0.8964 | -0.0399 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MITCHELL-ER8 | 0.9363 | 0.8964 | -0.0399 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MITCHELL-ER8 | 0.9363 | 0.8964 | -0.0399 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MITCHELL-ER8 | 0.9363 | 0.8964 | -0.0399 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MITCHELL-ER8 | 0.9367 | 0.8969 | -0.0398 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MITCHELL-ER8 | 0.9367 | 0.8969 | -0.0398 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MITCHELL-ER8 | 0.9367 | 0.8969 | -0.0398 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MITCHELL-ER8 | 0.9367 | 0.8969 | -0.0398 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MITCHELL-ER8 | 0.9367 | 0.8969 | -0.0398 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MITCHELL-ER8 | 0.9367 | 0.8969 | -0.0398 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MONTROSE-ER8 | 0.9107 | 0.8669 | -0.0438 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MONTROSE-ER8 | 0.9107 | 0.8669 | -0.0438 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MONTROSE-ER8 | 0.9107 | 0.8669 | -0.0438 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MONTROSE-ER8 | 0.9107 | 0.8669 | -0.0438 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MONTROSE-ER8 | 0.9107 | 0.8669 | -0.0438 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MONTROSE-ER8 | 0.9107 | 0.8669 | -0.0438 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MONTROSE-ER8 | 0.9105 | 0.867 | -0.0435 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MONTROSE-ER8 | 0.9105 | 0.867 | -0.0435 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MONTROSE-ER8 | 0.9105 | 0.867 | -0.0435 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MONTROSE-ER8 | 0.9105 | 0.867 | -0.0435 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MONTROSE-ER8 | 0.9105 | 0.867 | -0.0435 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MONTROSE-ER8 | 0.9105 | 0.867 | -0.0435 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MONTROSE-ER8 | 0.9122 | 0.8713 | -0.0409 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MONTROSE-ER8 | 0.9122 | 0.8713 | -0.0409 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MONTROSE-ER8 | 0.9122 | 0.8713 | -0.0409 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MONTROSE-ER8 | 0.9122 | 0.8713 | -0.0409 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MONTROSE-ER8 | 0.9122 | 0.8713 | -0.0409 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MONTROSE-ER8 | 0.9122 | 0.8713 | -0.0409 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MONTROSE-ER8 | 0.9135 | 0.8717 | -0.0418 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MONTROSE-ER8 | 0.9135 | 0.8717 | -0.0418 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MONTROSE-ER8 | 0.9135 | 0.8717 | -0.0418 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MONTROSE-ER8 | 0.9135 | 0.8717 | -0.0418 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MONTROSE-ER8 | 0.9135 | 0.8717 | -0.0418 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MONTROSE-ER8 | 0.9135 | 0.8717 | -0.0418 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MONTROSE-ER8 | 0.913 | 0.8722 | -0.0408 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MONTROSE-ER8 | 0.913 | 0.8722 | -0.0408 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MONTROSE-ER8 | 0.913 | 0.8722 | -0.0408 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MONTROSE-ER8 | 0.913 | 0.8722 | -0.0408 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MONTROSE-ER8 | 0.913 | 0.8722 | -0.0408 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MONTROSE-ER8 | 0.913 | 0.8722 | -0.0408 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MONTROSE-ER8 | 0.9134 | 0.8722 | -0.0412 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MONTROSE-ER8 | 0.9134 | 0.8722 | -0.0412 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MONTROSE-ER8 | 0.9134 | 0.8722 | -0.0412 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MONTROSE-ER8 | 0.9134 | 0.8722 | -0.0412 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MONTROSE-ER8 | 0.9134 | 0.8722 | -0.0412 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MONTROSE-ER8 | 0.9134 | 0.8722 | -0.0412 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MONTROSE-ER8 | 0.9136 | 0.8735 | -0.0401 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MONTROSE-ER8 | 0.9136 | 0.8735 | -0.0401 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MONTROSE-ER8 | 0.9136 | 0.8735 | -0.0401 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MONTROSE-ER8 | 0.9136 | 0.8735 | -0.0401 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MONTROSE-ER8 | 0.9136 | 0.8735 | -0.0401 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MONTROSE-ER8 | 0.9136 | 0.8735 | -0.0401 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MONTROSE-ER8 | 0.9154 | 0.8753 | -0.0401 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MONTROSE-ER8 | 0.9154 | 0.8753 | -0.0401 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MONTROSE-ER8 | 0.9154 | 0.8753 | -0.0401 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MONTROSE-ER8 | 0.9154 | 0.8753 | -0.0401 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MONTROSE-ER8 | 0.9154 | 0.8753 | -0.0401 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MONTROSE-ER8 | 0.9154 | 0.8753 | -0.0401 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MONTROSE-ER8 | 0.9163 | 0.8771 | -0.0392 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MONTROSE-ER8 | 0.9163 | 0.8771 | -0.0392 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MONTROSE-ER8 | 0.9163 | 0.8771 | -0.0392 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MONTROSE-ER8 | 0.9163 | 0.8771 | -0.0392 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MONTROSE-ER8 | 0.9163 | 0.8771 | -0.0392 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MONTROSE-ER8 | 0.9163 | 0.8771 | -0.0392 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MONTROSE-ER8 | 0.9166 | 0.8777 | -0.0389 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MONTROSE-ER8 | 0.9166 | 0.8777 | -0.0389 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MONTROSE-ER8 | 0.9166 | 0.8777 | -0.0389 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MONTROSE-ER8 | 0.9166 | 0.8777 | -0.0389 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MONTROSE-ER8 | 0.9166 | 0.8777 | -0.0389 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MONTROSE-ER8 | 0.9166 | 0.8777 | -0.0389 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-ELIS-ER7 | 0.9344 | 0.8987 | -0.0357 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-ELIS-ER7 | 0.9344 | 0.8987 | -0.0357 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-ELIS-ER7 | 0.9344 | 0.8987 | -0.0357 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-ELIS-ER7 | 0.9344 | 0.8987 | -0.0357 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-ELIS-ER7 | 0.9344 | 0.8987 | -0.0357 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-ELIS-ER7 | 0.9344 | 0.8987 | -0.0357 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-ELIS-ER7 | 0.9342 | 0.8989 | -0.0353 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-ELIS-ER7 | 0.9342 | 0.8989 | -0.0353 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-ELIS-ER7 | 0.9342 | 0.8989 | -0.0353 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-ELIS-ER7 | 0.9342 | 0.8989 | -0.0353 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-ELIS-ER7 | 0.9342 | 0.8989 | -0.0353 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-ELIS-ER7 | 0.9342 | 0.8989 | -0.0353 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-HMPA-ER8 | 0.9288 | 0.8931 | -0.0357 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-HMPA-ER8 | 0.9288 | 0.8931 | -0.0357 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-HMPA-ER8 | 0.9288 | 0.8931 | -0.0357 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-HMPA-ER8 | 0.9288 | 0.8931 | -0.0357 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-HMPA-ER8 | 0.9288 | 0.8931 | -0.0357 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-HMPA-ER8 | 0.9288 | 0.8931 | -0.0357 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-HMPA-ER8 | 0.9286 | 0.8933 | -0.0353 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-HMPA-ER8 | 0.9286 | 0.8933 | -0.0353 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-HMPA-ER8 | 0.9286 | 0.8933 | -0.0353 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-HMPA-ER8 | 0.9286 | 0.8933 | -0.0353 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-HMPA-ER8 | 0.9286 | 0.8933 | -0.0353 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-HMPA-ER8 | 0.9286 | 0.8933 | -0.0353 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-HMPA-ER8 | 0.9295 | 0.8953 | -0.0342 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-HMPA-ER8 | 0.9295 | 0.8953 | -0.0342 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-HMPA-ER8 | 0.9295 | 0.8953 | -0.0342 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-HMPA-ER8 | 0.9295 | 0.8953 | -0.0342 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-HMPA-ER8 | 0.9295 | 0.8953 | -0.0342 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-HMPA-ER8 | 0.9295 | 0.8953 | -0.0342 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-HMPA-ER8 | 0.9302 | 0.8963 | -0.0339 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-HMPA-ER8 | 0.9302 | 0.8963 | -0.0339 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-HMPA-ER8 | 0.9302 | 0.8963 | -0.0339 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-HMPA-ER8 | 0.9302 | 0.8963 | -0.0339 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-HMPA-ER8 | 0.9302 | 0.8963 | -0.0339 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-HMPA-ER8 | 0.9302 | 0.8963 | -0.0339 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-HMPA-ER8 | 0.9308 | 0.8973 | -0.0335 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-HMPA-ER8 | 0.9308 | 0.8973 | -0.0335 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-HMPA-ER8 | 0.9308 | 0.8973 | -0.0335 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-HMPA-ER8 | 0.9308 | 0.8973 | -0.0335 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-HMPA-ER8 | 0.9308 | 0.8973 | -0.0335 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-HMPA-ER8 | 0.9308 | 0.8973 | -0.0335 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-HRLM-ER8 | 0.9226 | 0.8866 | -0.036 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-HRLM-ER8 | 0.9226 | 0.8866 | -0.036 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-HRLM-ER8 | 0.9226 | 0.8866 | -0.036 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-HRLM-ER8 | 0.9226 | 0.8866 | -0.036 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-HRLM-ER8 | 0.9226 | 0.8866 | -0.036 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-HRLM-ER8 | 0.9226 | 0.8866 | -0.036 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-HRLM-ER8 | 0.9224 | 0.8868 | -0.0356 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-HRLM-ER8 | 0.9224 | 0.8868 | -0.0356 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-HRLM-ER8 | 0.9224 | 0.8868 | -0.0356 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-HRLM-ER8 | 0.9224 | 0.8868 | -0.0356 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-HRLM-ER8 | 0.9224 | 0.8868 | -0.0356 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-HRLM-ER8 | 0.9224 | 0.8868 | -0.0356 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-HRLM-ER8 | 0.9233 | 0.8889 | -0.0344 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-HRLM-ER8 | 0.9233 | 0.8889 | -0.0344 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-HRLM-ER8 | 0.9233 | 0.8889 | -0.0344 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-HRLM-ER8 | 0.9233 | 0.8889 | -0.0344 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-HRLM-ER8 | 0.9233 | 0.8889 | -0.0344 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-HRLM-ER8 | 0.9233 | 0.8889 | -0.0344 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-HRLM-ER8 | 0.924 | 0.8898 | -0.0342 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-HRLM-ER8 | 0.924 | 0.8898 | -0.0342 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-HRLM-ER8 | 0.924 | 0.8898 | -0.0342 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-HRLM-ER8 | 0.924 | 0.8898 | -0.0342 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-HRLM-ER8 | 0.924 | 0.8898 | -0.0342 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-HRLM-ER8 | 0.924 | 0.8898 | -0.0342 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-HRLM-ER8 | 0.9246 | 0.8908 | -0.0338 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-HRLM-ER8 | 0.9246 | 0.8908 | -0.0338 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-HRLM-ER8 | 0.9246 | 0.8908 | -0.0338 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-HRLM-ER8 | 0.9246 | 0.8908 | -0.0338 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-HRLM-ER8 | 0.9246 | 0.8908 | -0.0338 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-HRLM-ER8 | 0.9246 | 0.8908 | -0.0338 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-HRLM-ER8 | 0.9293 | 0.8957 | -0.0336 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-HRLM-ER8 | 0.9293 | 0.8957 | -0.0336 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-HRLM-ER8 | 0.9293 | 0.8957 | -0.0336 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-HRLM-ER8 | 0.9293 | 0.8957 | -0.0336 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-HRLM-ER8 | 0.9293 | 0.8957 | -0.0336 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-HRLM-ER8 | 0.9293 | 0.8957 | -0.0336 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-HRLM-ER8 | 0.9292 | 0.896 | -0.0332 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-HRLM-ER8 | 0.9292 | 0.896 | -0.0332 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-HRLM-ER8 | 0.9292 | 0.896 | -0.0332 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-HRLM-ER8 | 0.9292 | 0.896 | -0.0332 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-HRLM-ER8 | 0.9292 | 0.896 | -0.0332 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-HRLM-ER8 | 0.9292 | 0.896 | -0.0332 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-HRLM-ER8 | 0.9302 | 0.8976 | -0.0326 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-HRLM-ER8 | 0.9302 | 0.8976 | -0.0326 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-HRLM-ER8 | 0.9302 | 0.8976 | -0.0326 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-HRLM-ER8 | 0.9302 | 0.8976 | -0.0326 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-HRLM-ER8 | 0.9302 | 0.8976 | -0.0326 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-HRLM-ER8 | 0.9302 | 0.8976 | -0.0326 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-HRLM-ER8 | 0.931 | 0.8991 | -0.0319 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-HRLM-ER8 | 0.931 | 0.8991 | -0.0319 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-HRLM-ER8 | 0.931 | 0.8991 | -0.0319 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-HRLM-ER8 | 0.931 | 0.8991 | -0.0319 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-HRLM-ER8 | 0.931 | 0.8991 | -0.0319 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-HRLM-ER8 | 0.931 | 0.8991 | -0.0319 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-HRLM-ER8 | 0.9313 | 0.8996 | -0.0317 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-HRLM-ER8 | 0.9313 | 0.8996 | -0.0317 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-HRLM-ER8 | 0.9313 | 0.8996 | -0.0317 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-HRLM-ER8 | 0.9313 | 0.8996 | -0.0317 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-HRLM-ER8 | 0.9313 | 0.8996 | -0.0317 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-HRLM-ER8 | 0.9313 | 0.8996 | -0.0317 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-INDM-ER8 | 0.876 | 0.8297 | -0.0463 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-INDM-ER8 | 0.876 | 0.8297 | -0.0463 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-INDM-ER8 | 0.876 | 0.8297 | -0.0463 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-INDM-ER8 | 0.876 | 0.8297 | -0.0463 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-INDM-ER8 | 0.876 | 0.8297 | -0.0463 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-INDM-ER8 | 0.876 | 0.8297 | -0.0463 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-INDM-ER8 | 0.8758 | 0.8298 | -0.046 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-INDM-ER8 | 0.8758 | 0.8298 | -0.046 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-INDM-ER8 | 0.8758 | 0.8298 | -0.046 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-INDM-ER8 | 0.8758 | 0.8298 | -0.046 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-INDM-ER8 | 0.8758 | 0.8298 | -0.046 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-INDM-ER8 | 0.8758 | 0.8298 | -0.046 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-INDM-ER8 | 0.8776 | 0.8344 | -0.0432 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-INDM-ER8 | 0.8776 | 0.8344 | -0.0432 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-INDM-ER8 | 0.8776 | 0.8344 | -0.0432 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-INDM-ER8 | 0.8776 | 0.8344 | -0.0432 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-INDM-ER8 | 0.8776 | 0.8344 | -0.0432 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-INDM-ER8 | 0.8776 | 0.8344 | -0.0432 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-PLAT-ER8 | 0.9365 | 0.8857 | -0.0508 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-PLAT-ER8 | 0.9365 | 0.8857 | -0.0508 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-PLAT-ER8 | 0.9365 | 0.8857 | -0.0508 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-PLAT-ER8 | 0.9365 | 0.8857 | -0.0508 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-PLAT-ER8 | 0.9365 | 0.8857 | -0.0508 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-PLAT-ER8 | 0.9365 | 0.8857 | -0.0508 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-PLAT-ER8 | 0.9362 | 0.8859 | -0.0503 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-PLAT-ER8 | 0.9362 | 0.8859 | -0.0503 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-PLAT-ER8 | 0.9362 | 0.8859 | -0.0503 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-PLAT-ER8 | 0.9362 | 0.8859 | -0.0503 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-PLAT-ER8 | 0.9362 | 0.8859 | -0.0503 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-PLAT-ER8 | 0.9362 | 0.8859 | -0.0503 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-PLAT-ER8 | 0.938 | 0.8914 | -0.0466 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-PLAT-ER8 | 0.938 | 0.8914 | -0.0466 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-PLAT-ER8 | 0.938 | 0.8914 | -0.0466 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-PLAT-ER8 | 0.938 | 0.8914 | -0.0466 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-PLAT-ER8 | 0.938 | 0.8914 | -0.0466 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-PLAT-ER8 | 0.938 | 0.8914 | -0.0466 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-INDM-ER8 | 0.8784 | 0.8353 | -0.0431 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-INDM-ER8 | 0.8784 | 0.8353 | -0.0431 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-INDM-ER8 | 0.8784 | 0.8353 | -0.0431 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-INDM-ER8 | 0.8784 | 0.8353 | -0.0431 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-INDM-ER8 | 0.8784 | 0.8353 | -0.0431 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-INDM-ER8 | 0.8784 | 0.8353 | -0.0431 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-INDM-ER8 | 0.8801 | 0.836 | -0.0441 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-INDM-ER8 | 0.8801 | 0.836 | -0.0441 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-INDM-ER8 | 0.8801 | 0.836 | -0.0441 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-INDM-ER8 | 0.8801 | 0.836 | -0.0441 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-INDM-ER8 | 0.8801 | 0.836 | -0.0441 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-INDM-ER8 | 0.8801 | 0.836 | -0.0441 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-PLAT-ER8 | 0.938 | 0.892 | -0.046 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-PLAT-ER8 | 0.938 | 0.892 | -0.046 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-PLAT-ER8 | 0.938 | 0.892 | -0.046 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-PLAT-ER8 | 0.938 | 0.892 | -0.046 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-PLAT-ER8 | 0.938 | 0.892 | -0.046 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-PLAT-ER8 | 0.938 | 0.892 | -0.046 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-INDM-ER8 | 0.8801 | 0.8366 | -0.0435 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-INDM-ER8 | 0.8801 | 0.8366 | -0.0435 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-INDM-ER8 | 0.8801 | 0.8366 | -0.0435 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-INDM-ER8 | 0.8801 | 0.8366 | -0.0435 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-INDM-ER8 | 0.8801 | 0.8366 | -0.0435 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-INDM-ER8 | 0.8801 | 0.8366 | -0.0435 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-INDM-ER8 | 0.8791 | 0.8367 | -0.0424 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-INDM-ER8 | 0.8791 | 0.8367 | -0.0424 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-INDM-ER8 | 0.8791 | 0.8367 | -0.0424 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-INDM-ER8 | 0.8791 | 0.8367 | -0.0424 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-INDM-ER8 | 0.8791 | 0.8367 | -0.0424 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-INDM-ER8 | 0.8791 | 0.8367 | -0.0424 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-INDM-ER8 | 0.8821 | 0.8399 | -0.0422 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-INDM-ER8 | 0.8821 | 0.8399 | -0.0422 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-INDM-ER8 | 0.8821 | 0.8399 | -0.0422 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-INDM-ER8 | 0.8821 | 0.8399 | -0.0422 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-INDM-ER8 | 0.8821 | 0.8399 | -0.0422 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-INDM-ER8 | 0.8821 | 0.8399 | -0.0422 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-PLAT-ER8 | 0.9391 | 0.8942 | -0.0449 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-PLAT-ER8 | 0.9391 | 0.8942 | -0.0449 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-PLAT-ER8 | 0.9391 | 0.8942 | -0.0449 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-PLAT-ER8 | 0.9391 | 0.8942 | -0.0449 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-PLAT-ER8 | 0.9391 | 0.8942 | -0.0449 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-PLAT-ER8 | 0.9391 | 0.8942 | -0.0449 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-INDM-ER8 | 0.8831 | 0.8417 | -0.0414 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-INDM-ER8 | 0.8831 | 0.8417 | -0.0414 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-INDM-ER8 | 0.8831 | 0.8417 | -0.0414 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-INDM-ER8 | 0.8831 | 0.8417 | -0.0414 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-INDM-ER8 | 0.8831 | 0.8417 | -0.0414 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-INDM-ER8 | 0.8831 | 0.8417 | -0.0414 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-INDM-ER8 | 0.8834 | 0.8423 | -0.0411 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-INDM-ER8 | 0.8834 | 0.8423 | -0.0411 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-INDM-ER8 | 0.8834 | 0.8423 | -0.0411 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-INDM-ER8 | 0.8834 | 0.8423 | -0.0411 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-INDM-ER8 | 0.8834 | 0.8423 | -0.0411 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-INDM-ER8 | 0.8834 | 0.8423 | -0.0411 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-INDM-ER8 | 0.9041 | 0.8734 | -0.0307 |  | 0.9 | 1.05 | 0.10642 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-INDM-ER8 | 0.9041 | 0.8734 | -0.0307 |  | 0.9 | 1.05 | 0.24279 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-INDM-ER8 | 0.9041 | 0.8734 | -0.0307 |  | 0.9 | 1.05 | 0.09958 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-INDM-ER8 | 0.9041 | 0.8734 | -0.0307 |  | 0.9 | 1.05 | 0.03529 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-INDM-ER8 | 0.9041 | 0.8734 | -0.0307 |  | 0.9 | 1.05 | 0.0709 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-INDM-ER8 | 0.9041 | 0.8734 | -0.0307 |  | 0.9 | 1.05 | 0.14646 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-INDM-ER8 | 0.9041 | 0.8734 | -0.0307 |  | 0.9 | 1.05 | 0.10642 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-INDM-ER8 | 0.9041 | 0.8734 | -0.0307 |  | 0.9 | 1.05 | 0.24279 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-INDM-ER8 | 0.9041 | 0.8734 | -0.0307 |  | 0.9 | 1.05 | 0.09958 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-INDM-ER8 | 0.9041 | 0.8734 | -0.0307 |  | 0.9 | 1.05 | 0.03529 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-INDM-ER8 | 0.9041 | 0.8734 | -0.0307 |  | 0.9 | 1.05 | 0.0709 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-INDM-ER8 | 0.9041 | 0.8734 | -0.0307 |  | 0.9 | 1.05 | 0.14646 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-INDM-ER8 | 0.9041 | 0.8734 | -0.0307 |  | 0.9 | 1.05 | 0.10642 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-INDM-ER8 | 0.9041 | 0.8734 | -0.0307 |  | 0.9 | 1.05 | 0.24279 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-INDM-ER8 | 0.9041 | 0.8734 | -0.0307 |  | 0.9 | 1.05 | 0.09958 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-INDM-ER8 | 0.9041 | 0.8734 | -0.0307 |  | 0.9 | 1.05 | 0.03529 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-INDM-ER8 | 0.9041 | 0.8734 | -0.0307 |  | 0.9 | 1.05 | 0.0709 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-INDM-ER8 | 0.9041 | 0.8734 | -0.0307 |  | 0.9 | 1.05 | 0.14646 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-PLAT-ER8 | 0.9407 | 0.8962 | -0.0445 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-PLAT-ER8 | 0.9407 | 0.8962 | -0.0445 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-PLAT-ER8 | 0.9407 | 0.8962 | -0.0445 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-PLAT-ER8 | 0.9407 | 0.8962 | -0.0445 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-PLAT-ER8 | 0.9407 | 0.8962 | -0.0445 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-PLAT-ER8 | 0.9407 | 0.8962 | -0.0445 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-PLAT-ER8 | 0.9415 | 0.8974 | -0.0441 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-PLAT-ER8 | 0.9415 | 0.8974 | -0.0441 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-PLAT-ER8 | 0.9415 | 0.8974 | -0.0441 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-PLAT-ER8 | 0.9415 | 0.8974 | -0.0441 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-PLAT-ER8 | 0.9415 | 0.8974 | -0.0441 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-PLAT-ER8 | 0.9415 | 0.8974 | -0.0441 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-PLAT-ER8 | 0.9411 | 0.8975 | -0.0436 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-PLAT-ER8 | 0.9411 | 0.8975 | -0.0436 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-PLAT-ER8 | 0.9411 | 0.8975 | -0.0436 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-PLAT-ER8 | 0.9411 | 0.8975 | -0.0436 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-PLAT-ER8 | 0.9411 | 0.8975 | -0.0436 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-PLAT-ER8 | 0.9411 | 0.8975 | -0.0436 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-RVR1-ER8 | 0.9383 | 0.8878 | -0.0505 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-RVR1-ER8 | 0.9383 | 0.8878 | -0.0505 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-RVR1-ER8 | 0.9383 | 0.8878 | -0.0505 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-RVR1-ER8 | 0.9383 | 0.8878 | -0.0505 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-RVR1-ER8 | 0.9383 | 0.8878 | -0.0505 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-RVR1-ER8 | 0.9383 | 0.8878 | -0.0505 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-RVR1-ER8 | 0.938 | 0.888 | -0.05 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-RVR1-ER8 | 0.938 | 0.888 | -0.05 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-RVR1-ER8 | 0.938 | 0.888 | -0.05 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-RVR1-ER8 | 0.938 | 0.888 | -0.05 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-RVR1-ER8 | 0.938 | 0.888 | -0.05 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-RVR1-ER8 | 0.938 | 0.888 | -0.05 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-RVR1-ER8 | 0.94 | 0.8936 | -0.0464 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-RVR1-ER8 | 0.94 | 0.8936 | -0.0464 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-RVR1-ER8 | 0.94 | 0.8936 | -0.0464 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-RVR1-ER8 | 0.94 | 0.8936 | -0.0464 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-RVR1-ER8 | 0.94 | 0.8936 | -0.0464 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-RVR1-ER8 | 0.94 | 0.8936 | -0.0464 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-RVR1-ER8 | 0.9399 | 0.8942 | -0.0457 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-RVR1-ER8 | 0.9399 | 0.8942 | -0.0457 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-RVR1-ER8 | 0.9399 | 0.8942 | -0.0457 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-RVR1-ER8 | 0.9399 | 0.8942 | -0.0457 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-RVR1-ER8 | 0.9399 | 0.8942 | -0.0457 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-RVR1-ER8 | 0.9399 | 0.8942 | -0.0457 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-RVR1-ER8 | 0.941 | 0.8962 | -0.0448 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-RVR1-ER8 | 0.941 | 0.8962 | -0.0448 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-RVR1-ER8 | 0.941 | 0.8962 | -0.0448 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-RVR1-ER8 | 0.941 | 0.8962 | -0.0448 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-RVR1-ER8 | 0.941 | 0.8962 | -0.0448 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-RVR1-ER8 | 0.941 | 0.8962 | -0.0448 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-RVR1-ER8 | 0.9425 | 0.8982 | -0.0443 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-RVR1-ER8 | 0.9425 | 0.8982 | -0.0443 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-RVR1-ER8 | 0.9425 | 0.8982 | -0.0443 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-RVR1-ER8 | 0.9425 | 0.8982 | -0.0443 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-RVR1-ER8 | 0.9425 | 0.8982 | -0.0443 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-RVR1-ER8 | 0.9425 | 0.8982 | -0.0443 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-RVR1-ER8 | 0.9433 | 0.8994 | -0.0439 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-RVR1-ER8 | 0.9433 | 0.8994 | -0.0439 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-RVR1-ER8 | 0.9433 | 0.8994 | -0.0439 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-RVR1-ER8 | 0.9433 | 0.8994 | -0.0439 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-RVR1-ER8 | 0.9433 | 0.8994 | -0.0439 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-RVR1-ER8 | 0.9433 | 0.8994 | -0.0439 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-RVR1-ER8 | 0.943 | 0.8996 | -0.0434 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-RVR1-ER8 | 0.943 | 0.8996 | -0.0434 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-RVR1-ER8 | 0.943 | 0.8996 | -0.0434 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-RVR1-ER8 | 0.943 | 0.8996 | -0.0434 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-RVR1-ER8 | 0.943 | 0.8996 | -0.0434 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-RVR1-ER8 | 0.943 | 0.8996 | -0.0434 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-RVR2-ER8 | 0.9383 | 0.8878 | -0.0505 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-RVR2-ER8 | 0.9383 | 0.8878 | -0.0505 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-RVR2-ER8 | 0.9383 | 0.8878 | -0.0505 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-RVR2-ER8 | 0.9383 | 0.8878 | -0.0505 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-RVR2-ER8 | 0.9383 | 0.8878 | -0.0505 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-RVR2-ER8 | 0.9383 | 0.8878 | -0.0505 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-RVR2-ER8 | 0.938 | 0.888 | -0.05 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-RVR2-ER8 | 0.938 | 0.888 | -0.05 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-RVR2-ER8 | 0.938 | 0.888 | -0.05 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-RVR2-ER8 | 0.938 | 0.888 | -0.05 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-RVR2-ER8 | 0.938 | 0.888 | -0.05 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-RVR2-ER8 | 0.938 | 0.888 | -0.05 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-RVR2-ER8 | 0.94 | 0.8936 | -0.0464 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-RVR2-ER8 | 0.94 | 0.8936 | -0.0464 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-RVR2-ER8 | 0.94 | 0.8936 | -0.0464 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-RVR2-ER8 | 0.94 | 0.8936 | -0.0464 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-RVR2-ER8 | 0.94 | 0.8936 | -0.0464 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-RVR2-ER8 | 0.94 | 0.8936 | -0.0464 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-RVR2-ER8 | 0.94 | 0.8942 | -0.0458 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-RVR2-ER8 | 0.94 | 0.8942 | -0.0458 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-RVR2-ER8 | 0.94 | 0.8942 | -0.0458 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-RVR2-ER8 | 0.94 | 0.8942 | -0.0458 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-RVR2-ER8 | 0.94 | 0.8942 | -0.0458 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-RVR2-ER8 | 0.94 | 0.8942 | -0.0458 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-INDM-ER8 | 0.9067 | 0.878 | -0.0287 |  | 0.9 | 1.05 | 0.10623 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-INDM-ER8 | 0.9067 | 0.878 | -0.0287 |  | 0.9 | 1.05 | 0.24261 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-INDM-ER8 | 0.9067 | 0.878 | -0.0287 |  | 0.9 | 1.05 | 0.1005 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-INDM-ER8 | 0.9067 | 0.878 | -0.0287 |  | 0.9 | 1.05 | 0.03506 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-INDM-ER8 | 0.9067 | 0.878 | -0.0287 |  | 0.9 | 1.05 | 0.07067 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-INDM-ER8 | 0.9067 | 0.878 | -0.0287 |  | 0.9 | 1.05 | 0.14607 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-RVR2-ER8 | 0.941 | 0.8962 | -0.0448 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-RVR2-ER8 | 0.941 | 0.8962 | -0.0448 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-RVR2-ER8 | 0.941 | 0.8962 | -0.0448 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-RVR2-ER8 | 0.941 | 0.8962 | -0.0448 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-RVR2-ER8 | 0.941 | 0.8962 | -0.0448 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-RVR2-ER8 | 0.941 | 0.8962 | -0.0448 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-RVR2-ER8 | 0.9425 | 0.8982 | -0.0443 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-RVR2-ER8 | 0.9425 | 0.8982 | -0.0443 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-RVR2-ER8 | 0.9425 | 0.8982 | -0.0443 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-RVR2-ER8 | 0.9425 | 0.8982 | -0.0443 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-RVR2-ER8 | 0.9425 | 0.8982 | -0.0443 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-RVR2-ER8 | 0.9425 | 0.8982 | -0.0443 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-RVR2-ER8 | 0.9433 | 0.8994 | -0.0439 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-RVR2-ER8 | 0.9433 | 0.8994 | -0.0439 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-RVR2-ER8 | 0.9433 | 0.8994 | -0.0439 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-RVR2-ER8 | 0.9433 | 0.8994 | -0.0439 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-RVR2-ER8 | 0.9433 | 0.8994 | -0.0439 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-RVR2-ER8 | 0.9433 | 0.8994 | -0.0439 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-INDM-ER8 | 0.9068 | 0.878 | -0.0288 |  | 0.9 | 1.05 | 0.10623 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-INDM-ER8 | 0.9068 | 0.878 | -0.0288 |  | 0.9 | 1.05 | 0.24261 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-INDM-ER8 | 0.9068 | 0.878 | -0.0288 |  | 0.9 | 1.05 | 0.1005 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-INDM-ER8 | 0.9068 | 0.878 | -0.0288 |  | 0.9 | 1.05 | 0.03506 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-INDM-ER8 | 0.9068 | 0.878 | -0.0288 |  | 0.9 | 1.05 | 0.07067 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-INDM-ER8 | 0.9068 | 0.878 | -0.0288 |  | 0.9 | 1.05 | 0.14607 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-RVR2-ER8 | 0.943 | 0.8996 | -0.0434 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-RVR2-ER8 | 0.943 | 0.8996 | -0.0434 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-RVR2-ER8 | 0.943 | 0.8996 | -0.0434 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-RVR2-ER8 | 0.943 | 0.8996 | -0.0434 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-RVR2-ER8 | 0.943 | 0.8996 | -0.0434 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-RVR2-ER8 | 0.943 | 0.8996 | -0.0434 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-INDM-ER8 | 0.9068 | 0.878 | -0.0288 |  | 0.9 | 1.05 | 0.10623 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-INDM-ER8 | 0.9068 | 0.878 | -0.0288 |  | 0.9 | 1.05 | 0.24261 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-INDM-ER8 | 0.9068 | 0.878 | -0.0288 |  | 0.9 | 1.05 | 0.1005 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-INDM-ER8 | 0.9068 | 0.878 | -0.0288 |  | 0.9 | 1.05 | 0.03506 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-INDM-ER8 | 0.9068 | 0.878 | -0.0288 |  | 0.9 | 1.05 | 0.07067 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-INDM-ER8 | 0.9068 | 0.878 | -0.0288 |  | 0.9 | 1.05 | 0.14607 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-SALM-ER8 | 0.9106 | 0.8669 | -0.0437 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-SALM-ER8 | 0.9106 | 0.8669 | -0.0437 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-SALM-ER8 | 0.9106 | 0.8669 | -0.0437 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-SALM-ER8 | 0.9106 | 0.8669 | -0.0437 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-SALM-ER8 | 0.9106 | 0.8669 | -0.0437 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-SALM-ER8 | 0.9106 | 0.8669 | -0.0437 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-SALM-ER8 | 0.9104 | 0.867 | -0.0434 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-SALM-ER8 | 0.9104 | 0.867 | -0.0434 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-SALM-ER8 | 0.9104 | 0.867 | -0.0434 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-SALM-ER8 | 0.9104 | 0.867 | -0.0434 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-SALM-ER8 | 0.9104 | 0.867 | -0.0434 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-SALM-ER8 | 0.9104 | 0.867 | -0.0434 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-SALM-ER8 | 0.9127 | 0.871 | -0.0417 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-SALM-ER8 | 0.9127 | 0.871 | -0.0417 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-SALM-ER8 | 0.9127 | 0.871 | -0.0417 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-SALM-ER8 | 0.9127 | 0.871 | -0.0417 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-SALM-ER8 | 0.9127 | 0.871 | -0.0417 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-SALM-ER8 | 0.9127 | 0.871 | -0.0417 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-SALM-ER8 | 0.9121 | 0.8713 | -0.0408 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-SALM-ER8 | 0.9121 | 0.8713 | -0.0408 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-SALM-ER8 | 0.9121 | 0.8713 | -0.0408 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-SALM-ER8 | 0.9121 | 0.8713 | -0.0408 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-SALM-ER8 | 0.9121 | 0.8713 | -0.0408 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-SALM-ER8 | 0.9121 | 0.8713 | -0.0408 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-SALM-ER8 | 0.9127 | 0.8716 | -0.0411 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-SALM-ER8 | 0.9127 | 0.8716 | -0.0411 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-SALM-ER8 | 0.9127 | 0.8716 | -0.0411 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-SALM-ER8 | 0.9127 | 0.8716 | -0.0411 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-SALM-ER8 | 0.9127 | 0.8716 | -0.0411 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-SALM-ER8 | 0.9127 | 0.8716 | -0.0411 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-SALM-ER8 | 0.9129 | 0.8722 | -0.0407 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-SALM-ER8 | 0.9129 | 0.8722 | -0.0407 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-SALM-ER8 | 0.9129 | 0.8722 | -0.0407 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-SALM-ER8 | 0.9129 | 0.8722 | -0.0407 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-SALM-ER8 | 0.9129 | 0.8722 | -0.0407 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-SALM-ER8 | 0.9129 | 0.8722 | -0.0407 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-SALM-ER8 | 0.9135 | 0.8735 | -0.04 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-SALM-ER8 | 0.9135 | 0.8735 | -0.04 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-SALM-ER8 | 0.9135 | 0.8735 | -0.04 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-SALM-ER8 | 0.9135 | 0.8735 | -0.04 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-SALM-ER8 | 0.9135 | 0.8735 | -0.04 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-SALM-ER8 | 0.9135 | 0.8735 | -0.04 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-SALM-ER8 | 0.9147 | 0.8747 | -0.04 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-SALM-ER8 | 0.9147 | 0.8747 | -0.04 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-SALM-ER8 | 0.9147 | 0.8747 | -0.04 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-SALM-ER8 | 0.9147 | 0.8747 | -0.04 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-SALM-ER8 | 0.9147 | 0.8747 | -0.04 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-SALM-ER8 | 0.9147 | 0.8747 | -0.04 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-SALM-ER8 | 0.9156 | 0.8764 | -0.0392 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-SALM-ER8 | 0.9156 | 0.8764 | -0.0392 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-SALM-ER8 | 0.9156 | 0.8764 | -0.0392 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-SALM-ER8 | 0.9156 | 0.8764 | -0.0392 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-SALM-ER8 | 0.9156 | 0.8764 | -0.0392 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-SALM-ER8 | 0.9156 | 0.8764 | -0.0392 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-SALM-ER8 | 0.9159 | 0.877 | -0.0389 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-SALM-ER8 | 0.9159 | 0.877 | -0.0389 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-SALM-ER8 | 0.9159 | 0.877 | -0.0389 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-SALM-ER8 | 0.9159 | 0.877 | -0.0389 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-SALM-ER8 | 0.9159 | 0.877 | -0.0389 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-SALM-ER8 | 0.9159 | 0.877 | -0.0389 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-INDM-ER8 | 0.9096 | 0.8853 | -0.0243 |  | 0.9 | 1.05 | 0.10941 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-INDM-ER8 | 0.9096 | 0.8853 | -0.0243 |  | 0.9 | 1.05 | 0.05493 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | ORLAND-ER8 | 0.8954 | 0.8509 | -0.0445 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | ORLAND-ER8 | 0.8954 | 0.8509 | -0.0445 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | ORLAND-ER8 | 0.8954 | 0.8509 | -0.0445 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | ORLAND-ER8 | 0.8954 | 0.8509 | -0.0445 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | ORLAND-ER8 | 0.8954 | 0.8509 | -0.0445 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | ORLAND-ER8 | 0.8954 | 0.8509 | -0.0445 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | ORLAND-ER8 | 0.8952 | 0.8511 | -0.0441 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | ORLAND-ER8 | 0.8952 | 0.8511 | -0.0441 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | ORLAND-ER8 | 0.8952 | 0.8511 | -0.0441 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | ORLAND-ER8 | 0.8952 | 0.8511 | -0.0441 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | ORLAND-ER8 | 0.8952 | 0.8511 | -0.0441 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | ORLAND-ER8 | 0.8952 | 0.8511 | -0.0441 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | ORLAND-ER8 | 0.8967 | 0.8541 | -0.0426 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | ORLAND-ER8 | 0.8967 | 0.8541 | -0.0426 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | ORLAND-ER8 | 0.8967 | 0.8541 | -0.0426 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | ORLAND-ER8 | 0.8967 | 0.8541 | -0.0426 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | ORLAND-ER8 | 0.8967 | 0.8541 | -0.0426 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | ORLAND-ER8 | 0.8967 | 0.8541 | -0.0426 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | ORLAND-ER8 | 0.8967 | 0.8547 | -0.042 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | ORLAND-ER8 | 0.8967 | 0.8547 | -0.042 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | ORLAND-ER8 | 0.8967 | 0.8547 | -0.042 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | ORLAND-ER8 | 0.8967 | 0.8547 | -0.042 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | ORLAND-ER8 | 0.8967 | 0.8547 | -0.042 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | ORLAND-ER8 | 0.8967 | 0.8547 | -0.042 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | ORLAND-ER8 | 0.897 | 0.8554 | -0.0416 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | ORLAND-ER8 | 0.897 | 0.8554 | -0.0416 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | ORLAND-ER8 | 0.897 | 0.8554 | -0.0416 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | ORLAND-ER8 | 0.897 | 0.8554 | -0.0416 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | ORLAND-ER8 | 0.897 | 0.8554 | -0.0416 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | ORLAND-ER8 | 0.897 | 0.8554 | -0.0416 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-INDM-ER8 | 0.9138 | 0.8895 | -0.0243 |  | 0.9 | 1.05 | 0.03069 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-INDM-ER8 | 0.9138 | 0.8895 | -0.0243 |  | 0.9 | 1.05 | 0.10922 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-INDM-ER8 | 0.9138 | 0.8895 | -0.0243 |  | 0.9 | 1.05 | 0.05476 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | ORLAND-ER8 | 0.8977 | 0.8563 | -0.0414 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | ORLAND-ER8 | 0.8977 | 0.8563 | -0.0414 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | ORLAND-ER8 | 0.8977 | 0.8563 | -0.0414 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | ORLAND-ER8 | 0.8977 | 0.8563 | -0.0414 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | ORLAND-ER8 | 0.8977 | 0.8563 | -0.0414 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | ORLAND-ER8 | 0.8977 | 0.8563 | -0.0414 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-INDM-ER8 | 0.9121 | 0.8898 | -0.0223 |  | 0.9 | 1.05 | 0.05765 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-INDM-ER8 | 0.9121 | 0.8898 | -0.0223 |  | 0.9 | 1.05 | 0.04499 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-INDM-ER8 | 0.9121 | 0.8898 | -0.0223 |  | 0.9 | 1.05 | 0.05213 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-INDM-ER8 | 0.9121 | 0.8898 | -0.0223 |  | 0.9 | 1.05 | 0.07544 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-INDM-ER8 | 0.9121 | 0.8898 | -0.0223 |  | 0.9 | 1.05 | 0.07656 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-INDM-ER8 | 0.9121 | 0.8898 | -0.0223 |  | 0.9 | 1.05 | 0.05236 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-INDM-ER8 | 0.9127 | 0.8901 | -0.0226 |  | 0.9 | 1.05 | 0.03199 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-INDM-ER8 | 0.9127 | 0.8901 | -0.0226 |  | 0.9 | 1.05 | 0.04873 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-INDM-ER8 | 0.9127 | 0.8901 | -0.0226 |  | 0.9 | 1.05 | 0.09554 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-INDM-ER8 | 0.9127 | 0.8901 | -0.0226 |  | 0.9 | 1.05 | 0.08589 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-INDM-ER8 | 0.9127 | 0.8901 | -0.0226 |  | 0.9 | 1.05 | 0.04498 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-INDM-ER8 | 0.9127 | 0.8905 | -0.0222 |  | 0.9 | 1.05 | 0.03222 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-INDM-ER8 | 0.9127 | 0.8905 | -0.0222 |  | 0.9 | 1.05 | 0.04909 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-INDM-ER8 | 0.9127 | 0.8905 | -0.0222 |  | 0.9 | 1.05 | 0.09624 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-INDM-ER8 | 0.9127 | 0.8905 | -0.0222 |  | 0.9 | 1.05 | 0.08652 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-INDM-ER8 | 0.9127 | 0.8905 | -0.0222 |  | 0.9 | 1.05 | 0.04531 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-INDM-ER8 | 0.9136 | 0.891 | -0.0226 |  | 0.9 | 1.05 | 0.03222 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-INDM-ER8 | 0.9136 | 0.891 | -0.0226 |  | 0.9 | 1.05 | 0.04909 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-INDM-ER8 | 0.9136 | 0.891 | -0.0226 |  | 0.9 | 1.05 | 0.09624 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-INDM-ER8 | 0.9136 | 0.891 | -0.0226 |  | 0.9 | 1.05 | 0.08652 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-INDM-ER8 | 0.9136 | 0.891 | -0.0226 |  | 0.9 | 1.05 | 0.04531 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-INDM-ER8 | 0.9168 | 0.8951 | -0.0217 |  | 0.9 | 1.05 | 0.05737 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-INDM-ER8 | 0.9168 | 0.8951 | -0.0217 |  | 0.9 | 1.05 | 0.04472 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-INDM-ER8 | 0.9168 | 0.8951 | -0.0217 |  | 0.9 | 1.05 | 0.05275 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-INDM-ER8 | 0.9168 | 0.8951 | -0.0217 |  | 0.9 | 1.05 | 0.07518 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-INDM-ER8 | 0.9168 | 0.8951 | -0.0217 |  | 0.9 | 1.05 | 0.0763 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-INDM-ER8 | 0.9168 | 0.8951 | -0.0217 |  | 0.9 | 1.05 | 0.05195 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-INDM-ER8 | 0.9169 | 0.8952 | -0.0217 |  | 0.9 | 1.05 | 0.03187 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-INDM-ER8 | 0.9169 | 0.8952 | -0.0217 |  | 0.9 | 1.05 | 0.04986 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-INDM-ER8 | 0.9169 | 0.8952 | -0.0217 |  | 0.9 | 1.05 | 0.09536 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-INDM-ER8 | 0.9169 | 0.8952 | -0.0217 |  | 0.9 | 1.05 | 0.08573 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-INDM-ER8 | 0.9169 | 0.8952 | -0.0217 |  | 0.9 | 1.05 | 0.04463 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-INDM-ER8 | 0.9169 | 0.8955 | -0.0214 |  | 0.9 | 1.05 | 0.03211 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-INDM-ER8 | 0.9169 | 0.8955 | -0.0214 |  | 0.9 | 1.05 | 0.05023 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-INDM-ER8 | 0.9169 | 0.8955 | -0.0214 |  | 0.9 | 1.05 | 0.09607 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-INDM-ER8 | 0.9169 | 0.8955 | -0.0214 |  | 0.9 | 1.05 | 0.08636 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-INDM-ER8 | 0.9169 | 0.8955 | -0.0214 |  | 0.9 | 1.05 | 0.04496 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-INDM-ER8 | 0.9177 | 0.896 | -0.0217 |  | 0.9 | 1.05 | 0.03211 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-INDM-ER8 | 0.9177 | 0.896 | -0.0217 |  | 0.9 | 1.05 | 0.05023 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-INDM-ER8 | 0.9177 | 0.896 | -0.0217 |  | 0.9 | 1.05 | 0.09607 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-INDM-ER8 | 0.9177 | 0.896 | -0.0217 |  | 0.9 | 1.05 | 0.08636 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-INDM-ER8 | 0.9177 | 0.896 | -0.0217 |  | 0.9 | 1.05 | 0.04496 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-INDM-ER8 | 0.9212 | 0.8964 | -0.0248 |  | 0.9 | 1.05 | 0.10866 | 659423 GR.LS-LO-BE3 345 762544 G23-182-TAP 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-INDM-ER8 | 0.9212 | 0.8964 | -0.0248 |  | 0.9 | 1.05 | 0.49551 | 659423 GR.LS-LO-BE3 345 762544 G23-182-TAP 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-INDM-ER8 | 0.9212 | 0.8966 | -0.0246 |  | 0.9 | 1.05 | 0.03387 | POI 640252_0 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-INDM-ER8 | 0.9185 | 0.8966 | -0.0219 |  | 0.9 | 1.05 | 0.05737 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-INDM-ER8 | 0.9185 | 0.8966 | -0.0219 |  | 0.9 | 1.05 | 0.04472 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-INDM-ER8 | 0.9185 | 0.8966 | -0.0219 |  | 0.9 | 1.05 | 0.05275 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-INDM-ER8 | 0.9185 | 0.8966 | -0.0219 |  | 0.9 | 1.05 | 0.07518 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-INDM-ER8 | 0.9185 | 0.8966 | -0.0219 |  | 0.9 | 1.05 | 0.0763 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-INDM-ER8 | 0.9185 | 0.8966 | -0.0219 |  | 0.9 | 1.05 | 0.05195 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | ORLAND-ER8 | 0.8984 | 0.8576 | -0.0408 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | ORLAND-ER8 | 0.8984 | 0.8576 | -0.0408 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | ORLAND-ER8 | 0.8984 | 0.8576 | -0.0408 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | ORLAND-ER8 | 0.8984 | 0.8576 | -0.0408 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | ORLAND-ER8 | 0.8984 | 0.8576 | -0.0408 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | ORLAND-ER8 | 0.8984 | 0.8576 | -0.0408 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | ORLAND-ER8 | 0.8986 | 0.8579 | -0.0407 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | ORLAND-ER8 | 0.8986 | 0.8579 | -0.0407 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | ORLAND-ER8 | 0.8986 | 0.8579 | -0.0407 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | ORLAND-ER8 | 0.8986 | 0.8579 | -0.0407 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | ORLAND-ER8 | 0.8986 | 0.8579 | -0.0407 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | ORLAND-ER8 | 0.8986 | 0.8579 | -0.0407 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | ORLAND-ER8 | 0.8996 | 0.8596 | -0.04 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | ORLAND-ER8 | 0.8996 | 0.8596 | -0.04 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | ORLAND-ER8 | 0.8996 | 0.8596 | -0.04 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | ORLAND-ER8 | 0.8996 | 0.8596 | -0.04 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | ORLAND-ER8 | 0.8996 | 0.8596 | -0.04 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | ORLAND-ER8 | 0.8996 | 0.8596 | -0.04 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | ORLAND-ER8 | 0.8999 | 0.8602 | -0.0397 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | ORLAND-ER8 | 0.8999 | 0.8602 | -0.0397 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | ORLAND-ER8 | 0.8999 | 0.8602 | -0.0397 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | ORLAND-ER8 | 0.8999 | 0.8602 | -0.0397 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | ORLAND-ER8 | 0.8999 | 0.8602 | -0.0397 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | ORLAND-ER8 | 0.8999 | 0.8602 | -0.0397 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-INDM-ER8 | 0.9212 | 0.8969 | -0.0243 |  | 0.9 | 1.05 | 0.07277 | 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-INDM-ER8 | 0.9212 | 0.8969 | -0.0243 |  | 0.9 | 1.05 | 0.05101 | 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-INDM-ER8 | 0.9212 | 0.8969 | -0.0243 |  | 0.9 | 1.05 | 0.03331 | 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-INDM-ER8 | 0.9212 | 0.8969 | -0.0243 |  | 0.9 | 1.05 | 0.03727 | 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-INDM-ER8 | 0.9212 | 0.8969 | -0.0243 |  | 0.9 | 1.05 | 0.04392 | 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-INDM-ER8 | 0.9212 | 0.8969 | -0.0243 |  | 0.9 | 1.05 | 0.03744 | 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | ORLAND-ER8 | 0.9225 | 0.8929 | -0.0296 |  | 0.9 | 1.05 | 0.10642 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | ORLAND-ER8 | 0.9225 | 0.8929 | -0.0296 |  | 0.9 | 1.05 | 0.24279 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | ORLAND-ER8 | 0.9225 | 0.8929 | -0.0296 |  | 0.9 | 1.05 | 0.09958 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | ORLAND-ER8 | 0.9225 | 0.8929 | -0.0296 |  | 0.9 | 1.05 | 0.03529 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | ORLAND-ER8 | 0.9225 | 0.8929 | -0.0296 |  | 0.9 | 1.05 | 0.0709 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | ORLAND-ER8 | 0.9225 | 0.8929 | -0.0296 |  | 0.9 | 1.05 | 0.14646 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | ORLAND-ER8 | 0.9225 | 0.8929 | -0.0296 |  | 0.9 | 1.05 | 0.10642 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | ORLAND-ER8 | 0.9225 | 0.8929 | -0.0296 |  | 0.9 | 1.05 | 0.24279 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | ORLAND-ER8 | 0.9225 | 0.8929 | -0.0296 |  | 0.9 | 1.05 | 0.09958 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | ORLAND-ER8 | 0.9225 | 0.8929 | -0.0296 |  | 0.9 | 1.05 | 0.03529 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | ORLAND-ER8 | 0.9225 | 0.8929 | -0.0296 |  | 0.9 | 1.05 | 0.0709 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | ORLAND-ER8 | 0.9225 | 0.8929 | -0.0296 |  | 0.9 | 1.05 | 0.14646 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | ORLAND-ER8 | 0.9225 | 0.8929 | -0.0296 |  | 0.9 | 1.05 | 0.10642 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | ORLAND-ER8 | 0.9225 | 0.8929 | -0.0296 |  | 0.9 | 1.05 | 0.24279 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | ORLAND-ER8 | 0.9225 | 0.8929 | -0.0296 |  | 0.9 | 1.05 | 0.09958 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | ORLAND-ER8 | 0.9225 | 0.8929 | -0.0296 |  | 0.9 | 1.05 | 0.03529 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | ORLAND-ER8 | 0.9225 | 0.8929 | -0.0296 |  | 0.9 | 1.05 | 0.0709 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | ORLAND-ER8 | 0.9225 | 0.8929 | -0.0296 |  | 0.9 | 1.05 | 0.14646 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-INDM-ER8 | 0.9212 | 0.897 | -0.0242 |  | 0.9 | 1.05 | 0.11223 | POI 640510_8 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-INDM-ER8 | 0.9212 | 0.897 | -0.0242 |  | 0.9 | 1.05 | 0.09867 | POI 640510_8 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-INDM-ER8 | 0.9212 | 0.897 | -0.0242 |  | 0.9 | 1.05 | 0.10969 | POI 640510_8 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-INDM-ER8 | 0.9212 | 0.897 | -0.0242 |  | 0.9 | 1.05 | 0.18255 | POI 640510_8 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-INDM-ER8 | 0.9212 | 0.897 | -0.0242 |  | 0.9 | 1.05 | 0.14194 | POI 640510_8 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-INDM-ER8 | 0.9212 | 0.897 | -0.0242 |  | 0.9 | 1.05 | 0.1119 | POI 640510_8 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-INDM-ER8 | 0.9212 | 0.897 | -0.0242 |  | 0.9 | 1.05 | 0.11223 | POI 640510_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-INDM-ER8 | 0.9212 | 0.897 | -0.0242 |  | 0.9 | 1.05 | 0.09867 | POI 640510_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-INDM-ER8 | 0.9212 | 0.897 | -0.0242 |  | 0.9 | 1.05 | 0.10969 | POI 640510_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-INDM-ER8 | 0.9212 | 0.897 | -0.0242 |  | 0.9 | 1.05 | 0.18255 | POI 640510_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-INDM-ER8 | 0.9212 | 0.897 | -0.0242 |  | 0.9 | 1.05 | 0.14194 | POI 640510_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-INDM-ER8 | 0.9212 | 0.897 | -0.0242 |  | 0.9 | 1.05 | 0.1119 | POI 640510_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-INDM-ER8 | 0.9212 | 0.897 | -0.0242 |  | 0.9 | 1.05 | 0.11223 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-INDM-ER8 | 0.9212 | 0.897 | -0.0242 |  | 0.9 | 1.05 | 0.09867 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-INDM-ER8 | 0.9212 | 0.897 | -0.0242 |  | 0.9 | 1.05 | 0.10969 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-INDM-ER8 | 0.9212 | 0.897 | -0.0242 |  | 0.9 | 1.05 | 0.18255 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-INDM-ER8 | 0.9212 | 0.897 | -0.0242 |  | 0.9 | 1.05 | 0.14194 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-INDM-ER8 | 0.9212 | 0.897 | -0.0242 |  | 0.9 | 1.05 | 0.1119 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-INDM-ER8 | 0.9212 | 0.8971 | -0.0241 |  | 0.9 | 1.05 | 0.11223 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-INDM-ER8 | 0.9212 | 0.8971 | -0.0241 |  | 0.9 | 1.05 | 0.09867 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-INDM-ER8 | 0.9212 | 0.8971 | -0.0241 |  | 0.9 | 1.05 | 0.10969 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-INDM-ER8 | 0.9212 | 0.8971 | -0.0241 |  | 0.9 | 1.05 | 0.18255 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-INDM-ER8 | 0.9212 | 0.8971 | -0.0241 |  | 0.9 | 1.05 | 0.14194 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-INDM-ER8 | 0.9212 | 0.8971 | -0.0241 |  | 0.9 | 1.05 | 0.1119 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | ORLAND-ER8 | 0.9225 | 0.8946 | -0.0279 |  | 0.9 | 1.05 | 0.10623 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | ORLAND-ER8 | 0.9225 | 0.8946 | -0.0279 |  | 0.9 | 1.05 | 0.24261 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | ORLAND-ER8 | 0.9225 | 0.8946 | -0.0279 |  | 0.9 | 1.05 | 0.1005 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | ORLAND-ER8 | 0.9225 | 0.8946 | -0.0279 |  | 0.9 | 1.05 | 0.03506 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | ORLAND-ER8 | 0.9225 | 0.8946 | -0.0279 |  | 0.9 | 1.05 | 0.07067 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | ORLAND-ER8 | 0.9225 | 0.8946 | -0.0279 |  | 0.9 | 1.05 | 0.14607 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | ORLAND-ER8 | 0.9225 | 0.8946 | -0.0279 |  | 0.9 | 1.05 | 0.10623 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | ORLAND-ER8 | 0.9225 | 0.8946 | -0.0279 |  | 0.9 | 1.05 | 0.24261 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | ORLAND-ER8 | 0.9225 | 0.8946 | -0.0279 |  | 0.9 | 1.05 | 0.1005 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | ORLAND-ER8 | 0.9225 | 0.8946 | -0.0279 |  | 0.9 | 1.05 | 0.03506 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | ORLAND-ER8 | 0.9225 | 0.8946 | -0.0279 |  | 0.9 | 1.05 | 0.07067 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | ORLAND-ER8 | 0.9225 | 0.8946 | -0.0279 |  | 0.9 | 1.05 | 0.14607 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | ORLAND-ER8 | 0.9225 | 0.8946 | -0.0279 |  | 0.9 | 1.05 | 0.10623 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | ORLAND-ER8 | 0.9225 | 0.8946 | -0.0279 |  | 0.9 | 1.05 | 0.24261 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | ORLAND-ER8 | 0.9225 | 0.8946 | -0.0279 |  | 0.9 | 1.05 | 0.1005 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | ORLAND-ER8 | 0.9225 | 0.8946 | -0.0279 |  | 0.9 | 1.05 | 0.03506 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | ORLAND-ER8 | 0.9225 | 0.8946 | -0.0279 |  | 0.9 | 1.05 | 0.07067 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | ORLAND-ER8 | 0.9225 | 0.8946 | -0.0279 |  | 0.9 | 1.05 | 0.14607 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-INDM-ER8 | 0.9212 | 0.8988 | -0.0224 |  | 0.9 | 1.05 | 0.03541 | 659133 SIDNEY__-MB3 345 659135 STEGALL_-MB3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-INDM-ER8 | 0.9212 | 0.8988 | -0.0224 |  | 0.9 | 1.05 | 0.04707 | 155360 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-INDM-ER8 | 0.9212 | 0.8988 | -0.0224 |  | 0.9 | 1.05 | 0.03131 | 155360 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-INDM-ER8 | 0.924 | 0.8998 | -0.0242 |  | 0.9 | 1.05 | 0.04049 | POI 640374_5 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-INDM-ER8 | 0.924 | 0.8998 | -0.0242 |  | 0.9 | 1.05 | 0.0359 | POI 640374_5 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-INDM-ER8 | 0.924 | 0.8998 | -0.0242 |  | 0.9 | 1.05 | 0.04491 | POI 640374_5 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-INDM-ER8 | 0.924 | 0.8998 | -0.0242 |  | 0.9 | 1.05 | 0.05666 | POI 640374_5 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-INDM-ER8 | 0.924 | 0.8998 | -0.0242 |  | 0.9 | 1.05 | 0.04963 | POI 640374_5 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-INDM-ER8 | 0.924 | 0.8998 | -0.0242 |  | 0.9 | 1.05 | 0.04174 | POI 640374_5 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-LTCH-ER8 | 0.9358 | 0.8903 | -0.0455 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-LTCH-ER8 | 0.9358 | 0.8903 | -0.0455 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-LTCH-ER8 | 0.9358 | 0.8903 | -0.0455 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-LTCH-ER8 | 0.9358 | 0.8903 | -0.0455 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-LTCH-ER8 | 0.9358 | 0.8903 | -0.0455 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-LTCH-ER8 | 0.9358 | 0.8903 | -0.0455 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-LTCH-ER8 | 0.9354 | 0.8905 | -0.0449 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-LTCH-ER8 | 0.9354 | 0.8905 | -0.0449 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-LTCH-ER8 | 0.9354 | 0.8905 | -0.0449 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-LTCH-ER8 | 0.9354 | 0.8905 | -0.0449 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-LTCH-ER8 | 0.9354 | 0.8905 | -0.0449 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-LTCH-ER8 | 0.9354 | 0.8905 | -0.0449 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-LTCH-ER8 | 0.9368 | 0.8925 | -0.0443 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-LTCH-ER8 | 0.9368 | 0.8925 | -0.0443 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-LTCH-ER8 | 0.9368 | 0.8925 | -0.0443 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-LTCH-ER8 | 0.9368 | 0.8925 | -0.0443 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-LTCH-ER8 | 0.9368 | 0.8925 | -0.0443 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-LTCH-ER8 | 0.9368 | 0.8925 | -0.0443 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-LTCH-ER8 | 0.9368 | 0.8953 | -0.0415 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-LTCH-ER8 | 0.9368 | 0.8953 | -0.0415 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-LTCH-ER8 | 0.9368 | 0.8953 | -0.0415 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-LTCH-ER8 | 0.9368 | 0.8953 | -0.0415 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-LTCH-ER8 | 0.9368 | 0.8953 | -0.0415 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-LTCH-ER8 | 0.9368 | 0.8953 | -0.0415 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-LTCH-ER8 | 0.9386 | 0.8959 | -0.0427 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-LTCH-ER8 | 0.9386 | 0.8959 | -0.0427 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-LTCH-ER8 | 0.9386 | 0.8959 | -0.0427 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-LTCH-ER8 | 0.9386 | 0.8959 | -0.0427 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-LTCH-ER8 | 0.9386 | 0.8959 | -0.0427 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-LTCH-ER8 | 0.9386 | 0.8959 | -0.0427 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-LTCH-ER8 | 0.9372 | 0.8962 | -0.041 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-LTCH-ER8 | 0.9372 | 0.8962 | -0.041 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-LTCH-ER8 | 0.9372 | 0.8962 | -0.041 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-LTCH-ER8 | 0.9372 | 0.8962 | -0.041 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-LTCH-ER8 | 0.9372 | 0.8962 | -0.041 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-LTCH-ER8 | 0.9372 | 0.8962 | -0.041 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-LTCH-ER8 | 0.9388 | 0.8968 | -0.042 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-LTCH-ER8 | 0.9388 | 0.8968 | -0.042 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-LTCH-ER8 | 0.9388 | 0.8968 | -0.042 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-LTCH-ER8 | 0.9388 | 0.8968 | -0.042 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-LTCH-ER8 | 0.9388 | 0.8968 | -0.042 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-LTCH-ER8 | 0.9388 | 0.8968 | -0.042 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-LTCH-ER8 | 0.9396 | 0.8995 | -0.0401 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-LTCH-ER8 | 0.9396 | 0.8995 | -0.0401 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-LTCH-ER8 | 0.9396 | 0.8995 | -0.0401 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-LTCH-ER8 | 0.9396 | 0.8995 | -0.0401 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-LTCH-ER8 | 0.9396 | 0.8995 | -0.0401 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-LTCH-ER8 | 0.9396 | 0.8995 | -0.0401 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-MRRD-ER7 | 0.9338 | 0.8981 | -0.0357 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-MRRD-ER7 | 0.9338 | 0.8981 | -0.0357 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-MRRD-ER7 | 0.9338 | 0.8981 | -0.0357 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-MRRD-ER7 | 0.9338 | 0.8981 | -0.0357 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-MRRD-ER7 | 0.9338 | 0.8981 | -0.0357 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-MRRD-ER7 | 0.9338 | 0.8981 | -0.0357 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-MRRD-ER7 | 0.9336 | 0.8982 | -0.0354 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-MRRD-ER7 | 0.9336 | 0.8982 | -0.0354 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-MRRD-ER7 | 0.9336 | 0.8982 | -0.0354 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-MRRD-ER7 | 0.9336 | 0.8982 | -0.0354 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-MRRD-ER7 | 0.9336 | 0.8982 | -0.0354 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-MRRD-ER7 | 0.9336 | 0.8982 | -0.0354 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-NMAR-ER8 | 0.906 | 0.8617 | -0.0443 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-NMAR-ER8 | 0.906 | 0.8617 | -0.0443 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-NMAR-ER8 | 0.906 | 0.8617 | -0.0443 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-NMAR-ER8 | 0.906 | 0.8617 | -0.0443 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-NMAR-ER8 | 0.906 | 0.8617 | -0.0443 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-NMAR-ER8 | 0.906 | 0.8617 | -0.0443 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-NMAR-ER8 | 0.9058 | 0.8619 | -0.0439 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-NMAR-ER8 | 0.9058 | 0.8619 | -0.0439 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-NMAR-ER8 | 0.9058 | 0.8619 | -0.0439 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-NMAR-ER8 | 0.9058 | 0.8619 | -0.0439 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-NMAR-ER8 | 0.9058 | 0.8619 | -0.0439 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-NMAR-ER8 | 0.9058 | 0.8619 | -0.0439 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-NMAR-ER8 | 0.9075 | 0.8662 | -0.0413 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-NMAR-ER8 | 0.9075 | 0.8662 | -0.0413 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-NMAR-ER8 | 0.9075 | 0.8662 | -0.0413 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-NMAR-ER8 | 0.9075 | 0.8662 | -0.0413 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-NMAR-ER8 | 0.9075 | 0.8662 | -0.0413 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-NMAR-ER8 | 0.9075 | 0.8662 | -0.0413 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-NMAR-ER8 | 0.909 | 0.8668 | -0.0422 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-NMAR-ER8 | 0.909 | 0.8668 | -0.0422 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-NMAR-ER8 | 0.909 | 0.8668 | -0.0422 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-NMAR-ER8 | 0.909 | 0.8668 | -0.0422 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-NMAR-ER8 | 0.909 | 0.8668 | -0.0422 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-NMAR-ER8 | 0.909 | 0.8668 | -0.0422 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-NMAR-ER8 | 0.9083 | 0.8671 | -0.0412 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-NMAR-ER8 | 0.9083 | 0.8671 | -0.0412 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-NMAR-ER8 | 0.9083 | 0.8671 | -0.0412 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-NMAR-ER8 | 0.9083 | 0.8671 | -0.0412 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-NMAR-ER8 | 0.9083 | 0.8671 | -0.0412 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-NMAR-ER8 | 0.9083 | 0.8671 | -0.0412 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-NMAR-ER8 | 0.909 | 0.8673 | -0.0417 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-NMAR-ER8 | 0.909 | 0.8673 | -0.0417 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-NMAR-ER8 | 0.909 | 0.8673 | -0.0417 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-NMAR-ER8 | 0.909 | 0.8673 | -0.0417 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-NMAR-ER8 | 0.909 | 0.8673 | -0.0417 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-NMAR-ER8 | 0.909 | 0.8673 | -0.0417 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-NMAR-ER8 | 0.909 | 0.8684 | -0.0406 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-NMAR-ER8 | 0.909 | 0.8684 | -0.0406 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-NMAR-ER8 | 0.909 | 0.8684 | -0.0406 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-NMAR-ER8 | 0.909 | 0.8684 | -0.0406 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-NMAR-ER8 | 0.909 | 0.8684 | -0.0406 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-NMAR-ER8 | 0.909 | 0.8684 | -0.0406 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-NMAR-ER8 | 0.9109 | 0.8705 | -0.0404 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-NMAR-ER8 | 0.9109 | 0.8705 | -0.0404 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-NMAR-ER8 | 0.9109 | 0.8705 | -0.0404 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-NMAR-ER8 | 0.9109 | 0.8705 | -0.0404 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-NMAR-ER8 | 0.9109 | 0.8705 | -0.0404 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-NMAR-ER8 | 0.9109 | 0.8705 | -0.0404 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-NMAR-ER8 | 0.9119 | 0.8723 | -0.0396 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-NMAR-ER8 | 0.9119 | 0.8723 | -0.0396 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-NMAR-ER8 | 0.9119 | 0.8723 | -0.0396 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-NMAR-ER8 | 0.9119 | 0.8723 | -0.0396 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-NMAR-ER8 | 0.9119 | 0.8723 | -0.0396 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-NMAR-ER8 | 0.9119 | 0.8723 | -0.0396 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-NMAR-ER8 | 0.9122 | 0.8728 | -0.0394 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-NMAR-ER8 | 0.9122 | 0.8728 | -0.0394 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-NMAR-ER8 | 0.9122 | 0.8728 | -0.0394 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-NMAR-ER8 | 0.9122 | 0.8728 | -0.0394 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-NMAR-ER8 | 0.9122 | 0.8728 | -0.0394 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-NMAR-ER8 | 0.9122 | 0.8728 | -0.0394 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-PARK-ER8 | 0.9302 | 0.8946 | -0.0356 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-PARK-ER8 | 0.9302 | 0.8946 | -0.0356 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-PARK-ER8 | 0.9302 | 0.8946 | -0.0356 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-PARK-ER8 | 0.9302 | 0.8946 | -0.0356 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-PARK-ER8 | 0.9302 | 0.8946 | -0.0356 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-PARK-ER8 | 0.9302 | 0.8946 | -0.0356 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-PARK-ER8 | 0.93 | 0.8947 | -0.0353 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-PARK-ER8 | 0.93 | 0.8947 | -0.0353 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-PARK-ER8 | 0.93 | 0.8947 | -0.0353 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-PARK-ER8 | 0.93 | 0.8947 | -0.0353 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-PARK-ER8 | 0.93 | 0.8947 | -0.0353 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-PARK-ER8 | 0.93 | 0.8947 | -0.0353 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-PARK-ER8 | 0.9309 | 0.8968 | -0.0341 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-PARK-ER8 | 0.9309 | 0.8968 | -0.0341 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-PARK-ER8 | 0.9309 | 0.8968 | -0.0341 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-PARK-ER8 | 0.9309 | 0.8968 | -0.0341 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-PARK-ER8 | 0.9309 | 0.8968 | -0.0341 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-PARK-ER8 | 0.9309 | 0.8968 | -0.0341 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-PARK-ER8 | 0.9316 | 0.8977 | -0.0339 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-PARK-ER8 | 0.9316 | 0.8977 | -0.0339 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-PARK-ER8 | 0.9316 | 0.8977 | -0.0339 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-PARK-ER8 | 0.9316 | 0.8977 | -0.0339 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-PARK-ER8 | 0.9316 | 0.8977 | -0.0339 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-PARK-ER8 | 0.9316 | 0.8977 | -0.0339 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-PARK-ER8 | 0.9322 | 0.8987 | -0.0335 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-PARK-ER8 | 0.9322 | 0.8987 | -0.0335 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-PARK-ER8 | 0.9322 | 0.8987 | -0.0335 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-PARK-ER8 | 0.9322 | 0.8987 | -0.0335 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-PARK-ER8 | 0.9322 | 0.8987 | -0.0335 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-PARK-ER8 | 0.9322 | 0.8987 | -0.0335 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-PLNO-ER8 | 0.9292 | 0.883 | -0.0462 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-PLNO-ER8 | 0.9292 | 0.883 | -0.0462 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-PLNO-ER8 | 0.9292 | 0.883 | -0.0462 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-PLNO-ER8 | 0.9292 | 0.883 | -0.0462 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-PLNO-ER8 | 0.9292 | 0.883 | -0.0462 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-PLNO-ER8 | 0.9292 | 0.883 | -0.0462 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-PLNO-ER8 | 0.9288 | 0.8832 | -0.0456 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-PLNO-ER8 | 0.9288 | 0.8832 | -0.0456 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-PLNO-ER8 | 0.9288 | 0.8832 | -0.0456 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-PLNO-ER8 | 0.9288 | 0.8832 | -0.0456 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-PLNO-ER8 | 0.9288 | 0.8832 | -0.0456 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-PLNO-ER8 | 0.9288 | 0.8832 | -0.0456 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-PLNO-ER8 | 0.9301 | 0.8851 | -0.045 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-PLNO-ER8 | 0.9301 | 0.8851 | -0.045 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-PLNO-ER8 | 0.9301 | 0.8851 | -0.045 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-PLNO-ER8 | 0.9301 | 0.8851 | -0.045 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-PLNO-ER8 | 0.9301 | 0.8851 | -0.045 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-PLNO-ER8 | 0.9301 | 0.8851 | -0.045 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-PLNO-ER8 | 0.9301 | 0.888 | -0.0421 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-PLNO-ER8 | 0.9301 | 0.888 | -0.0421 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-PLNO-ER8 | 0.9301 | 0.888 | -0.0421 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-PLNO-ER8 | 0.9301 | 0.888 | -0.0421 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-PLNO-ER8 | 0.9301 | 0.888 | -0.0421 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-PLNO-ER8 | 0.9301 | 0.888 | -0.0421 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-PLNO-ER8 | 0.9321 | 0.8887 | -0.0434 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-PLNO-ER8 | 0.9321 | 0.8887 | -0.0434 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-PLNO-ER8 | 0.9321 | 0.8887 | -0.0434 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-PLNO-ER8 | 0.9321 | 0.8887 | -0.0434 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-PLNO-ER8 | 0.9321 | 0.8887 | -0.0434 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-PLNO-ER8 | 0.9321 | 0.8887 | -0.0434 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-PLNO-ER8 | 0.9307 | 0.8891 | -0.0416 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-PLNO-ER8 | 0.9307 | 0.8891 | -0.0416 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-PLNO-ER8 | 0.9307 | 0.8891 | -0.0416 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-PLNO-ER8 | 0.9307 | 0.8891 | -0.0416 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-PLNO-ER8 | 0.9307 | 0.8891 | -0.0416 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-PLNO-ER8 | 0.9307 | 0.8891 | -0.0416 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-PLNO-ER8 | 0.9322 | 0.8895 | -0.0427 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-PLNO-ER8 | 0.9322 | 0.8895 | -0.0427 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-PLNO-ER8 | 0.9322 | 0.8895 | -0.0427 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-PLNO-ER8 | 0.9322 | 0.8895 | -0.0427 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-PLNO-ER8 | 0.9322 | 0.8895 | -0.0427 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-PLNO-ER8 | 0.9322 | 0.8895 | -0.0427 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-PLNO-ER8 | 0.9331 | 0.8924 | -0.0407 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-PLNO-ER8 | 0.9331 | 0.8924 | -0.0407 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-PLNO-ER8 | 0.9331 | 0.8924 | -0.0407 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-PLNO-ER8 | 0.9331 | 0.8924 | -0.0407 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-PLNO-ER8 | 0.9331 | 0.8924 | -0.0407 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-PLNO-ER8 | 0.9331 | 0.8924 | -0.0407 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | PUKWANA-ER8 | 0.9243 | 0.8725 | -0.0518 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | PUKWANA-ER8 | 0.9243 | 0.8725 | -0.0518 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | PUKWANA-ER8 | 0.9243 | 0.8725 | -0.0518 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | PUKWANA-ER8 | 0.9243 | 0.8725 | -0.0518 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | PUKWANA-ER8 | 0.9243 | 0.8725 | -0.0518 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | PUKWANA-ER8 | 0.9243 | 0.8725 | -0.0518 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | PUKWANA-ER8 | 0.924 | 0.8727 | -0.0513 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | PUKWANA-ER8 | 0.924 | 0.8727 | -0.0513 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | PUKWANA-ER8 | 0.924 | 0.8727 | -0.0513 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | PUKWANA-ER8 | 0.924 | 0.8727 | -0.0513 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | PUKWANA-ER8 | 0.924 | 0.8727 | -0.0513 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | PUKWANA-ER8 | 0.924 | 0.8727 | -0.0513 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | PUKWANA-ER8 | 0.9258 | 0.8782 | -0.0476 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | PUKWANA-ER8 | 0.9258 | 0.8782 | -0.0476 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | PUKWANA-ER8 | 0.9258 | 0.8782 | -0.0476 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | PUKWANA-ER8 | 0.9258 | 0.8782 | -0.0476 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | PUKWANA-ER8 | 0.9258 | 0.8782 | -0.0476 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | PUKWANA-ER8 | 0.9258 | 0.8782 | -0.0476 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-PLNO-ER8 | 0.9346 | 0.8945 | -0.0401 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-PLNO-ER8 | 0.9346 | 0.8945 | -0.0401 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-PLNO-ER8 | 0.9346 | 0.8945 | -0.0401 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-PLNO-ER8 | 0.9346 | 0.8945 | -0.0401 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-PLNO-ER8 | 0.9346 | 0.8945 | -0.0401 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-PLNO-ER8 | 0.9346 | 0.8945 | -0.0401 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-PLNO-ER8 | 0.935 | 0.895 | -0.04 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-PLNO-ER8 | 0.935 | 0.895 | -0.04 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-PLNO-ER8 | 0.935 | 0.895 | -0.04 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-PLNO-ER8 | 0.935 | 0.895 | -0.04 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-PLNO-ER8 | 0.935 | 0.895 | -0.04 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-PLNO-ER8 | 0.935 | 0.895 | -0.04 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | PUKWANA-ER8 | 0.9258 | 0.8788 | -0.047 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | PUKWANA-ER8 | 0.9258 | 0.8788 | -0.047 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | PUKWANA-ER8 | 0.9258 | 0.8788 | -0.047 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | PUKWANA-ER8 | 0.9258 | 0.8788 | -0.047 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | PUKWANA-ER8 | 0.9258 | 0.8788 | -0.047 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | PUKWANA-ER8 | 0.9258 | 0.8788 | -0.047 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | PUKWANA-ER8 | 0.927 | 0.8811 | -0.0459 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | PUKWANA-ER8 | 0.927 | 0.8811 | -0.0459 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | PUKWANA-ER8 | 0.927 | 0.8811 | -0.0459 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | PUKWANA-ER8 | 0.927 | 0.8811 | -0.0459 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | PUKWANA-ER8 | 0.927 | 0.8811 | -0.0459 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | PUKWANA-ER8 | 0.927 | 0.8811 | -0.0459 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | PUKWANA-ER8 | 0.9286 | 0.8832 | -0.0454 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | PUKWANA-ER8 | 0.9286 | 0.8832 | -0.0454 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | PUKWANA-ER8 | 0.9286 | 0.8832 | -0.0454 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | PUKWANA-ER8 | 0.9286 | 0.8832 | -0.0454 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | PUKWANA-ER8 | 0.9286 | 0.8832 | -0.0454 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | PUKWANA-ER8 | 0.9286 | 0.8832 | -0.0454 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | PUKWANA-ER8 | 0.9294 | 0.8844 | -0.045 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | PUKWANA-ER8 | 0.9294 | 0.8844 | -0.045 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | PUKWANA-ER8 | 0.9294 | 0.8844 | -0.045 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | PUKWANA-ER8 | 0.9294 | 0.8844 | -0.045 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | PUKWANA-ER8 | 0.9294 | 0.8844 | -0.045 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | PUKWANA-ER8 | 0.9294 | 0.8844 | -0.045 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | PUKWANA-ER8 | 0.9288 | 0.8844 | -0.0444 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | PUKWANA-ER8 | 0.9288 | 0.8844 | -0.0444 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | PUKWANA-ER8 | 0.9288 | 0.8844 | -0.0444 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | PUKWANA-ER8 | 0.9288 | 0.8844 | -0.0444 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | PUKWANA-ER8 | 0.9288 | 0.8844 | -0.0444 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | PUKWANA-ER8 | 0.9288 | 0.8844 | -0.0444 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | PUKWANA-ER8 | 0.9307 | 0.8871 | -0.0436 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | PUKWANA-ER8 | 0.9307 | 0.8871 | -0.0436 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | PUKWANA-ER8 | 0.9307 | 0.8871 | -0.0436 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | PUKWANA-ER8 | 0.9307 | 0.8871 | -0.0436 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | PUKWANA-ER8 | 0.9307 | 0.8871 | -0.0436 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | PUKWANA-ER8 | 0.9307 | 0.8871 | -0.0436 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | PUKWANA-ER8 | 0.931 | 0.8876 | -0.0434 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | PUKWANA-ER8 | 0.931 | 0.8876 | -0.0434 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | PUKWANA-ER8 | 0.931 | 0.8876 | -0.0434 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | PUKWANA-ER8 | 0.931 | 0.8876 | -0.0434 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | PUKWANA-ER8 | 0.931 | 0.8876 | -0.0434 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | PUKWANA-ER8 | 0.931 | 0.8876 | -0.0434 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SALEM-ER8 | 0.9106 | 0.8669 | -0.0437 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SALEM-ER8 | 0.9106 | 0.8669 | -0.0437 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SALEM-ER8 | 0.9106 | 0.8669 | -0.0437 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SALEM-ER8 | 0.9106 | 0.8669 | -0.0437 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SALEM-ER8 | 0.9106 | 0.8669 | -0.0437 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SALEM-ER8 | 0.9106 | 0.8669 | -0.0437 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SALEM-ER8 | 0.9104 | 0.8671 | -0.0433 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SALEM-ER8 | 0.9104 | 0.8671 | -0.0433 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SALEM-ER8 | 0.9104 | 0.8671 | -0.0433 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SALEM-ER8 | 0.9104 | 0.8671 | -0.0433 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SALEM-ER8 | 0.9104 | 0.8671 | -0.0433 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SALEM-ER8 | 0.9104 | 0.8671 | -0.0433 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SALEM-ER8 | 0.9128 | 0.8711 | -0.0417 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SALEM-ER8 | 0.9128 | 0.8711 | -0.0417 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SALEM-ER8 | 0.9128 | 0.8711 | -0.0417 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SALEM-ER8 | 0.9128 | 0.8711 | -0.0417 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SALEM-ER8 | 0.9128 | 0.8711 | -0.0417 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SALEM-ER8 | 0.9128 | 0.8711 | -0.0417 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SALEM-ER8 | 0.9122 | 0.8713 | -0.0409 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SALEM-ER8 | 0.9122 | 0.8713 | -0.0409 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SALEM-ER8 | 0.9122 | 0.8713 | -0.0409 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SALEM-ER8 | 0.9122 | 0.8713 | -0.0409 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SALEM-ER8 | 0.9122 | 0.8713 | -0.0409 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SALEM-ER8 | 0.9122 | 0.8713 | -0.0409 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SALEM-ER8 | 0.9128 | 0.8716 | -0.0412 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SALEM-ER8 | 0.9128 | 0.8716 | -0.0412 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SALEM-ER8 | 0.9128 | 0.8716 | -0.0412 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SALEM-ER8 | 0.9128 | 0.8716 | -0.0412 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SALEM-ER8 | 0.9128 | 0.8716 | -0.0412 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SALEM-ER8 | 0.9128 | 0.8716 | -0.0412 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SALEM-ER8 | 0.9129 | 0.8722 | -0.0407 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SALEM-ER8 | 0.9129 | 0.8722 | -0.0407 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SALEM-ER8 | 0.9129 | 0.8722 | -0.0407 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SALEM-ER8 | 0.9129 | 0.8722 | -0.0407 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SALEM-ER8 | 0.9129 | 0.8722 | -0.0407 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SALEM-ER8 | 0.9129 | 0.8722 | -0.0407 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SALEM-ER8 | 0.9136 | 0.8735 | -0.0401 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SALEM-ER8 | 0.9136 | 0.8735 | -0.0401 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SALEM-ER8 | 0.9136 | 0.8735 | -0.0401 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SALEM-ER8 | 0.9136 | 0.8735 | -0.0401 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SALEM-ER8 | 0.9136 | 0.8735 | -0.0401 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SALEM-ER8 | 0.9136 | 0.8735 | -0.0401 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-SPNC-ER8 | 0.9065 | 0.8625 | -0.044 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-SPNC-ER8 | 0.9065 | 0.8625 | -0.044 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-SPNC-ER8 | 0.9065 | 0.8625 | -0.044 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-SPNC-ER8 | 0.9065 | 0.8625 | -0.044 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-SPNC-ER8 | 0.9065 | 0.8625 | -0.044 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-SPNC-ER8 | 0.9065 | 0.8625 | -0.044 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-SPNC-ER8 | 0.9063 | 0.8626 | -0.0437 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-SPNC-ER8 | 0.9063 | 0.8626 | -0.0437 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-SPNC-ER8 | 0.9063 | 0.8626 | -0.0437 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-SPNC-ER8 | 0.9063 | 0.8626 | -0.0437 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-SPNC-ER8 | 0.9063 | 0.8626 | -0.0437 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-SPNC-ER8 | 0.9063 | 0.8626 | -0.0437 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-SPNC-ER8 | 0.9085 | 0.8665 | -0.042 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-SPNC-ER8 | 0.9085 | 0.8665 | -0.042 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-SPNC-ER8 | 0.9085 | 0.8665 | -0.042 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-SPNC-ER8 | 0.9085 | 0.8665 | -0.042 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-SPNC-ER8 | 0.9085 | 0.8665 | -0.042 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-SPNC-ER8 | 0.9085 | 0.8665 | -0.042 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-SPNC-ER8 | 0.9081 | 0.867 | -0.0411 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-SPNC-ER8 | 0.9081 | 0.867 | -0.0411 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-SPNC-ER8 | 0.9081 | 0.867 | -0.0411 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-SPNC-ER8 | 0.9081 | 0.867 | -0.0411 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-SPNC-ER8 | 0.9081 | 0.867 | -0.0411 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-SPNC-ER8 | 0.9081 | 0.867 | -0.0411 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-SPNC-ER8 | 0.9085 | 0.867 | -0.0415 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-SPNC-ER8 | 0.9085 | 0.867 | -0.0415 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-SPNC-ER8 | 0.9085 | 0.867 | -0.0415 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-SPNC-ER8 | 0.9085 | 0.867 | -0.0415 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-SPNC-ER8 | 0.9085 | 0.867 | -0.0415 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-SPNC-ER8 | 0.9085 | 0.867 | -0.0415 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-SPNC-ER8 | 0.9088 | 0.8679 | -0.0409 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-SPNC-ER8 | 0.9088 | 0.8679 | -0.0409 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-SPNC-ER8 | 0.9088 | 0.8679 | -0.0409 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-SPNC-ER8 | 0.9088 | 0.8679 | -0.0409 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-SPNC-ER8 | 0.9088 | 0.8679 | -0.0409 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-SPNC-ER8 | 0.9088 | 0.8679 | -0.0409 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SALEM-ER8 | 0.9147 | 0.8747 | -0.04 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SALEM-ER8 | 0.9147 | 0.8747 | -0.04 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SALEM-ER8 | 0.9147 | 0.8747 | -0.04 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SALEM-ER8 | 0.9147 | 0.8747 | -0.04 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SALEM-ER8 | 0.9147 | 0.8747 | -0.04 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SALEM-ER8 | 0.9147 | 0.8747 | -0.04 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SALEM-ER8 | 0.9157 | 0.8765 | -0.0392 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SALEM-ER8 | 0.9157 | 0.8765 | -0.0392 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SALEM-ER8 | 0.9157 | 0.8765 | -0.0392 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SALEM-ER8 | 0.9157 | 0.8765 | -0.0392 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SALEM-ER8 | 0.9157 | 0.8765 | -0.0392 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SALEM-ER8 | 0.9157 | 0.8765 | -0.0392 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MOS-SPNC-ER8 | 0.9095 | 0.8691 | -0.0404 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MOS-SPNC-ER8 | 0.9095 | 0.8691 | -0.0404 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MOS-SPNC-ER8 | 0.9095 | 0.8691 | -0.0404 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MOS-SPNC-ER8 | 0.9095 | 0.8691 | -0.0404 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MOS-SPNC-ER8 | 0.9095 | 0.8691 | -0.0404 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MOS-SPNC-ER8 | 0.9095 | 0.8691 | -0.0404 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-SPNC-ER8 | 0.9105 | 0.8702 | -0.0403 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-SPNC-ER8 | 0.9105 | 0.8702 | -0.0403 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-SPNC-ER8 | 0.9105 | 0.8702 | -0.0403 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-SPNC-ER8 | 0.9105 | 0.8702 | -0.0403 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-SPNC-ER8 | 0.9105 | 0.8702 | -0.0403 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-SPNC-ER8 | 0.9105 | 0.8702 | -0.0403 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SALEM-ER8 | 0.916 | 0.877 | -0.039 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SALEM-ER8 | 0.916 | 0.877 | -0.039 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SALEM-ER8 | 0.916 | 0.877 | -0.039 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SALEM-ER8 | 0.916 | 0.877 | -0.039 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SALEM-ER8 | 0.916 | 0.877 | -0.039 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SALEM-ER8 | 0.916 | 0.877 | -0.039 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SHINDLER-ER7 | 0.9246 | 0.8884 | -0.0362 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SHINDLER-ER7 | 0.9246 | 0.8884 | -0.0362 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SHINDLER-ER7 | 0.9246 | 0.8884 | -0.0362 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SHINDLER-ER7 | 0.9246 | 0.8884 | -0.0362 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SHINDLER-ER7 | 0.9246 | 0.8884 | -0.0362 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SHINDLER-ER7 | 0.9246 | 0.8884 | -0.0362 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SHINDLER-ER7 | 0.9244 | 0.8886 | -0.0358 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SHINDLER-ER7 | 0.9244 | 0.8886 | -0.0358 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SHINDLER-ER7 | 0.9244 | 0.8886 | -0.0358 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SHINDLER-ER7 | 0.9244 | 0.8886 | -0.0358 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SHINDLER-ER7 | 0.9244 | 0.8886 | -0.0358 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SHINDLER-ER7 | 0.9244 | 0.8886 | -0.0358 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-SPNC-ER8 | 0.9114 | 0.8719 | -0.0395 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-SPNC-ER8 | 0.9114 | 0.8719 | -0.0395 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-SPNC-ER8 | 0.9114 | 0.8719 | -0.0395 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-SPNC-ER8 | 0.9114 | 0.8719 | -0.0395 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-SPNC-ER8 | 0.9114 | 0.8719 | -0.0395 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-SPNC-ER8 | 0.9114 | 0.8719 | -0.0395 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SHINDLER-ER7 | 0.9253 | 0.8907 | -0.0346 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SHINDLER-ER7 | 0.9253 | 0.8907 | -0.0346 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SHINDLER-ER7 | 0.9253 | 0.8907 | -0.0346 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SHINDLER-ER7 | 0.9253 | 0.8907 | -0.0346 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SHINDLER-ER7 | 0.9253 | 0.8907 | -0.0346 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SHINDLER-ER7 | 0.9253 | 0.8907 | -0.0346 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SHINDLER-ER7 | 0.926 | 0.8916 | -0.0344 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SHINDLER-ER7 | 0.926 | 0.8916 | -0.0344 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SHINDLER-ER7 | 0.926 | 0.8916 | -0.0344 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SHINDLER-ER7 | 0.926 | 0.8916 | -0.0344 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SHINDLER-ER7 | 0.926 | 0.8916 | -0.0344 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SHINDLER-ER7 | 0.926 | 0.8916 | -0.0344 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SHINDLER-ER7 | 0.9266 | 0.8926 | -0.034 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SHINDLER-ER7 | 0.9266 | 0.8926 | -0.034 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SHINDLER-ER7 | 0.9266 | 0.8926 | -0.034 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SHINDLER-ER7 | 0.9266 | 0.8926 | -0.034 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SHINDLER-ER7 | 0.9266 | 0.8926 | -0.034 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SHINDLER-ER7 | 0.9266 | 0.8926 | -0.034 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW1142-ER8 | 0.9175 | 0.8744 | -0.0431 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW1142-ER8 | 0.9175 | 0.8744 | -0.0431 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW1142-ER8 | 0.9175 | 0.8744 | -0.0431 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW1142-ER8 | 0.9175 | 0.8744 | -0.0431 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW1142-ER8 | 0.9175 | 0.8744 | -0.0431 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW1142-ER8 | 0.9175 | 0.8744 | -0.0431 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW1142-ER8 | 0.9173 | 0.8745 | -0.0428 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW1142-ER8 | 0.9173 | 0.8745 | -0.0428 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW1142-ER8 | 0.9173 | 0.8745 | -0.0428 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW1142-ER8 | 0.9173 | 0.8745 | -0.0428 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW1142-ER8 | 0.9173 | 0.8745 | -0.0428 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW1142-ER8 | 0.9173 | 0.8745 | -0.0428 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW1142-ER8 | 0.919 | 0.8787 | -0.0403 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW1142-ER8 | 0.919 | 0.8787 | -0.0403 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW1142-ER8 | 0.919 | 0.8787 | -0.0403 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW1142-ER8 | 0.919 | 0.8787 | -0.0403 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW1142-ER8 | 0.919 | 0.8787 | -0.0403 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW1142-ER8 | 0.919 | 0.8787 | -0.0403 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW1142-ER8 | 0.9199 | 0.8788 | -0.0411 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW1142-ER8 | 0.9199 | 0.8788 | -0.0411 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW1142-ER8 | 0.9199 | 0.8788 | -0.0411 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW1142-ER8 | 0.9199 | 0.8788 | -0.0411 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW1142-ER8 | 0.9199 | 0.8788 | -0.0411 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW1142-ER8 | 0.9199 | 0.8788 | -0.0411 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW1142-ER8 | 0.9199 | 0.8793 | -0.0406 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW1142-ER8 | 0.9199 | 0.8793 | -0.0406 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW1142-ER8 | 0.9199 | 0.8793 | -0.0406 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW1142-ER8 | 0.9199 | 0.8793 | -0.0406 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW1142-ER8 | 0.9199 | 0.8793 | -0.0406 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW1142-ER8 | 0.9199 | 0.8793 | -0.0406 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW1142-ER8 | 0.9197 | 0.8796 | -0.0401 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW1142-ER8 | 0.9197 | 0.8796 | -0.0401 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW1142-ER8 | 0.9197 | 0.8796 | -0.0401 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW1142-ER8 | 0.9197 | 0.8796 | -0.0401 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW1142-ER8 | 0.9197 | 0.8796 | -0.0401 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW1142-ER8 | 0.9197 | 0.8796 | -0.0401 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW1142-ER8 | 0.9204 | 0.8809 | -0.0395 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW1142-ER8 | 0.9204 | 0.8809 | -0.0395 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW1142-ER8 | 0.9204 | 0.8809 | -0.0395 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW1142-ER8 | 0.9204 | 0.8809 | -0.0395 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW1142-ER8 | 0.9204 | 0.8809 | -0.0395 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW1142-ER8 | 0.9204 | 0.8809 | -0.0395 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW1142-ER8 | 0.9218 | 0.8824 | -0.0394 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW1142-ER8 | 0.9218 | 0.8824 | -0.0394 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW1142-ER8 | 0.9218 | 0.8824 | -0.0394 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW1142-ER8 | 0.9218 | 0.8824 | -0.0394 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW1142-ER8 | 0.9218 | 0.8824 | -0.0394 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW1142-ER8 | 0.9218 | 0.8824 | -0.0394 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MOS-SPNC-ER8 | 0.9117 | 0.8725 | -0.0392 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MOS-SPNC-ER8 | 0.9117 | 0.8725 | -0.0392 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MOS-SPNC-ER8 | 0.9117 | 0.8725 | -0.0392 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MOS-SPNC-ER8 | 0.9117 | 0.8725 | -0.0392 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MOS-SPNC-ER8 | 0.9117 | 0.8725 | -0.0392 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MOS-SPNC-ER8 | 0.9117 | 0.8725 | -0.0392 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MTVERNON-ER8 | 0.9418 | 0.8968 | -0.045 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MTVERNON-ER8 | 0.9418 | 0.8968 | -0.045 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MTVERNON-ER8 | 0.9418 | 0.8968 | -0.045 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MTVERNON-ER8 | 0.9418 | 0.8968 | -0.045 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MTVERNON-ER8 | 0.9418 | 0.8968 | -0.045 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MTVERNON-ER8 | 0.9418 | 0.8968 | -0.045 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | MTVERNON-ER8 | 0.9415 | 0.897 | -0.0445 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | MTVERNON-ER8 | 0.9415 | 0.897 | -0.0445 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | MTVERNON-ER8 | 0.9415 | 0.897 | -0.0445 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | MTVERNON-ER8 | 0.9415 | 0.897 | -0.0445 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | MTVERNON-ER8 | 0.9415 | 0.897 | -0.0445 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | MTVERNON-ER8 | 0.9415 | 0.897 | -0.0445 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | MTVERNON-ER8 | 0.943 | 0.8991 | -0.0439 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | MTVERNON-ER8 | 0.943 | 0.8991 | -0.0439 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | MTVERNON-ER8 | 0.943 | 0.8991 | -0.0439 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | MTVERNON-ER8 | 0.943 | 0.8991 | -0.0439 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | MTVERNON-ER8 | 0.943 | 0.8991 | -0.0439 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | MTVERNON-ER8 | 0.943 | 0.8991 | -0.0439 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW1142-ER8 | 0.9228 | 0.8841 | -0.0387 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW1142-ER8 | 0.9228 | 0.8841 | -0.0387 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW1142-ER8 | 0.9228 | 0.8841 | -0.0387 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW1142-ER8 | 0.9228 | 0.8841 | -0.0387 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW1142-ER8 | 0.9228 | 0.8841 | -0.0387 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW1142-ER8 | 0.9228 | 0.8841 | -0.0387 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW1142-ER8 | 0.9231 | 0.8847 | -0.0384 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW1142-ER8 | 0.9231 | 0.8847 | -0.0384 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW1142-ER8 | 0.9231 | 0.8847 | -0.0384 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW1142-ER8 | 0.9231 | 0.8847 | -0.0384 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW1142-ER8 | 0.9231 | 0.8847 | -0.0384 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW1142-ER8 | 0.9231 | 0.8847 | -0.0384 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW124-ER8 | 0.9101 | 0.8666 | -0.0435 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW124-ER8 | 0.9101 | 0.8666 | -0.0435 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW124-ER8 | 0.9101 | 0.8666 | -0.0435 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW124-ER8 | 0.9101 | 0.8666 | -0.0435 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW124-ER8 | 0.9101 | 0.8666 | -0.0435 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW124-ER8 | 0.9101 | 0.8666 | -0.0435 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW124-ER8 | 0.9099 | 0.8667 | -0.0432 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW124-ER8 | 0.9099 | 0.8667 | -0.0432 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW124-ER8 | 0.9099 | 0.8667 | -0.0432 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW124-ER8 | 0.9099 | 0.8667 | -0.0432 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW124-ER8 | 0.9099 | 0.8667 | -0.0432 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW124-ER8 | 0.9099 | 0.8667 | -0.0432 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW124-ER8 | 0.9117 | 0.8701 | -0.0416 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW124-ER8 | 0.9117 | 0.8701 | -0.0416 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW124-ER8 | 0.9117 | 0.8701 | -0.0416 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW124-ER8 | 0.9117 | 0.8701 | -0.0416 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW124-ER8 | 0.9117 | 0.8701 | -0.0416 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW124-ER8 | 0.9117 | 0.8701 | -0.0416 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW124-ER8 | 0.9117 | 0.8706 | -0.0411 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW124-ER8 | 0.9117 | 0.8706 | -0.0411 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW124-ER8 | 0.9117 | 0.8706 | -0.0411 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW124-ER8 | 0.9117 | 0.8706 | -0.0411 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW124-ER8 | 0.9117 | 0.8706 | -0.0411 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW124-ER8 | 0.9117 | 0.8706 | -0.0411 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | PARKERCI-ER8 | 0.927 | 0.8912 | -0.0358 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | PARKERCI-ER8 | 0.927 | 0.8912 | -0.0358 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | PARKERCI-ER8 | 0.927 | 0.8912 | -0.0358 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | PARKERCI-ER8 | 0.927 | 0.8912 | -0.0358 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | PARKERCI-ER8 | 0.927 | 0.8912 | -0.0358 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | PARKERCI-ER8 | 0.927 | 0.8912 | -0.0358 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | PARKERCI-ER8 | 0.9268 | 0.8914 | -0.0354 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | PARKERCI-ER8 | 0.9268 | 0.8914 | -0.0354 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | PARKERCI-ER8 | 0.9268 | 0.8914 | -0.0354 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | PARKERCI-ER8 | 0.9268 | 0.8914 | -0.0354 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | PARKERCI-ER8 | 0.9268 | 0.8914 | -0.0354 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | PARKERCI-ER8 | 0.9268 | 0.8914 | -0.0354 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | PARKERCI-ER8 | 0.9277 | 0.8935 | -0.0342 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | PARKERCI-ER8 | 0.9277 | 0.8935 | -0.0342 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | PARKERCI-ER8 | 0.9277 | 0.8935 | -0.0342 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | PARKERCI-ER8 | 0.9277 | 0.8935 | -0.0342 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | PARKERCI-ER8 | 0.9277 | 0.8935 | -0.0342 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | PARKERCI-ER8 | 0.9277 | 0.8935 | -0.0342 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW124-ER8 | 0.9117 | 0.871 | -0.0407 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW124-ER8 | 0.9117 | 0.871 | -0.0407 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW124-ER8 | 0.9117 | 0.871 | -0.0407 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW124-ER8 | 0.9117 | 0.871 | -0.0407 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW124-ER8 | 0.9117 | 0.871 | -0.0407 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW124-ER8 | 0.9117 | 0.871 | -0.0407 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | PARKERCI-ER8 | 0.9284 | 0.8944 | -0.034 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | PARKERCI-ER8 | 0.9284 | 0.8944 | -0.034 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | PARKERCI-ER8 | 0.9284 | 0.8944 | -0.034 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | PARKERCI-ER8 | 0.9284 | 0.8944 | -0.034 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | PARKERCI-ER8 | 0.9284 | 0.8944 | -0.034 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | PARKERCI-ER8 | 0.9284 | 0.8944 | -0.034 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | PARKERCI-ER8 | 0.929 | 0.8954 | -0.0336 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | PARKERCI-ER8 | 0.929 | 0.8954 | -0.0336 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | PARKERCI-ER8 | 0.929 | 0.8954 | -0.0336 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | PARKERCI-ER8 | 0.929 | 0.8954 | -0.0336 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | PARKERCI-ER8 | 0.929 | 0.8954 | -0.0336 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | PARKERCI-ER8 | 0.929 | 0.8954 | -0.0336 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW124-ER8 | 0.9124 | 0.8719 | -0.0405 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW124-ER8 | 0.9124 | 0.8719 | -0.0405 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW124-ER8 | 0.9124 | 0.8719 | -0.0405 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW124-ER8 | 0.9124 | 0.8719 | -0.0405 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW124-ER8 | 0.9124 | 0.8719 | -0.0405 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW124-ER8 | 0.9124 | 0.8719 | -0.0405 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW124-ER8 | 0.9131 | 0.8731 | -0.04 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW124-ER8 | 0.9131 | 0.8731 | -0.04 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW124-ER8 | 0.9131 | 0.8731 | -0.04 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW124-ER8 | 0.9131 | 0.8731 | -0.04 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW124-ER8 | 0.9131 | 0.8731 | -0.04 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW124-ER8 | 0.9131 | 0.8731 | -0.04 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW124-ER8 | 0.9137 | 0.8738 | -0.0399 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW124-ER8 | 0.9137 | 0.8738 | -0.0399 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW124-ER8 | 0.9137 | 0.8738 | -0.0399 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW124-ER8 | 0.9137 | 0.8738 | -0.0399 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW124-ER8 | 0.9137 | 0.8738 | -0.0399 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW124-ER8 | 0.9137 | 0.8738 | -0.0399 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | PARKER-ER8 | 0.9294 | 0.8937 | -0.0357 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | PARKER-ER8 | 0.9294 | 0.8937 | -0.0357 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | PARKER-ER8 | 0.9294 | 0.8937 | -0.0357 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | PARKER-ER8 | 0.9294 | 0.8937 | -0.0357 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | PARKER-ER8 | 0.9294 | 0.8937 | -0.0357 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | PARKER-ER8 | 0.9294 | 0.8937 | -0.0357 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW124-ER8 | 0.9146 | 0.8755 | -0.0391 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW124-ER8 | 0.9146 | 0.8755 | -0.0391 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW124-ER8 | 0.9146 | 0.8755 | -0.0391 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW124-ER8 | 0.9146 | 0.8755 | -0.0391 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW124-ER8 | 0.9146 | 0.8755 | -0.0391 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW124-ER8 | 0.9146 | 0.8755 | -0.0391 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW124-ER8 | 0.9149 | 0.8761 | -0.0388 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW124-ER8 | 0.9149 | 0.8761 | -0.0388 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW124-ER8 | 0.9149 | 0.8761 | -0.0388 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW124-ER8 | 0.9149 | 0.8761 | -0.0388 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW124-ER8 | 0.9149 | 0.8761 | -0.0388 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW124-ER8 | 0.9149 | 0.8761 | -0.0388 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW145-ER8 | 0.8983 | 0.8539 | -0.0444 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW145-ER8 | 0.8983 | 0.8539 | -0.0444 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW145-ER8 | 0.8983 | 0.8539 | -0.0444 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW145-ER8 | 0.8983 | 0.8539 | -0.0444 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW145-ER8 | 0.8983 | 0.8539 | -0.0444 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW145-ER8 | 0.8983 | 0.8539 | -0.0444 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW145-ER8 | 0.8981 | 0.8541 | -0.044 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW145-ER8 | 0.8981 | 0.8541 | -0.044 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW145-ER8 | 0.8981 | 0.8541 | -0.044 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW145-ER8 | 0.8981 | 0.8541 | -0.044 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW145-ER8 | 0.8981 | 0.8541 | -0.044 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW145-ER8 | 0.8981 | 0.8541 | -0.044 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW145-ER8 | 0.8997 | 0.8573 | -0.0424 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW145-ER8 | 0.8997 | 0.8573 | -0.0424 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW145-ER8 | 0.8997 | 0.8573 | -0.0424 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW145-ER8 | 0.8997 | 0.8573 | -0.0424 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW145-ER8 | 0.8997 | 0.8573 | -0.0424 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW145-ER8 | 0.8997 | 0.8573 | -0.0424 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW145-ER8 | 0.8997 | 0.8578 | -0.0419 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW145-ER8 | 0.8997 | 0.8578 | -0.0419 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW145-ER8 | 0.8997 | 0.8578 | -0.0419 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW145-ER8 | 0.8997 | 0.8578 | -0.0419 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW145-ER8 | 0.8997 | 0.8578 | -0.0419 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW145-ER8 | 0.8997 | 0.8578 | -0.0419 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | PARKER-ER8 | 0.9292 | 0.8939 | -0.0353 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | PARKER-ER8 | 0.9292 | 0.8939 | -0.0353 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | PARKER-ER8 | 0.9292 | 0.8939 | -0.0353 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | PARKER-ER8 | 0.9292 | 0.8939 | -0.0353 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | PARKER-ER8 | 0.9292 | 0.8939 | -0.0353 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | PARKER-ER8 | 0.9292 | 0.8939 | -0.0353 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW145-ER8 | 0.8998 | 0.8584 | -0.0414 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW145-ER8 | 0.8998 | 0.8584 | -0.0414 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW145-ER8 | 0.8998 | 0.8584 | -0.0414 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW145-ER8 | 0.8998 | 0.8584 | -0.0414 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW145-ER8 | 0.8998 | 0.8584 | -0.0414 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW145-ER8 | 0.8998 | 0.8584 | -0.0414 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW145-ER8 | 0.9006 | 0.8593 | -0.0413 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW145-ER8 | 0.9006 | 0.8593 | -0.0413 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW145-ER8 | 0.9006 | 0.8593 | -0.0413 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW145-ER8 | 0.9006 | 0.8593 | -0.0413 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW145-ER8 | 0.9006 | 0.8593 | -0.0413 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW145-ER8 | 0.9006 | 0.8593 | -0.0413 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW145-ER8 | 0.9013 | 0.8606 | -0.0407 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW145-ER8 | 0.9013 | 0.8606 | -0.0407 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW145-ER8 | 0.9013 | 0.8606 | -0.0407 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW145-ER8 | 0.9013 | 0.8606 | -0.0407 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW145-ER8 | 0.9013 | 0.8606 | -0.0407 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW145-ER8 | 0.9013 | 0.8606 | -0.0407 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW145-ER8 | 0.9016 | 0.861 | -0.0406 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW145-ER8 | 0.9016 | 0.861 | -0.0406 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW145-ER8 | 0.9016 | 0.861 | -0.0406 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW145-ER8 | 0.9016 | 0.861 | -0.0406 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW145-ER8 | 0.9016 | 0.861 | -0.0406 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW145-ER8 | 0.9016 | 0.861 | -0.0406 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW145-ER8 | 0.9026 | 0.8628 | -0.0398 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW145-ER8 | 0.9026 | 0.8628 | -0.0398 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW145-ER8 | 0.9026 | 0.8628 | -0.0398 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW145-ER8 | 0.9026 | 0.8628 | -0.0398 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW145-ER8 | 0.9026 | 0.8628 | -0.0398 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW145-ER8 | 0.9026 | 0.8628 | -0.0398 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW145-ER8 | 0.9029 | 0.8634 | -0.0395 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW145-ER8 | 0.9029 | 0.8634 | -0.0395 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW145-ER8 | 0.9029 | 0.8634 | -0.0395 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW145-ER8 | 0.9029 | 0.8634 | -0.0395 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW145-ER8 | 0.9029 | 0.8634 | -0.0395 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW145-ER8 | 0.9029 | 0.8634 | -0.0395 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | PARKER-ER8 | 0.9301 | 0.8959 | -0.0342 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | PARKER-ER8 | 0.9301 | 0.8959 | -0.0342 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | PARKER-ER8 | 0.9301 | 0.8959 | -0.0342 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | PARKER-ER8 | 0.9301 | 0.8959 | -0.0342 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | PARKER-ER8 | 0.9301 | 0.8959 | -0.0342 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | PARKER-ER8 | 0.9301 | 0.8959 | -0.0342 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW145-ER8 | 0.9253 | 0.8958 | -0.0295 |  | 0.9 | 1.05 | 0.10642 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW145-ER8 | 0.9253 | 0.8958 | -0.0295 |  | 0.9 | 1.05 | 0.24279 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW145-ER8 | 0.9253 | 0.8958 | -0.0295 |  | 0.9 | 1.05 | 0.09958 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW145-ER8 | 0.9253 | 0.8958 | -0.0295 |  | 0.9 | 1.05 | 0.03529 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW145-ER8 | 0.9253 | 0.8958 | -0.0295 |  | 0.9 | 1.05 | 0.0709 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW145-ER8 | 0.9253 | 0.8958 | -0.0295 |  | 0.9 | 1.05 | 0.14646 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW145-ER8 | 0.9253 | 0.8958 | -0.0295 |  | 0.9 | 1.05 | 0.10642 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW145-ER8 | 0.9253 | 0.8958 | -0.0295 |  | 0.9 | 1.05 | 0.24279 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW145-ER8 | 0.9253 | 0.8958 | -0.0295 |  | 0.9 | 1.05 | 0.09958 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW145-ER8 | 0.9253 | 0.8958 | -0.0295 |  | 0.9 | 1.05 | 0.03529 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW145-ER8 | 0.9253 | 0.8958 | -0.0295 |  | 0.9 | 1.05 | 0.0709 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW145-ER8 | 0.9253 | 0.8958 | -0.0295 |  | 0.9 | 1.05 | 0.14646 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW145-ER8 | 0.9253 | 0.8958 | -0.0295 |  | 0.9 | 1.05 | 0.10642 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW145-ER8 | 0.9253 | 0.8958 | -0.0295 |  | 0.9 | 1.05 | 0.24279 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW145-ER8 | 0.9253 | 0.8958 | -0.0295 |  | 0.9 | 1.05 | 0.09958 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW145-ER8 | 0.9253 | 0.8958 | -0.0295 |  | 0.9 | 1.05 | 0.03529 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW145-ER8 | 0.9253 | 0.8958 | -0.0295 |  | 0.9 | 1.05 | 0.0709 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW145-ER8 | 0.9253 | 0.8958 | -0.0295 |  | 0.9 | 1.05 | 0.14646 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | PARKER-ER8 | 0.9308 | 0.8969 | -0.0339 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | PARKER-ER8 | 0.9308 | 0.8969 | -0.0339 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | PARKER-ER8 | 0.9308 | 0.8969 | -0.0339 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | PARKER-ER8 | 0.9308 | 0.8969 | -0.0339 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | PARKER-ER8 | 0.9308 | 0.8969 | -0.0339 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | PARKER-ER8 | 0.9308 | 0.8969 | -0.0339 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | PARKER-ER8 | 0.9314 | 0.8979 | -0.0335 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | PARKER-ER8 | 0.9314 | 0.8979 | -0.0335 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | PARKER-ER8 | 0.9314 | 0.8979 | -0.0335 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | PARKER-ER8 | 0.9314 | 0.8979 | -0.0335 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | PARKER-ER8 | 0.9314 | 0.8979 | -0.0335 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | PARKER-ER8 | 0.9314 | 0.8979 | -0.0335 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW145-ER8 | 0.9254 | 0.8976 | -0.0278 |  | 0.9 | 1.05 | 0.10623 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW145-ER8 | 0.9254 | 0.8976 | -0.0278 |  | 0.9 | 1.05 | 0.24261 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW145-ER8 | 0.9254 | 0.8976 | -0.0278 |  | 0.9 | 1.05 | 0.1005 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW145-ER8 | 0.9254 | 0.8976 | -0.0278 |  | 0.9 | 1.05 | 0.03506 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW145-ER8 | 0.9254 | 0.8976 | -0.0278 |  | 0.9 | 1.05 | 0.07067 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW145-ER8 | 0.9254 | 0.8976 | -0.0278 |  | 0.9 | 1.05 | 0.14607 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | PLANO-ER8 | 0.9274 | 0.8811 | -0.0463 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | PLANO-ER8 | 0.9274 | 0.8811 | -0.0463 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | PLANO-ER8 | 0.9274 | 0.8811 | -0.0463 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | PLANO-ER8 | 0.9274 | 0.8811 | -0.0463 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | PLANO-ER8 | 0.9274 | 0.8811 | -0.0463 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | PLANO-ER8 | 0.9274 | 0.8811 | -0.0463 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW145-ER8 | 0.9254 | 0.8977 | -0.0277 |  | 0.9 | 1.05 | 0.10623 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW145-ER8 | 0.9254 | 0.8977 | -0.0277 |  | 0.9 | 1.05 | 0.24261 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW145-ER8 | 0.9254 | 0.8977 | -0.0277 |  | 0.9 | 1.05 | 0.1005 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW145-ER8 | 0.9254 | 0.8977 | -0.0277 |  | 0.9 | 1.05 | 0.03506 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW145-ER8 | 0.9254 | 0.8977 | -0.0277 |  | 0.9 | 1.05 | 0.07067 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW145-ER8 | 0.9254 | 0.8977 | -0.0277 |  | 0.9 | 1.05 | 0.14607 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW145-ER8 | 0.9254 | 0.8977 | -0.0277 |  | 0.9 | 1.05 | 0.10623 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW145-ER8 | 0.9254 | 0.8977 | -0.0277 |  | 0.9 | 1.05 | 0.24261 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW145-ER8 | 0.9254 | 0.8977 | -0.0277 |  | 0.9 | 1.05 | 0.1005 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW145-ER8 | 0.9254 | 0.8977 | -0.0277 |  | 0.9 | 1.05 | 0.03506 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW145-ER8 | 0.9254 | 0.8977 | -0.0277 |  | 0.9 | 1.05 | 0.07067 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW145-ER8 | 0.9254 | 0.8977 | -0.0277 |  | 0.9 | 1.05 | 0.14607 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | PLANO-ER8 | 0.927 | 0.8813 | -0.0457 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | PLANO-ER8 | 0.927 | 0.8813 | -0.0457 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | PLANO-ER8 | 0.927 | 0.8813 | -0.0457 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | PLANO-ER8 | 0.927 | 0.8813 | -0.0457 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | PLANO-ER8 | 0.927 | 0.8813 | -0.0457 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | PLANO-ER8 | 0.927 | 0.8813 | -0.0457 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW159-ER8 | 0.912 | 0.8685 | -0.0435 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW159-ER8 | 0.912 | 0.8685 | -0.0435 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW159-ER8 | 0.912 | 0.8685 | -0.0435 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW159-ER8 | 0.912 | 0.8685 | -0.0435 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW159-ER8 | 0.912 | 0.8685 | -0.0435 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW159-ER8 | 0.912 | 0.8685 | -0.0435 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW159-ER8 | 0.9118 | 0.8687 | -0.0431 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW159-ER8 | 0.9118 | 0.8687 | -0.0431 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW159-ER8 | 0.9118 | 0.8687 | -0.0431 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW159-ER8 | 0.9118 | 0.8687 | -0.0431 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW159-ER8 | 0.9118 | 0.8687 | -0.0431 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW159-ER8 | 0.9118 | 0.8687 | -0.0431 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW159-ER8 | 0.9143 | 0.8727 | -0.0416 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW159-ER8 | 0.9143 | 0.8727 | -0.0416 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW159-ER8 | 0.9143 | 0.8727 | -0.0416 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW159-ER8 | 0.9143 | 0.8727 | -0.0416 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW159-ER8 | 0.9143 | 0.8727 | -0.0416 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW159-ER8 | 0.9143 | 0.8727 | -0.0416 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW159-ER8 | 0.9135 | 0.8729 | -0.0406 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW159-ER8 | 0.9135 | 0.8729 | -0.0406 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW159-ER8 | 0.9135 | 0.8729 | -0.0406 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW159-ER8 | 0.9135 | 0.8729 | -0.0406 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW159-ER8 | 0.9135 | 0.8729 | -0.0406 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW159-ER8 | 0.9135 | 0.8729 | -0.0406 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW159-ER8 | 0.9143 | 0.8733 | -0.041 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW159-ER8 | 0.9143 | 0.8733 | -0.041 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW159-ER8 | 0.9143 | 0.8733 | -0.041 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW159-ER8 | 0.9143 | 0.8733 | -0.041 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW159-ER8 | 0.9143 | 0.8733 | -0.041 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW159-ER8 | 0.9143 | 0.8733 | -0.041 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW159-ER8 | 0.9143 | 0.8738 | -0.0405 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW159-ER8 | 0.9143 | 0.8738 | -0.0405 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW159-ER8 | 0.9143 | 0.8738 | -0.0405 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW159-ER8 | 0.9143 | 0.8738 | -0.0405 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW159-ER8 | 0.9143 | 0.8738 | -0.0405 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW159-ER8 | 0.9143 | 0.8738 | -0.0405 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | PLANO-ER8 | 0.9283 | 0.8832 | -0.0451 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | PLANO-ER8 | 0.9283 | 0.8832 | -0.0451 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | PLANO-ER8 | 0.9283 | 0.8832 | -0.0451 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | PLANO-ER8 | 0.9283 | 0.8832 | -0.0451 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | PLANO-ER8 | 0.9283 | 0.8832 | -0.0451 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | PLANO-ER8 | 0.9283 | 0.8832 | -0.0451 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW159-ER8 | 0.9149 | 0.8751 | -0.0398 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW159-ER8 | 0.9149 | 0.8751 | -0.0398 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW159-ER8 | 0.9149 | 0.8751 | -0.0398 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW159-ER8 | 0.9149 | 0.8751 | -0.0398 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW159-ER8 | 0.9149 | 0.8751 | -0.0398 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW159-ER8 | 0.9149 | 0.8751 | -0.0398 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | PLANO-ER8 | 0.9283 | 0.8861 | -0.0422 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | PLANO-ER8 | 0.9283 | 0.8861 | -0.0422 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | PLANO-ER8 | 0.9283 | 0.8861 | -0.0422 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | PLANO-ER8 | 0.9283 | 0.8861 | -0.0422 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | PLANO-ER8 | 0.9283 | 0.8861 | -0.0422 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | PLANO-ER8 | 0.9283 | 0.8861 | -0.0422 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | PLANO-ER8 | 0.9303 | 0.8868 | -0.0435 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | PLANO-ER8 | 0.9303 | 0.8868 | -0.0435 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | PLANO-ER8 | 0.9303 | 0.8868 | -0.0435 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | PLANO-ER8 | 0.9303 | 0.8868 | -0.0435 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | PLANO-ER8 | 0.9303 | 0.8868 | -0.0435 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | PLANO-ER8 | 0.9303 | 0.8868 | -0.0435 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW159-ER8 | 0.9162 | 0.8764 | -0.0398 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW159-ER8 | 0.9162 | 0.8764 | -0.0398 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW159-ER8 | 0.9162 | 0.8764 | -0.0398 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW159-ER8 | 0.9162 | 0.8764 | -0.0398 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW159-ER8 | 0.9162 | 0.8764 | -0.0398 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW159-ER8 | 0.9162 | 0.8764 | -0.0398 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | PLANO-ER8 | 0.9289 | 0.8872 | -0.0417 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | PLANO-ER8 | 0.9289 | 0.8872 | -0.0417 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | PLANO-ER8 | 0.9289 | 0.8872 | -0.0417 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | PLANO-ER8 | 0.9289 | 0.8872 | -0.0417 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | PLANO-ER8 | 0.9289 | 0.8872 | -0.0417 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | PLANO-ER8 | 0.9289 | 0.8872 | -0.0417 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | PLANO-ER8 | 0.9303 | 0.8875 | -0.0428 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | PLANO-ER8 | 0.9303 | 0.8875 | -0.0428 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | PLANO-ER8 | 0.9303 | 0.8875 | -0.0428 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | PLANO-ER8 | 0.9303 | 0.8875 | -0.0428 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | PLANO-ER8 | 0.9303 | 0.8875 | -0.0428 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | PLANO-ER8 | 0.9303 | 0.8875 | -0.0428 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | PLANO-ER8 | 0.9313 | 0.8905 | -0.0408 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | PLANO-ER8 | 0.9313 | 0.8905 | -0.0408 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | PLANO-ER8 | 0.9313 | 0.8905 | -0.0408 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | PLANO-ER8 | 0.9313 | 0.8905 | -0.0408 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | PLANO-ER8 | 0.9313 | 0.8905 | -0.0408 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | PLANO-ER8 | 0.9313 | 0.8905 | -0.0408 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | PLANO-ER8 | 0.9328 | 0.8925 | -0.0403 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | PLANO-ER8 | 0.9328 | 0.8925 | -0.0403 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | PLANO-ER8 | 0.9328 | 0.8925 | -0.0403 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | PLANO-ER8 | 0.9328 | 0.8925 | -0.0403 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | PLANO-ER8 | 0.9328 | 0.8925 | -0.0403 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | PLANO-ER8 | 0.9328 | 0.8925 | -0.0403 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW159-ER8 | 0.9171 | 0.8781 | -0.039 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW159-ER8 | 0.9171 | 0.8781 | -0.039 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW159-ER8 | 0.9171 | 0.8781 | -0.039 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW159-ER8 | 0.9171 | 0.8781 | -0.039 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW159-ER8 | 0.9171 | 0.8781 | -0.039 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW159-ER8 | 0.9171 | 0.8781 | -0.039 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW159-ER8 | 0.9174 | 0.8787 | -0.0387 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW159-ER8 | 0.9174 | 0.8787 | -0.0387 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW159-ER8 | 0.9174 | 0.8787 | -0.0387 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW159-ER8 | 0.9174 | 0.8787 | -0.0387 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW159-ER8 | 0.9174 | 0.8787 | -0.0387 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW159-ER8 | 0.9174 | 0.8787 | -0.0387 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW162-ER8 | 0.8963 | 0.8519 | -0.0444 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW162-ER8 | 0.8963 | 0.8519 | -0.0444 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW162-ER8 | 0.8963 | 0.8519 | -0.0444 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW162-ER8 | 0.8963 | 0.8519 | -0.0444 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW162-ER8 | 0.8963 | 0.8519 | -0.0444 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW162-ER8 | 0.8963 | 0.8519 | -0.0444 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | PLANO-ER8 | 0.9331 | 0.893 | -0.0401 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | PLANO-ER8 | 0.9331 | 0.893 | -0.0401 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | PLANO-ER8 | 0.9331 | 0.893 | -0.0401 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | PLANO-ER8 | 0.9331 | 0.893 | -0.0401 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | PLANO-ER8 | 0.9331 | 0.893 | -0.0401 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | PLANO-ER8 | 0.9331 | 0.893 | -0.0401 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SANDCRK-ER8 | 0.933 | 0.8951 | -0.0379 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SANDCRK-ER8 | 0.933 | 0.8951 | -0.0379 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SANDCRK-ER8 | 0.933 | 0.8951 | -0.0379 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SANDCRK-ER8 | 0.933 | 0.8951 | -0.0379 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SANDCRK-ER8 | 0.933 | 0.8951 | -0.0379 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SANDCRK-ER8 | 0.933 | 0.8951 | -0.0379 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SANDCRK-ER8 | 0.9329 | 0.8952 | -0.0377 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SANDCRK-ER8 | 0.9329 | 0.8952 | -0.0377 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SANDCRK-ER8 | 0.9329 | 0.8952 | -0.0377 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SANDCRK-ER8 | 0.9329 | 0.8952 | -0.0377 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SANDCRK-ER8 | 0.9329 | 0.8952 | -0.0377 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SANDCRK-ER8 | 0.9329 | 0.8952 | -0.0377 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SPENCER-ER8 | 0.9065 | 0.8625 | -0.044 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SPENCER-ER8 | 0.9065 | 0.8625 | -0.044 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SPENCER-ER8 | 0.9065 | 0.8625 | -0.044 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SPENCER-ER8 | 0.9065 | 0.8625 | -0.044 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SPENCER-ER8 | 0.9065 | 0.8625 | -0.044 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SPENCER-ER8 | 0.9065 | 0.8625 | -0.044 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SPENCER-ER8 | 0.9063 | 0.8626 | -0.0437 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SPENCER-ER8 | 0.9063 | 0.8626 | -0.0437 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SPENCER-ER8 | 0.9063 | 0.8626 | -0.0437 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SPENCER-ER8 | 0.9063 | 0.8626 | -0.0437 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SPENCER-ER8 | 0.9063 | 0.8626 | -0.0437 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SPENCER-ER8 | 0.9063 | 0.8626 | -0.0437 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SPENCER-ER8 | 0.9085 | 0.8665 | -0.042 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SPENCER-ER8 | 0.9085 | 0.8665 | -0.042 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SPENCER-ER8 | 0.9085 | 0.8665 | -0.042 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SPENCER-ER8 | 0.9085 | 0.8665 | -0.042 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SPENCER-ER8 | 0.9085 | 0.8665 | -0.042 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SPENCER-ER8 | 0.9085 | 0.8665 | -0.042 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SPENCER-ER8 | 0.908 | 0.8669 | -0.0411 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SPENCER-ER8 | 0.908 | 0.8669 | -0.0411 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SPENCER-ER8 | 0.908 | 0.8669 | -0.0411 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SPENCER-ER8 | 0.908 | 0.8669 | -0.0411 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SPENCER-ER8 | 0.908 | 0.8669 | -0.0411 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SPENCER-ER8 | 0.908 | 0.8669 | -0.0411 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SPENCER-ER8 | 0.9085 | 0.867 | -0.0415 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SPENCER-ER8 | 0.9085 | 0.867 | -0.0415 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SPENCER-ER8 | 0.9085 | 0.867 | -0.0415 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SPENCER-ER8 | 0.9085 | 0.867 | -0.0415 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SPENCER-ER8 | 0.9085 | 0.867 | -0.0415 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SPENCER-ER8 | 0.9085 | 0.867 | -0.0415 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW162-ER8 | 0.8961 | 0.852 | -0.0441 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW162-ER8 | 0.8961 | 0.852 | -0.0441 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW162-ER8 | 0.8961 | 0.852 | -0.0441 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW162-ER8 | 0.8961 | 0.852 | -0.0441 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW162-ER8 | 0.8961 | 0.852 | -0.0441 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW162-ER8 | 0.8961 | 0.852 | -0.0441 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW162-ER8 | 0.8977 | 0.8552 | -0.0425 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW162-ER8 | 0.8977 | 0.8552 | -0.0425 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW162-ER8 | 0.8977 | 0.8552 | -0.0425 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW162-ER8 | 0.8977 | 0.8552 | -0.0425 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW162-ER8 | 0.8977 | 0.8552 | -0.0425 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW162-ER8 | 0.8977 | 0.8552 | -0.0425 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW162-ER8 | 0.8977 | 0.8557 | -0.042 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW162-ER8 | 0.8977 | 0.8557 | -0.042 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW162-ER8 | 0.8977 | 0.8557 | -0.042 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW162-ER8 | 0.8977 | 0.8557 | -0.042 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW162-ER8 | 0.8977 | 0.8557 | -0.042 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW162-ER8 | 0.8977 | 0.8557 | -0.042 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW162-ER8 | 0.8979 | 0.8564 | -0.0415 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW162-ER8 | 0.8979 | 0.8564 | -0.0415 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW162-ER8 | 0.8979 | 0.8564 | -0.0415 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW162-ER8 | 0.8979 | 0.8564 | -0.0415 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW162-ER8 | 0.8979 | 0.8564 | -0.0415 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW162-ER8 | 0.8979 | 0.8564 | -0.0415 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW162-ER8 | 0.8986 | 0.8573 | -0.0413 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW162-ER8 | 0.8986 | 0.8573 | -0.0413 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW162-ER8 | 0.8986 | 0.8573 | -0.0413 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW162-ER8 | 0.8986 | 0.8573 | -0.0413 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW162-ER8 | 0.8986 | 0.8573 | -0.0413 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW162-ER8 | 0.8986 | 0.8573 | -0.0413 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SPENCER-ER8 | 0.9088 | 0.8678 | -0.041 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SPENCER-ER8 | 0.9088 | 0.8678 | -0.041 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SPENCER-ER8 | 0.9088 | 0.8678 | -0.041 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SPENCER-ER8 | 0.9088 | 0.8678 | -0.041 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SPENCER-ER8 | 0.9088 | 0.8678 | -0.041 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SPENCER-ER8 | 0.9088 | 0.8678 | -0.041 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SPENCER-ER8 | 0.9094 | 0.8691 | -0.0403 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SPENCER-ER8 | 0.9094 | 0.8691 | -0.0403 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SPENCER-ER8 | 0.9094 | 0.8691 | -0.0403 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SPENCER-ER8 | 0.9094 | 0.8691 | -0.0403 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SPENCER-ER8 | 0.9094 | 0.8691 | -0.0403 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SPENCER-ER8 | 0.9094 | 0.8691 | -0.0403 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SPENCER-ER8 | 0.9104 | 0.8701 | -0.0403 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SPENCER-ER8 | 0.9104 | 0.8701 | -0.0403 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SPENCER-ER8 | 0.9104 | 0.8701 | -0.0403 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SPENCER-ER8 | 0.9104 | 0.8701 | -0.0403 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SPENCER-ER8 | 0.9104 | 0.8701 | -0.0403 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SPENCER-ER8 | 0.9104 | 0.8701 | -0.0403 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW162-ER8 | 0.8993 | 0.8586 | -0.0407 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW162-ER8 | 0.8993 | 0.8586 | -0.0407 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW162-ER8 | 0.8993 | 0.8586 | -0.0407 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW162-ER8 | 0.8993 | 0.8586 | -0.0407 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW162-ER8 | 0.8993 | 0.8586 | -0.0407 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW162-ER8 | 0.8993 | 0.8586 | -0.0407 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW162-ER8 | 0.8996 | 0.8589 | -0.0407 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW162-ER8 | 0.8996 | 0.8589 | -0.0407 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW162-ER8 | 0.8996 | 0.8589 | -0.0407 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW162-ER8 | 0.8996 | 0.8589 | -0.0407 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW162-ER8 | 0.8996 | 0.8589 | -0.0407 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW162-ER8 | 0.8996 | 0.8589 | -0.0407 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW162-ER8 | 0.9006 | 0.8607 | -0.0399 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW162-ER8 | 0.9006 | 0.8607 | -0.0399 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW162-ER8 | 0.9006 | 0.8607 | -0.0399 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW162-ER8 | 0.9006 | 0.8607 | -0.0399 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW162-ER8 | 0.9006 | 0.8607 | -0.0399 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW162-ER8 | 0.9006 | 0.8607 | -0.0399 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW162-ER8 | 0.9009 | 0.8613 | -0.0396 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW162-ER8 | 0.9009 | 0.8613 | -0.0396 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW162-ER8 | 0.9009 | 0.8613 | -0.0396 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW162-ER8 | 0.9009 | 0.8613 | -0.0396 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW162-ER8 | 0.9009 | 0.8613 | -0.0396 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW162-ER8 | 0.9009 | 0.8613 | -0.0396 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SPENCER-ER8 | 0.9114 | 0.8719 | -0.0395 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SPENCER-ER8 | 0.9114 | 0.8719 | -0.0395 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SPENCER-ER8 | 0.9114 | 0.8719 | -0.0395 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SPENCER-ER8 | 0.9114 | 0.8719 | -0.0395 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SPENCER-ER8 | 0.9114 | 0.8719 | -0.0395 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SPENCER-ER8 | 0.9114 | 0.8719 | -0.0395 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW162-ER8 | 0.9234 | 0.8938 | -0.0296 |  | 0.9 | 1.05 | 0.10642 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW162-ER8 | 0.9234 | 0.8938 | -0.0296 |  | 0.9 | 1.05 | 0.24279 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW162-ER8 | 0.9234 | 0.8938 | -0.0296 |  | 0.9 | 1.05 | 0.09958 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW162-ER8 | 0.9234 | 0.8938 | -0.0296 |  | 0.9 | 1.05 | 0.03529 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW162-ER8 | 0.9234 | 0.8938 | -0.0296 |  | 0.9 | 1.05 | 0.0709 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW162-ER8 | 0.9234 | 0.8938 | -0.0296 |  | 0.9 | 1.05 | 0.14646 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SPENCER-ER8 | 0.9117 | 0.8725 | -0.0392 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SPENCER-ER8 | 0.9117 | 0.8725 | -0.0392 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SPENCER-ER8 | 0.9117 | 0.8725 | -0.0392 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SPENCER-ER8 | 0.9117 | 0.8725 | -0.0392 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SPENCER-ER8 | 0.9117 | 0.8725 | -0.0392 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SPENCER-ER8 | 0.9117 | 0.8725 | -0.0392 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SUNDOWN-ER7 | 0.9349 | 0.8993 | -0.0356 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SUNDOWN-ER7 | 0.9349 | 0.8993 | -0.0356 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SUNDOWN-ER7 | 0.9349 | 0.8993 | -0.0356 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SUNDOWN-ER7 | 0.9349 | 0.8993 | -0.0356 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SUNDOWN-ER7 | 0.9349 | 0.8993 | -0.0356 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SUNDOWN-ER7 | 0.9349 | 0.8993 | -0.0356 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SUNDOWN-ER7 | 0.9347 | 0.8994 | -0.0353 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SUNDOWN-ER7 | 0.9347 | 0.8994 | -0.0353 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SUNDOWN-ER7 | 0.9347 | 0.8994 | -0.0353 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SUNDOWN-ER7 | 0.9347 | 0.8994 | -0.0353 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SUNDOWN-ER7 | 0.9347 | 0.8994 | -0.0353 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SUNDOWN-ER7 | 0.9347 | 0.8994 | -0.0353 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW130-ER8 | 0.9107 | 0.8669 | -0.0438 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW130-ER8 | 0.9107 | 0.8669 | -0.0438 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW130-ER8 | 0.9107 | 0.8669 | -0.0438 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW130-ER8 | 0.9107 | 0.8669 | -0.0438 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW130-ER8 | 0.9107 | 0.8669 | -0.0438 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW130-ER8 | 0.9107 | 0.8669 | -0.0438 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW130-ER8 | 0.9105 | 0.8671 | -0.0434 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW130-ER8 | 0.9105 | 0.8671 | -0.0434 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW130-ER8 | 0.9105 | 0.8671 | -0.0434 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW130-ER8 | 0.9105 | 0.8671 | -0.0434 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW130-ER8 | 0.9105 | 0.8671 | -0.0434 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW130-ER8 | 0.9105 | 0.8671 | -0.0434 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW130-ER8 | 0.9123 | 0.8714 | -0.0409 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW130-ER8 | 0.9123 | 0.8714 | -0.0409 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW130-ER8 | 0.9123 | 0.8714 | -0.0409 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW130-ER8 | 0.9123 | 0.8714 | -0.0409 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW130-ER8 | 0.9123 | 0.8714 | -0.0409 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW130-ER8 | 0.9123 | 0.8714 | -0.0409 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW130-ER8 | 0.9135 | 0.8717 | -0.0418 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW130-ER8 | 0.9135 | 0.8717 | -0.0418 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW130-ER8 | 0.9135 | 0.8717 | -0.0418 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW130-ER8 | 0.9135 | 0.8717 | -0.0418 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW130-ER8 | 0.9135 | 0.8717 | -0.0418 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW130-ER8 | 0.9135 | 0.8717 | -0.0418 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW130-ER8 | 0.9135 | 0.8722 | -0.0413 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW130-ER8 | 0.9135 | 0.8722 | -0.0413 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW130-ER8 | 0.9135 | 0.8722 | -0.0413 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW130-ER8 | 0.9135 | 0.8722 | -0.0413 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW130-ER8 | 0.9135 | 0.8722 | -0.0413 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW130-ER8 | 0.9135 | 0.8722 | -0.0413 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW162-ER8 | 0.9234 | 0.8938 | -0.0296 |  | 0.9 | 1.05 | 0.10642 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW162-ER8 | 0.9234 | 0.8938 | -0.0296 |  | 0.9 | 1.05 | 0.24279 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW162-ER8 | 0.9234 | 0.8938 | -0.0296 |  | 0.9 | 1.05 | 0.09958 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW162-ER8 | 0.9234 | 0.8938 | -0.0296 |  | 0.9 | 1.05 | 0.03529 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW162-ER8 | 0.9234 | 0.8938 | -0.0296 |  | 0.9 | 1.05 | 0.0709 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW162-ER8 | 0.9234 | 0.8938 | -0.0296 |  | 0.9 | 1.05 | 0.14646 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW162-ER8 | 0.9234 | 0.8938 | -0.0296 |  | 0.9 | 1.05 | 0.10642 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW162-ER8 | 0.9234 | 0.8938 | -0.0296 |  | 0.9 | 1.05 | 0.24279 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW162-ER8 | 0.9234 | 0.8938 | -0.0296 |  | 0.9 | 1.05 | 0.09958 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW162-ER8 | 0.9234 | 0.8938 | -0.0296 |  | 0.9 | 1.05 | 0.03529 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW162-ER8 | 0.9234 | 0.8938 | -0.0296 |  | 0.9 | 1.05 | 0.0709 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW162-ER8 | 0.9234 | 0.8938 | -0.0296 |  | 0.9 | 1.05 | 0.14646 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW130-ER8 | 0.913 | 0.8723 | -0.0407 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW130-ER8 | 0.913 | 0.8723 | -0.0407 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW130-ER8 | 0.913 | 0.8723 | -0.0407 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW130-ER8 | 0.913 | 0.8723 | -0.0407 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW130-ER8 | 0.913 | 0.8723 | -0.0407 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW130-ER8 | 0.913 | 0.8723 | -0.0407 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW130-ER8 | 0.9137 | 0.8735 | -0.0402 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW130-ER8 | 0.9137 | 0.8735 | -0.0402 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW130-ER8 | 0.9137 | 0.8735 | -0.0402 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW130-ER8 | 0.9137 | 0.8735 | -0.0402 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW130-ER8 | 0.9137 | 0.8735 | -0.0402 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW130-ER8 | 0.9137 | 0.8735 | -0.0402 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW130-ER8 | 0.9154 | 0.8754 | -0.04 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW130-ER8 | 0.9154 | 0.8754 | -0.04 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW130-ER8 | 0.9154 | 0.8754 | -0.04 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW130-ER8 | 0.9154 | 0.8754 | -0.04 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW130-ER8 | 0.9154 | 0.8754 | -0.04 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW130-ER8 | 0.9154 | 0.8754 | -0.04 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW162-ER8 | 0.9235 | 0.8956 | -0.0279 |  | 0.9 | 1.05 | 0.10623 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW162-ER8 | 0.9235 | 0.8956 | -0.0279 |  | 0.9 | 1.05 | 0.24261 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW162-ER8 | 0.9235 | 0.8956 | -0.0279 |  | 0.9 | 1.05 | 0.1005 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW162-ER8 | 0.9235 | 0.8956 | -0.0279 |  | 0.9 | 1.05 | 0.03506 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW162-ER8 | 0.9235 | 0.8956 | -0.0279 |  | 0.9 | 1.05 | 0.07067 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW162-ER8 | 0.9235 | 0.8956 | -0.0279 |  | 0.9 | 1.05 | 0.14607 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW162-ER8 | 0.9235 | 0.8956 | -0.0279 |  | 0.9 | 1.05 | 0.10623 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW162-ER8 | 0.9235 | 0.8956 | -0.0279 |  | 0.9 | 1.05 | 0.24261 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW162-ER8 | 0.9235 | 0.8956 | -0.0279 |  | 0.9 | 1.05 | 0.1005 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW162-ER8 | 0.9235 | 0.8956 | -0.0279 |  | 0.9 | 1.05 | 0.03506 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW162-ER8 | 0.9235 | 0.8956 | -0.0279 |  | 0.9 | 1.05 | 0.07067 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW162-ER8 | 0.9235 | 0.8956 | -0.0279 |  | 0.9 | 1.05 | 0.14607 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW162-ER8 | 0.9235 | 0.8956 | -0.0279 |  | 0.9 | 1.05 | 0.10623 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW162-ER8 | 0.9235 | 0.8956 | -0.0279 |  | 0.9 | 1.05 | 0.24261 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW162-ER8 | 0.9235 | 0.8956 | -0.0279 |  | 0.9 | 1.05 | 0.1005 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW162-ER8 | 0.9235 | 0.8956 | -0.0279 |  | 0.9 | 1.05 | 0.03506 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW162-ER8 | 0.9235 | 0.8956 | -0.0279 |  | 0.9 | 1.05 | 0.07067 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW162-ER8 | 0.9235 | 0.8956 | -0.0279 |  | 0.9 | 1.05 | 0.14607 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW130-ER8 | 0.9163 | 0.8771 | -0.0392 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW130-ER8 | 0.9163 | 0.8771 | -0.0392 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW130-ER8 | 0.9163 | 0.8771 | -0.0392 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW130-ER8 | 0.9163 | 0.8771 | -0.0392 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW130-ER8 | 0.9163 | 0.8771 | -0.0392 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW130-ER8 | 0.9163 | 0.8771 | -0.0392 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW130-ER8 | 0.9166 | 0.8777 | -0.0389 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW130-ER8 | 0.9166 | 0.8777 | -0.0389 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW130-ER8 | 0.9166 | 0.8777 | -0.0389 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW130-ER8 | 0.9166 | 0.8777 | -0.0389 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW130-ER8 | 0.9166 | 0.8777 | -0.0389 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW130-ER8 | 0.9166 | 0.8777 | -0.0389 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW144-ER8 | 0.8883 | 0.8427 | -0.0456 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW144-ER8 | 0.8883 | 0.8427 | -0.0456 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW144-ER8 | 0.8883 | 0.8427 | -0.0456 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW144-ER8 | 0.8883 | 0.8427 | -0.0456 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW144-ER8 | 0.8883 | 0.8427 | -0.0456 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW144-ER8 | 0.8883 | 0.8427 | -0.0456 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW144-ER8 | 0.8881 | 0.8429 | -0.0452 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW144-ER8 | 0.8881 | 0.8429 | -0.0452 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW144-ER8 | 0.8881 | 0.8429 | -0.0452 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW144-ER8 | 0.8881 | 0.8429 | -0.0452 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW144-ER8 | 0.8881 | 0.8429 | -0.0452 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW144-ER8 | 0.8881 | 0.8429 | -0.0452 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW144-ER8 | 0.8899 | 0.8474 | -0.0425 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW144-ER8 | 0.8899 | 0.8474 | -0.0425 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW144-ER8 | 0.8899 | 0.8474 | -0.0425 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW144-ER8 | 0.8899 | 0.8474 | -0.0425 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW144-ER8 | 0.8899 | 0.8474 | -0.0425 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW144-ER8 | 0.8899 | 0.8474 | -0.0425 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW144-ER8 | 0.8907 | 0.8483 | -0.0424 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW144-ER8 | 0.8907 | 0.8483 | -0.0424 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW144-ER8 | 0.8907 | 0.8483 | -0.0424 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW144-ER8 | 0.8907 | 0.8483 | -0.0424 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW144-ER8 | 0.8907 | 0.8483 | -0.0424 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW144-ER8 | 0.8907 | 0.8483 | -0.0424 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW144-ER8 | 0.892 | 0.8486 | -0.0434 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW144-ER8 | 0.892 | 0.8486 | -0.0434 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW144-ER8 | 0.892 | 0.8486 | -0.0434 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW144-ER8 | 0.892 | 0.8486 | -0.0434 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW144-ER8 | 0.892 | 0.8486 | -0.0434 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW144-ER8 | 0.892 | 0.8486 | -0.0434 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW144-ER8 | 0.892 | 0.8492 | -0.0428 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW144-ER8 | 0.892 | 0.8492 | -0.0428 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW144-ER8 | 0.892 | 0.8492 | -0.0428 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW144-ER8 | 0.892 | 0.8492 | -0.0428 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW144-ER8 | 0.892 | 0.8492 | -0.0428 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW144-ER8 | 0.892 | 0.8492 | -0.0428 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW144-ER8 | 0.8914 | 0.8496 | -0.0418 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW144-ER8 | 0.8914 | 0.8496 | -0.0418 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW144-ER8 | 0.8914 | 0.8496 | -0.0418 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW144-ER8 | 0.8914 | 0.8496 | -0.0418 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW144-ER8 | 0.8914 | 0.8496 | -0.0418 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW144-ER8 | 0.8914 | 0.8496 | -0.0418 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW144-ER8 | 0.894 | 0.8524 | -0.0416 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW144-ER8 | 0.894 | 0.8524 | -0.0416 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW144-ER8 | 0.894 | 0.8524 | -0.0416 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW144-ER8 | 0.894 | 0.8524 | -0.0416 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW144-ER8 | 0.894 | 0.8524 | -0.0416 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW144-ER8 | 0.894 | 0.8524 | -0.0416 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW144-ER8 | 0.895 | 0.8542 | -0.0408 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW144-ER8 | 0.895 | 0.8542 | -0.0408 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW144-ER8 | 0.895 | 0.8542 | -0.0408 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW144-ER8 | 0.895 | 0.8542 | -0.0408 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW144-ER8 | 0.895 | 0.8542 | -0.0408 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW144-ER8 | 0.895 | 0.8542 | -0.0408 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW144-ER8 | 0.8953 | 0.8548 | -0.0405 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW144-ER8 | 0.8953 | 0.8548 | -0.0405 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW144-ER8 | 0.8953 | 0.8548 | -0.0405 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW144-ER8 | 0.8953 | 0.8548 | -0.0405 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW144-ER8 | 0.8953 | 0.8548 | -0.0405 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW144-ER8 | 0.8953 | 0.8548 | -0.0405 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW144-ER8 | 0.9159 | 0.8857 | -0.0302 |  | 0.9 | 1.05 | 0.10642 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW144-ER8 | 0.9159 | 0.8857 | -0.0302 |  | 0.9 | 1.05 | 0.24279 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW144-ER8 | 0.9159 | 0.8857 | -0.0302 |  | 0.9 | 1.05 | 0.09958 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW144-ER8 | 0.9159 | 0.8857 | -0.0302 |  | 0.9 | 1.05 | 0.03529 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW144-ER8 | 0.9159 | 0.8857 | -0.0302 |  | 0.9 | 1.05 | 0.0709 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW144-ER8 | 0.9159 | 0.8857 | -0.0302 |  | 0.9 | 1.05 | 0.14646 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW170-ER8 | 0.9156 | 0.8724 | -0.0432 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW170-ER8 | 0.9156 | 0.8724 | -0.0432 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW170-ER8 | 0.9156 | 0.8724 | -0.0432 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW170-ER8 | 0.9156 | 0.8724 | -0.0432 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW170-ER8 | 0.9156 | 0.8724 | -0.0432 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW170-ER8 | 0.9156 | 0.8724 | -0.0432 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW170-ER8 | 0.9154 | 0.8726 | -0.0428 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW170-ER8 | 0.9154 | 0.8726 | -0.0428 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW170-ER8 | 0.9154 | 0.8726 | -0.0428 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW170-ER8 | 0.9154 | 0.8726 | -0.0428 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW170-ER8 | 0.9154 | 0.8726 | -0.0428 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW170-ER8 | 0.9154 | 0.8726 | -0.0428 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW144-ER8 | 0.9159 | 0.8857 | -0.0302 |  | 0.9 | 1.05 | 0.10642 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW144-ER8 | 0.9159 | 0.8857 | -0.0302 |  | 0.9 | 1.05 | 0.24279 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW144-ER8 | 0.9159 | 0.8857 | -0.0302 |  | 0.9 | 1.05 | 0.09958 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW144-ER8 | 0.9159 | 0.8857 | -0.0302 |  | 0.9 | 1.05 | 0.03529 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW144-ER8 | 0.9159 | 0.8857 | -0.0302 |  | 0.9 | 1.05 | 0.0709 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW144-ER8 | 0.9159 | 0.8857 | -0.0302 |  | 0.9 | 1.05 | 0.14646 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW144-ER8 | 0.9159 | 0.8857 | -0.0302 |  | 0.9 | 1.05 | 0.10642 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW144-ER8 | 0.9159 | 0.8857 | -0.0302 |  | 0.9 | 1.05 | 0.24279 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW144-ER8 | 0.9159 | 0.8857 | -0.0302 |  | 0.9 | 1.05 | 0.09958 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW144-ER8 | 0.9159 | 0.8857 | -0.0302 |  | 0.9 | 1.05 | 0.03529 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW144-ER8 | 0.9159 | 0.8857 | -0.0302 |  | 0.9 | 1.05 | 0.0709 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW144-ER8 | 0.9159 | 0.8857 | -0.0302 |  | 0.9 | 1.05 | 0.14646 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW144-ER8 | 0.9183 | 0.8899 | -0.0284 |  | 0.9 | 1.05 | 0.10623 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW144-ER8 | 0.9183 | 0.8899 | -0.0284 |  | 0.9 | 1.05 | 0.24261 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW144-ER8 | 0.9183 | 0.8899 | -0.0284 |  | 0.9 | 1.05 | 0.1005 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW144-ER8 | 0.9183 | 0.8899 | -0.0284 |  | 0.9 | 1.05 | 0.03506 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW144-ER8 | 0.9183 | 0.8899 | -0.0284 |  | 0.9 | 1.05 | 0.07067 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW144-ER8 | 0.9183 | 0.8899 | -0.0284 |  | 0.9 | 1.05 | 0.14607 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW144-ER8 | 0.9183 | 0.8899 | -0.0284 |  | 0.9 | 1.05 | 0.10623 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW144-ER8 | 0.9183 | 0.8899 | -0.0284 |  | 0.9 | 1.05 | 0.24261 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW144-ER8 | 0.9183 | 0.8899 | -0.0284 |  | 0.9 | 1.05 | 0.1005 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW144-ER8 | 0.9183 | 0.8899 | -0.0284 |  | 0.9 | 1.05 | 0.03506 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW144-ER8 | 0.9183 | 0.8899 | -0.0284 |  | 0.9 | 1.05 | 0.07067 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW144-ER8 | 0.9183 | 0.8899 | -0.0284 |  | 0.9 | 1.05 | 0.14607 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW144-ER8 | 0.9183 | 0.8899 | -0.0284 |  | 0.9 | 1.05 | 0.10623 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW144-ER8 | 0.9183 | 0.8899 | -0.0284 |  | 0.9 | 1.05 | 0.24261 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW144-ER8 | 0.9183 | 0.8899 | -0.0284 |  | 0.9 | 1.05 | 0.1005 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW144-ER8 | 0.9183 | 0.8899 | -0.0284 |  | 0.9 | 1.05 | 0.03506 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW144-ER8 | 0.9183 | 0.8899 | -0.0284 |  | 0.9 | 1.05 | 0.07067 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW144-ER8 | 0.9183 | 0.8899 | -0.0284 |  | 0.9 | 1.05 | 0.14607 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW170-ER8 | 0.9179 | 0.8766 | -0.0413 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW170-ER8 | 0.9179 | 0.8766 | -0.0413 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW170-ER8 | 0.9179 | 0.8766 | -0.0413 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW170-ER8 | 0.9179 | 0.8766 | -0.0413 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW170-ER8 | 0.9179 | 0.8766 | -0.0413 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW170-ER8 | 0.9179 | 0.8766 | -0.0413 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW170-ER8 | 0.9172 | 0.8768 | -0.0404 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW170-ER8 | 0.9172 | 0.8768 | -0.0404 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW170-ER8 | 0.9172 | 0.8768 | -0.0404 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW170-ER8 | 0.9172 | 0.8768 | -0.0404 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW170-ER8 | 0.9172 | 0.8768 | -0.0404 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW170-ER8 | 0.9172 | 0.8768 | -0.0404 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW170-ER8 | 0.9179 | 0.8771 | -0.0408 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW170-ER8 | 0.9179 | 0.8771 | -0.0408 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW170-ER8 | 0.9179 | 0.8771 | -0.0408 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW170-ER8 | 0.9179 | 0.8771 | -0.0408 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW170-ER8 | 0.9179 | 0.8771 | -0.0408 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW170-ER8 | 0.9179 | 0.8771 | -0.0408 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW170-ER8 | 0.9179 | 0.8777 | -0.0402 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW170-ER8 | 0.9179 | 0.8777 | -0.0402 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW170-ER8 | 0.9179 | 0.8777 | -0.0402 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW170-ER8 | 0.9179 | 0.8777 | -0.0402 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW170-ER8 | 0.9179 | 0.8777 | -0.0402 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW170-ER8 | 0.9179 | 0.8777 | -0.0402 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW170-ER8 | 0.9185 | 0.8789 | -0.0396 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW170-ER8 | 0.9185 | 0.8789 | -0.0396 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW170-ER8 | 0.9185 | 0.8789 | -0.0396 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW170-ER8 | 0.9185 | 0.8789 | -0.0396 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW170-ER8 | 0.9185 | 0.8789 | -0.0396 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW170-ER8 | 0.9185 | 0.8789 | -0.0396 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW144-ER8 | 0.9214 | 0.8974 | -0.024 |  | 0.9 | 1.05 | 0.10941 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW144-ER8 | 0.9214 | 0.8974 | -0.024 |  | 0.9 | 1.05 | 0.05493 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW170-ER8 | 0.9198 | 0.8802 | -0.0396 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW170-ER8 | 0.9198 | 0.8802 | -0.0396 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW170-ER8 | 0.9198 | 0.8802 | -0.0396 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW170-ER8 | 0.9198 | 0.8802 | -0.0396 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW170-ER8 | 0.9198 | 0.8802 | -0.0396 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW170-ER8 | 0.9198 | 0.8802 | -0.0396 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW156-ER8 | 0.8852 | 0.8394 | -0.0458 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW156-ER8 | 0.8852 | 0.8394 | -0.0458 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW156-ER8 | 0.8852 | 0.8394 | -0.0458 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW156-ER8 | 0.8852 | 0.8394 | -0.0458 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW156-ER8 | 0.8852 | 0.8394 | -0.0458 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW156-ER8 | 0.8852 | 0.8394 | -0.0458 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW156-ER8 | 0.885 | 0.8396 | -0.0454 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW156-ER8 | 0.885 | 0.8396 | -0.0454 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW156-ER8 | 0.885 | 0.8396 | -0.0454 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW156-ER8 | 0.885 | 0.8396 | -0.0454 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW156-ER8 | 0.885 | 0.8396 | -0.0454 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW156-ER8 | 0.885 | 0.8396 | -0.0454 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW156-ER8 | 0.8868 | 0.8441 | -0.0427 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW156-ER8 | 0.8868 | 0.8441 | -0.0427 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW156-ER8 | 0.8868 | 0.8441 | -0.0427 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW156-ER8 | 0.8868 | 0.8441 | -0.0427 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW156-ER8 | 0.8868 | 0.8441 | -0.0427 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW156-ER8 | 0.8868 | 0.8441 | -0.0427 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW170-ER8 | 0.9207 | 0.8819 | -0.0388 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW170-ER8 | 0.9207 | 0.8819 | -0.0388 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW170-ER8 | 0.9207 | 0.8819 | -0.0388 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW170-ER8 | 0.9207 | 0.8819 | -0.0388 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW170-ER8 | 0.9207 | 0.8819 | -0.0388 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW170-ER8 | 0.9207 | 0.8819 | -0.0388 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW170-ER8 | 0.921 | 0.8825 | -0.0385 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW170-ER8 | 0.921 | 0.8825 | -0.0385 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW170-ER8 | 0.921 | 0.8825 | -0.0385 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW170-ER8 | 0.921 | 0.8825 | -0.0385 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW170-ER8 | 0.921 | 0.8825 | -0.0385 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW170-ER8 | 0.921 | 0.8825 | -0.0385 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW425-ER8 | 0.9283 | 0.8768 | -0.0515 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW425-ER8 | 0.9283 | 0.8768 | -0.0515 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW425-ER8 | 0.9283 | 0.8768 | -0.0515 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW425-ER8 | 0.9283 | 0.8768 | -0.0515 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW425-ER8 | 0.9283 | 0.8768 | -0.0515 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW425-ER8 | 0.9283 | 0.8768 | -0.0515 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW156-ER8 | 0.8876 | 0.845 | -0.0426 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW156-ER8 | 0.8876 | 0.845 | -0.0426 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW156-ER8 | 0.8876 | 0.845 | -0.0426 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW156-ER8 | 0.8876 | 0.845 | -0.0426 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW156-ER8 | 0.8876 | 0.845 | -0.0426 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW156-ER8 | 0.8876 | 0.845 | -0.0426 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW156-ER8 | 0.889 | 0.8454 | -0.0436 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW156-ER8 | 0.889 | 0.8454 | -0.0436 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW156-ER8 | 0.889 | 0.8454 | -0.0436 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW156-ER8 | 0.889 | 0.8454 | -0.0436 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW156-ER8 | 0.889 | 0.8454 | -0.0436 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW156-ER8 | 0.889 | 0.8454 | -0.0436 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW156-ER8 | 0.889 | 0.846 | -0.043 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW156-ER8 | 0.889 | 0.846 | -0.043 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW156-ER8 | 0.889 | 0.846 | -0.043 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW156-ER8 | 0.889 | 0.846 | -0.043 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW156-ER8 | 0.889 | 0.846 | -0.043 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW156-ER8 | 0.889 | 0.846 | -0.043 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW156-ER8 | 0.8883 | 0.8463 | -0.042 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW156-ER8 | 0.8883 | 0.8463 | -0.042 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW156-ER8 | 0.8883 | 0.8463 | -0.042 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW156-ER8 | 0.8883 | 0.8463 | -0.042 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW156-ER8 | 0.8883 | 0.8463 | -0.042 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW156-ER8 | 0.8883 | 0.8463 | -0.042 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW156-ER8 | 0.891 | 0.8493 | -0.0417 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW156-ER8 | 0.891 | 0.8493 | -0.0417 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW156-ER8 | 0.891 | 0.8493 | -0.0417 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW156-ER8 | 0.891 | 0.8493 | -0.0417 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW156-ER8 | 0.891 | 0.8493 | -0.0417 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW156-ER8 | 0.891 | 0.8493 | -0.0417 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW425-ER8 | 0.928 | 0.877 | -0.051 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW425-ER8 | 0.928 | 0.877 | -0.051 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW425-ER8 | 0.928 | 0.877 | -0.051 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW425-ER8 | 0.928 | 0.877 | -0.051 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW425-ER8 | 0.928 | 0.877 | -0.051 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW425-ER8 | 0.928 | 0.877 | -0.051 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW156-ER8 | 0.892 | 0.8511 | -0.0409 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW156-ER8 | 0.892 | 0.8511 | -0.0409 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW156-ER8 | 0.892 | 0.8511 | -0.0409 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW156-ER8 | 0.892 | 0.8511 | -0.0409 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW156-ER8 | 0.892 | 0.8511 | -0.0409 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW156-ER8 | 0.892 | 0.8511 | -0.0409 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW156-ER8 | 0.8923 | 0.8517 | -0.0406 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW156-ER8 | 0.8923 | 0.8517 | -0.0406 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW156-ER8 | 0.8923 | 0.8517 | -0.0406 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW156-ER8 | 0.8923 | 0.8517 | -0.0406 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW156-ER8 | 0.8923 | 0.8517 | -0.0406 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW156-ER8 | 0.8923 | 0.8517 | -0.0406 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW425-ER8 | 0.9299 | 0.8826 | -0.0473 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW425-ER8 | 0.9299 | 0.8826 | -0.0473 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW425-ER8 | 0.9299 | 0.8826 | -0.0473 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW425-ER8 | 0.9299 | 0.8826 | -0.0473 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW425-ER8 | 0.9299 | 0.8826 | -0.0473 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW425-ER8 | 0.9299 | 0.8826 | -0.0473 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW425-ER8 | 0.9299 | 0.8832 | -0.0467 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW425-ER8 | 0.9299 | 0.8832 | -0.0467 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW425-ER8 | 0.9299 | 0.8832 | -0.0467 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW425-ER8 | 0.9299 | 0.8832 | -0.0467 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW425-ER8 | 0.9299 | 0.8832 | -0.0467 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW425-ER8 | 0.9299 | 0.8832 | -0.0467 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW425-ER8 | 0.931 | 0.8854 | -0.0456 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW425-ER8 | 0.931 | 0.8854 | -0.0456 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW425-ER8 | 0.931 | 0.8854 | -0.0456 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW425-ER8 | 0.931 | 0.8854 | -0.0456 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW425-ER8 | 0.931 | 0.8854 | -0.0456 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW425-ER8 | 0.931 | 0.8854 | -0.0456 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW425-ER8 | 0.9326 | 0.8875 | -0.0451 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW425-ER8 | 0.9326 | 0.8875 | -0.0451 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW425-ER8 | 0.9326 | 0.8875 | -0.0451 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW425-ER8 | 0.9326 | 0.8875 | -0.0451 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW425-ER8 | 0.9326 | 0.8875 | -0.0451 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW425-ER8 | 0.9326 | 0.8875 | -0.0451 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW156-ER8 | 0.9129 | 0.8826 | -0.0303 |  | 0.9 | 1.05 | 0.10642 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW156-ER8 | 0.9129 | 0.8826 | -0.0303 |  | 0.9 | 1.05 | 0.24279 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW156-ER8 | 0.9129 | 0.8826 | -0.0303 |  | 0.9 | 1.05 | 0.09958 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW156-ER8 | 0.9129 | 0.8826 | -0.0303 |  | 0.9 | 1.05 | 0.03529 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW156-ER8 | 0.9129 | 0.8826 | -0.0303 |  | 0.9 | 1.05 | 0.0709 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW156-ER8 | 0.9129 | 0.8826 | -0.0303 |  | 0.9 | 1.05 | 0.14646 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW156-ER8 | 0.913 | 0.8826 | -0.0304 |  | 0.9 | 1.05 | 0.10642 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW156-ER8 | 0.913 | 0.8826 | -0.0304 |  | 0.9 | 1.05 | 0.24279 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW156-ER8 | 0.913 | 0.8826 | -0.0304 |  | 0.9 | 1.05 | 0.09958 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW156-ER8 | 0.913 | 0.8826 | -0.0304 |  | 0.9 | 1.05 | 0.03529 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW156-ER8 | 0.913 | 0.8826 | -0.0304 |  | 0.9 | 1.05 | 0.0709 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW156-ER8 | 0.913 | 0.8826 | -0.0304 |  | 0.9 | 1.05 | 0.14646 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW425-ER8 | 0.9334 | 0.8887 | -0.0447 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW425-ER8 | 0.9334 | 0.8887 | -0.0447 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW425-ER8 | 0.9334 | 0.8887 | -0.0447 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW425-ER8 | 0.9334 | 0.8887 | -0.0447 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW425-ER8 | 0.9334 | 0.8887 | -0.0447 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW425-ER8 | 0.9334 | 0.8887 | -0.0447 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW425-ER8 | 0.9329 | 0.8887 | -0.0442 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW425-ER8 | 0.9329 | 0.8887 | -0.0442 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW425-ER8 | 0.9329 | 0.8887 | -0.0442 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW425-ER8 | 0.9329 | 0.8887 | -0.0442 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW425-ER8 | 0.9329 | 0.8887 | -0.0442 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW425-ER8 | 0.9329 | 0.8887 | -0.0442 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW156-ER8 | 0.913 | 0.8826 | -0.0304 |  | 0.9 | 1.05 | 0.10642 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW156-ER8 | 0.913 | 0.8826 | -0.0304 |  | 0.9 | 1.05 | 0.24279 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW156-ER8 | 0.913 | 0.8826 | -0.0304 |  | 0.9 | 1.05 | 0.09958 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW156-ER8 | 0.913 | 0.8826 | -0.0304 |  | 0.9 | 1.05 | 0.03529 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW156-ER8 | 0.913 | 0.8826 | -0.0304 |  | 0.9 | 1.05 | 0.0709 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW156-ER8 | 0.913 | 0.8826 | -0.0304 |  | 0.9 | 1.05 | 0.14646 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW425-ER8 | 0.9348 | 0.8914 | -0.0434 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW425-ER8 | 0.9348 | 0.8914 | -0.0434 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW425-ER8 | 0.9348 | 0.8914 | -0.0434 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW425-ER8 | 0.9348 | 0.8914 | -0.0434 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW425-ER8 | 0.9348 | 0.8914 | -0.0434 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW425-ER8 | 0.9348 | 0.8914 | -0.0434 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW425-ER8 | 0.935 | 0.8919 | -0.0431 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW425-ER8 | 0.935 | 0.8919 | -0.0431 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW425-ER8 | 0.935 | 0.8919 | -0.0431 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW425-ER8 | 0.935 | 0.8919 | -0.0431 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW425-ER8 | 0.935 | 0.8919 | -0.0431 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW425-ER8 | 0.935 | 0.8919 | -0.0431 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW156-ER8 | 0.9154 | 0.8869 | -0.0285 |  | 0.9 | 1.05 | 0.10623 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW156-ER8 | 0.9154 | 0.8869 | -0.0285 |  | 0.9 | 1.05 | 0.24261 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW156-ER8 | 0.9154 | 0.8869 | -0.0285 |  | 0.9 | 1.05 | 0.1005 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW156-ER8 | 0.9154 | 0.8869 | -0.0285 |  | 0.9 | 1.05 | 0.03506 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW156-ER8 | 0.9154 | 0.8869 | -0.0285 |  | 0.9 | 1.05 | 0.07067 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW156-ER8 | 0.9154 | 0.8869 | -0.0285 |  | 0.9 | 1.05 | 0.14607 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW156-ER8 | 0.9154 | 0.8869 | -0.0285 |  | 0.9 | 1.05 | 0.10623 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW156-ER8 | 0.9154 | 0.8869 | -0.0285 |  | 0.9 | 1.05 | 0.24261 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW156-ER8 | 0.9154 | 0.8869 | -0.0285 |  | 0.9 | 1.05 | 0.1005 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW156-ER8 | 0.9154 | 0.8869 | -0.0285 |  | 0.9 | 1.05 | 0.03506 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW156-ER8 | 0.9154 | 0.8869 | -0.0285 |  | 0.9 | 1.05 | 0.07067 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW156-ER8 | 0.9154 | 0.8869 | -0.0285 |  | 0.9 | 1.05 | 0.14607 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW156-ER8 | 0.9154 | 0.8869 | -0.0285 |  | 0.9 | 1.05 | 0.10623 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW156-ER8 | 0.9154 | 0.8869 | -0.0285 |  | 0.9 | 1.05 | 0.24261 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW156-ER8 | 0.9154 | 0.8869 | -0.0285 |  | 0.9 | 1.05 | 0.1005 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW156-ER8 | 0.9154 | 0.8869 | -0.0285 |  | 0.9 | 1.05 | 0.03506 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW156-ER8 | 0.9154 | 0.8869 | -0.0285 |  | 0.9 | 1.05 | 0.07067 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW156-ER8 | 0.9154 | 0.8869 | -0.0285 |  | 0.9 | 1.05 | 0.14607 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW156-ER8 | 0.9185 | 0.8944 | -0.0241 |  | 0.9 | 1.05 | 0.10941 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW156-ER8 | 0.9185 | 0.8944 | -0.0241 |  | 0.9 | 1.05 | 0.05493 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW156-ER8 | 0.9223 | 0.8983 | -0.024 |  | 0.9 | 1.05 | 0.03069 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW156-ER8 | 0.9223 | 0.8983 | -0.024 |  | 0.9 | 1.05 | 0.10922 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW156-ER8 | 0.9223 | 0.8983 | -0.024 |  | 0.9 | 1.05 | 0.05476 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW156-ER8 | 0.9209 | 0.8988 | -0.0221 |  | 0.9 | 1.05 | 0.05765 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW156-ER8 | 0.9209 | 0.8988 | -0.0221 |  | 0.9 | 1.05 | 0.04499 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW156-ER8 | 0.9209 | 0.8988 | -0.0221 |  | 0.9 | 1.05 | 0.05213 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW156-ER8 | 0.9209 | 0.8988 | -0.0221 |  | 0.9 | 1.05 | 0.07544 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW156-ER8 | 0.9209 | 0.8988 | -0.0221 |  | 0.9 | 1.05 | 0.07656 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW156-ER8 | 0.9209 | 0.8988 | -0.0221 |  | 0.9 | 1.05 | 0.05236 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW156-ER8 | 0.9215 | 0.8992 | -0.0223 |  | 0.9 | 1.05 | 0.03199 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW156-ER8 | 0.9215 | 0.8992 | -0.0223 |  | 0.9 | 1.05 | 0.04873 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW156-ER8 | 0.9215 | 0.8992 | -0.0223 |  | 0.9 | 1.05 | 0.09554 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW156-ER8 | 0.9215 | 0.8992 | -0.0223 |  | 0.9 | 1.05 | 0.08589 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW156-ER8 | 0.9215 | 0.8992 | -0.0223 |  | 0.9 | 1.05 | 0.04498 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW156-ER8 | 0.9215 | 0.8995 | -0.022 |  | 0.9 | 1.05 | 0.03222 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW156-ER8 | 0.9215 | 0.8995 | -0.022 |  | 0.9 | 1.05 | 0.04909 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW156-ER8 | 0.9215 | 0.8995 | -0.022 |  | 0.9 | 1.05 | 0.09624 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW156-ER8 | 0.9215 | 0.8995 | -0.022 |  | 0.9 | 1.05 | 0.08652 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW156-ER8 | 0.9215 | 0.8995 | -0.022 |  | 0.9 | 1.05 | 0.04531 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW412-ER8 | 0.9431 | 0.8981 | -0.045 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW412-ER8 | 0.9431 | 0.8981 | -0.045 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW412-ER8 | 0.9431 | 0.8981 | -0.045 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW412-ER8 | 0.9431 | 0.8981 | -0.045 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW412-ER8 | 0.9431 | 0.8981 | -0.045 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW412-ER8 | 0.9431 | 0.8981 | -0.045 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW412-ER8 | 0.9428 | 0.8983 | -0.0445 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW412-ER8 | 0.9428 | 0.8983 | -0.0445 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW412-ER8 | 0.9428 | 0.8983 | -0.0445 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW412-ER8 | 0.9428 | 0.8983 | -0.0445 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW412-ER8 | 0.9428 | 0.8983 | -0.0445 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW412-ER8 | 0.9428 | 0.8983 | -0.0445 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW640-ER8 | 0.9244 | 0.8854 | -0.039 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW640-ER8 | 0.9244 | 0.8854 | -0.039 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW640-ER8 | 0.9244 | 0.8854 | -0.039 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW640-ER8 | 0.9244 | 0.8854 | -0.039 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW640-ER8 | 0.9244 | 0.8854 | -0.039 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW640-ER8 | 0.9244 | 0.8854 | -0.039 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW640-ER8 | 0.9238 | 0.8857 | -0.0381 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW640-ER8 | 0.9238 | 0.8857 | -0.0381 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW640-ER8 | 0.9238 | 0.8857 | -0.0381 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW640-ER8 | 0.9238 | 0.8857 | -0.0381 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW640-ER8 | 0.9238 | 0.8857 | -0.0381 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW640-ER8 | 0.9238 | 0.8857 | -0.0381 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW640-ER8 | 0.9244 | 0.8863 | -0.0381 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW640-ER8 | 0.9244 | 0.8863 | -0.0381 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW640-ER8 | 0.9244 | 0.8863 | -0.0381 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW640-ER8 | 0.9244 | 0.8863 | -0.0381 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW640-ER8 | 0.9244 | 0.8863 | -0.0381 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW640-ER8 | 0.9244 | 0.8863 | -0.0381 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW640-ER8 | 0.9277 | 0.8878 | -0.0399 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW640-ER8 | 0.9277 | 0.8878 | -0.0399 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW640-ER8 | 0.9277 | 0.8878 | -0.0399 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW640-ER8 | 0.9277 | 0.8878 | -0.0399 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW640-ER8 | 0.9277 | 0.8878 | -0.0399 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW640-ER8 | 0.9277 | 0.8878 | -0.0399 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW640-ER8 | 0.9271 | 0.8884 | -0.0387 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW640-ER8 | 0.9271 | 0.8884 | -0.0387 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW640-ER8 | 0.9271 | 0.8884 | -0.0387 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW640-ER8 | 0.9271 | 0.8884 | -0.0387 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW640-ER8 | 0.9271 | 0.8884 | -0.0387 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW640-ER8 | 0.9271 | 0.8884 | -0.0387 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW640-ER8 | 0.9273 | 0.8889 | -0.0384 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW640-ER8 | 0.9273 | 0.8889 | -0.0384 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW640-ER8 | 0.9273 | 0.8889 | -0.0384 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW640-ER8 | 0.9273 | 0.8889 | -0.0384 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW640-ER8 | 0.9273 | 0.8889 | -0.0384 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW640-ER8 | 0.9273 | 0.8889 | -0.0384 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW640-ER8 | 0.9262 | 0.8895 | -0.0367 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW640-ER8 | 0.9262 | 0.8895 | -0.0367 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW640-ER8 | 0.9262 | 0.8895 | -0.0367 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW640-ER8 | 0.9262 | 0.8895 | -0.0367 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW640-ER8 | 0.9262 | 0.8895 | -0.0367 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW640-ER8 | 0.9262 | 0.8895 | -0.0367 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW640-ER8 | 0.9269 | 0.8908 | -0.0361 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW640-ER8 | 0.9269 | 0.8908 | -0.0361 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW640-ER8 | 0.9269 | 0.8908 | -0.0361 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW640-ER8 | 0.9269 | 0.8908 | -0.0361 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW640-ER8 | 0.9269 | 0.8908 | -0.0361 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW640-ER8 | 0.9269 | 0.8908 | -0.0361 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW640-ER8 | 0.9288 | 0.8913 | -0.0375 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW640-ER8 | 0.9288 | 0.8913 | -0.0375 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW640-ER8 | 0.9288 | 0.8913 | -0.0375 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW640-ER8 | 0.9288 | 0.8913 | -0.0375 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW640-ER8 | 0.9288 | 0.8913 | -0.0375 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW640-ER8 | 0.9288 | 0.8913 | -0.0375 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW640-ER8 | 0.9306 | 0.8935 | -0.0371 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW640-ER8 | 0.9306 | 0.8935 | -0.0371 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW640-ER8 | 0.9306 | 0.8935 | -0.0371 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW640-ER8 | 0.9306 | 0.8935 | -0.0371 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW640-ER8 | 0.9306 | 0.8935 | -0.0371 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW640-ER8 | 0.9306 | 0.8935 | -0.0371 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW-EMERY-ER8 | 0.924 | 0.8775 | -0.0465 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW-EMERY-ER8 | 0.924 | 0.8775 | -0.0465 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW-EMERY-ER8 | 0.924 | 0.8775 | -0.0465 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW-EMERY-ER8 | 0.924 | 0.8775 | -0.0465 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW-EMERY-ER8 | 0.924 | 0.8775 | -0.0465 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW-EMERY-ER8 | 0.924 | 0.8775 | -0.0465 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW-EMERY-ER8 | 0.9237 | 0.8777 | -0.046 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW-EMERY-ER8 | 0.9237 | 0.8777 | -0.046 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW-EMERY-ER8 | 0.9237 | 0.8777 | -0.046 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW-EMERY-ER8 | 0.9237 | 0.8777 | -0.046 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW-EMERY-ER8 | 0.9237 | 0.8777 | -0.046 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW-EMERY-ER8 | 0.9237 | 0.8777 | -0.046 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW-EMERY-ER8 | 0.9249 | 0.8795 | -0.0454 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW-EMERY-ER8 | 0.9249 | 0.8795 | -0.0454 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW-EMERY-ER8 | 0.9249 | 0.8795 | -0.0454 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW-EMERY-ER8 | 0.9249 | 0.8795 | -0.0454 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW-EMERY-ER8 | 0.9249 | 0.8795 | -0.0454 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW-EMERY-ER8 | 0.9249 | 0.8795 | -0.0454 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW-EMERY-ER8 | 0.9249 | 0.8825 | -0.0424 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW-EMERY-ER8 | 0.9249 | 0.8825 | -0.0424 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW-EMERY-ER8 | 0.9249 | 0.8825 | -0.0424 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW-EMERY-ER8 | 0.9249 | 0.8825 | -0.0424 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW-EMERY-ER8 | 0.9249 | 0.8825 | -0.0424 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW-EMERY-ER8 | 0.9249 | 0.8825 | -0.0424 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW-EMERY-ER8 | 0.927 | 0.8833 | -0.0437 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW-EMERY-ER8 | 0.927 | 0.8833 | -0.0437 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW-EMERY-ER8 | 0.927 | 0.8833 | -0.0437 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW-EMERY-ER8 | 0.927 | 0.8833 | -0.0437 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW-EMERY-ER8 | 0.927 | 0.8833 | -0.0437 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW-EMERY-ER8 | 0.927 | 0.8833 | -0.0437 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW-EMERY-ER8 | 0.9255 | 0.8836 | -0.0419 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW-EMERY-ER8 | 0.9255 | 0.8836 | -0.0419 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW-EMERY-ER8 | 0.9255 | 0.8836 | -0.0419 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW-EMERY-ER8 | 0.9255 | 0.8836 | -0.0419 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW-EMERY-ER8 | 0.9255 | 0.8836 | -0.0419 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW-EMERY-ER8 | 0.9255 | 0.8836 | -0.0419 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW-EMERY-ER8 | 0.9269 | 0.8839 | -0.043 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW-EMERY-ER8 | 0.9269 | 0.8839 | -0.043 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW-EMERY-ER8 | 0.9269 | 0.8839 | -0.043 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW-EMERY-ER8 | 0.9269 | 0.8839 | -0.043 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW-EMERY-ER8 | 0.9269 | 0.8839 | -0.043 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW-EMERY-ER8 | 0.9269 | 0.8839 | -0.043 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW-EMERY-ER8 | 0.928 | 0.8869 | -0.0411 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW-EMERY-ER8 | 0.928 | 0.8869 | -0.0411 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW-EMERY-ER8 | 0.928 | 0.8869 | -0.0411 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW-EMERY-ER8 | 0.928 | 0.8869 | -0.0411 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW-EMERY-ER8 | 0.928 | 0.8869 | -0.0411 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW-EMERY-ER8 | 0.928 | 0.8869 | -0.0411 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW-EMERY-ER8 | 0.9294 | 0.889 | -0.0404 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW-EMERY-ER8 | 0.9294 | 0.889 | -0.0404 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW-EMERY-ER8 | 0.9294 | 0.889 | -0.0404 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW-EMERY-ER8 | 0.9294 | 0.889 | -0.0404 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW-EMERY-ER8 | 0.9294 | 0.889 | -0.0404 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW-EMERY-ER8 | 0.9294 | 0.889 | -0.0404 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW-EMERY-ER8 | 0.9298 | 0.8895 | -0.0403 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW-EMERY-ER8 | 0.9298 | 0.8895 | -0.0403 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW-EMERY-ER8 | 0.9298 | 0.8895 | -0.0403 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW-EMERY-ER8 | 0.9298 | 0.8895 | -0.0403 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW-EMERY-ER8 | 0.9298 | 0.8895 | -0.0403 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW-EMERY-ER8 | 0.9298 | 0.8895 | -0.0403 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW-SANDC-ER8 | 0.9337 | 0.8958 | -0.0379 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW-SANDC-ER8 | 0.9337 | 0.8958 | -0.0379 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW-SANDC-ER8 | 0.9337 | 0.8958 | -0.0379 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW-SANDC-ER8 | 0.9337 | 0.8958 | -0.0379 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW-SANDC-ER8 | 0.9337 | 0.8958 | -0.0379 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW-SANDC-ER8 | 0.9337 | 0.8958 | -0.0379 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW-SANDC-ER8 | 0.9336 | 0.8959 | -0.0377 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW-SANDC-ER8 | 0.9336 | 0.8959 | -0.0377 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW-SANDC-ER8 | 0.9336 | 0.8959 | -0.0377 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW-SANDC-ER8 | 0.9336 | 0.8959 | -0.0377 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW-SANDC-ER8 | 0.9336 | 0.8959 | -0.0377 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW-SANDC-ER8 | 0.9336 | 0.8959 | -0.0377 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW-SPENC-ER8 | 0.9065 | 0.8625 | -0.044 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW-SPENC-ER8 | 0.9065 | 0.8625 | -0.044 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW-SPENC-ER8 | 0.9065 | 0.8625 | -0.044 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW-SPENC-ER8 | 0.9065 | 0.8625 | -0.044 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW-SPENC-ER8 | 0.9065 | 0.8625 | -0.044 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW-SPENC-ER8 | 0.9065 | 0.8625 | -0.044 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW-SPENC-ER8 | 0.9063 | 0.8626 | -0.0437 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW-SPENC-ER8 | 0.9063 | 0.8626 | -0.0437 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW-SPENC-ER8 | 0.9063 | 0.8626 | -0.0437 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW-SPENC-ER8 | 0.9063 | 0.8626 | -0.0437 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW-SPENC-ER8 | 0.9063 | 0.8626 | -0.0437 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW-SPENC-ER8 | 0.9063 | 0.8626 | -0.0437 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW-SPENC-ER8 | 0.9085 | 0.8665 | -0.042 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW-SPENC-ER8 | 0.9085 | 0.8665 | -0.042 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW-SPENC-ER8 | 0.9085 | 0.8665 | -0.042 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW-SPENC-ER8 | 0.9085 | 0.8665 | -0.042 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW-SPENC-ER8 | 0.9085 | 0.8665 | -0.042 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW-SPENC-ER8 | 0.9085 | 0.8665 | -0.042 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW-SPENC-ER8 | 0.9081 | 0.8669 | -0.0412 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW-SPENC-ER8 | 0.9081 | 0.8669 | -0.0412 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW-SPENC-ER8 | 0.9081 | 0.8669 | -0.0412 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW-SPENC-ER8 | 0.9081 | 0.8669 | -0.0412 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW-SPENC-ER8 | 0.9081 | 0.8669 | -0.0412 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW-SPENC-ER8 | 0.9081 | 0.8669 | -0.0412 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW-SPENC-ER8 | 0.9085 | 0.867 | -0.0415 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW-SPENC-ER8 | 0.9085 | 0.867 | -0.0415 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW-SPENC-ER8 | 0.9085 | 0.867 | -0.0415 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW-SPENC-ER8 | 0.9085 | 0.867 | -0.0415 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW-SPENC-ER8 | 0.9085 | 0.867 | -0.0415 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW-SPENC-ER8 | 0.9085 | 0.867 | -0.0415 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW-SPENC-ER8 | 0.9088 | 0.8679 | -0.0409 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW-SPENC-ER8 | 0.9088 | 0.8679 | -0.0409 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW-SPENC-ER8 | 0.9088 | 0.8679 | -0.0409 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW-SPENC-ER8 | 0.9088 | 0.8679 | -0.0409 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW-SPENC-ER8 | 0.9088 | 0.8679 | -0.0409 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW-SPENC-ER8 | 0.9088 | 0.8679 | -0.0409 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SW-SPENC-ER8 | 0.9095 | 0.8691 | -0.0404 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SW-SPENC-ER8 | 0.9095 | 0.8691 | -0.0404 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SW-SPENC-ER8 | 0.9095 | 0.8691 | -0.0404 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SW-SPENC-ER8 | 0.9095 | 0.8691 | -0.0404 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SW-SPENC-ER8 | 0.9095 | 0.8691 | -0.0404 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SW-SPENC-ER8 | 0.9095 | 0.8691 | -0.0404 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW-SPENC-ER8 | 0.9105 | 0.8702 | -0.0403 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW-SPENC-ER8 | 0.9105 | 0.8702 | -0.0403 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW-SPENC-ER8 | 0.9105 | 0.8702 | -0.0403 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW-SPENC-ER8 | 0.9105 | 0.8702 | -0.0403 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW-SPENC-ER8 | 0.9105 | 0.8702 | -0.0403 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW-SPENC-ER8 | 0.9105 | 0.8702 | -0.0403 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW-SPENC-ER8 | 0.9114 | 0.8719 | -0.0395 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW-SPENC-ER8 | 0.9114 | 0.8719 | -0.0395 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW-SPENC-ER8 | 0.9114 | 0.8719 | -0.0395 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW-SPENC-ER8 | 0.9114 | 0.8719 | -0.0395 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW-SPENC-ER8 | 0.9114 | 0.8719 | -0.0395 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW-SPENC-ER8 | 0.9114 | 0.8719 | -0.0395 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | SW-SPENC-ER8 | 0.9117 | 0.8725 | -0.0392 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | SW-SPENC-ER8 | 0.9117 | 0.8725 | -0.0392 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | SW-SPENC-ER8 | 0.9117 | 0.8725 | -0.0392 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | SW-SPENC-ER8 | 0.9117 | 0.8725 | -0.0392 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | SW-SPENC-ER8 | 0.9117 | 0.8725 | -0.0392 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | SW-SPENC-ER8 | 0.9117 | 0.8725 | -0.0392 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SXFALLS2-ER7 | 0.9339 | 0.8982 | -0.0357 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SXFALLS2-ER7 | 0.9339 | 0.8982 | -0.0357 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SXFALLS2-ER7 | 0.9339 | 0.8982 | -0.0357 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SXFALLS2-ER7 | 0.9339 | 0.8982 | -0.0357 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SXFALLS2-ER7 | 0.9339 | 0.8982 | -0.0357 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SXFALLS2-ER7 | 0.9339 | 0.8982 | -0.0357 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SXFALLS2-ER7 | 0.9337 | 0.8984 | -0.0353 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SXFALLS2-ER7 | 0.9337 | 0.8984 | -0.0353 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SXFALLS2-ER7 | 0.9337 | 0.8984 | -0.0353 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SXFALLS2-ER7 | 0.9337 | 0.8984 | -0.0353 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SXFALLS2-ER7 | 0.9337 | 0.8984 | -0.0353 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SXFALLS2-ER7 | 0.9337 | 0.8984 | -0.0353 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | TRKYRDGE-ER8 | 0.924 | 0.885 | -0.039 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | TRKYRDGE-ER8 | 0.924 | 0.885 | -0.039 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | TRKYRDGE-ER8 | 0.924 | 0.885 | -0.039 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | TRKYRDGE-ER8 | 0.924 | 0.885 | -0.039 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | TRKYRDGE-ER8 | 0.924 | 0.885 | -0.039 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | TRKYRDGE-ER8 | 0.924 | 0.885 | -0.039 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | TRKYRDGE-ER8 | 0.9234 | 0.8853 | -0.0381 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | TRKYRDGE-ER8 | 0.9234 | 0.8853 | -0.0381 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | TRKYRDGE-ER8 | 0.9234 | 0.8853 | -0.0381 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | TRKYRDGE-ER8 | 0.9234 | 0.8853 | -0.0381 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | TRKYRDGE-ER8 | 0.9234 | 0.8853 | -0.0381 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | TRKYRDGE-ER8 | 0.9234 | 0.8853 | -0.0381 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | TRKYRDGE-ER8 | 0.924 | 0.8858 | -0.0382 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | TRKYRDGE-ER8 | 0.924 | 0.8858 | -0.0382 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | TRKYRDGE-ER8 | 0.924 | 0.8858 | -0.0382 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | TRKYRDGE-ER8 | 0.924 | 0.8858 | -0.0382 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | TRKYRDGE-ER8 | 0.924 | 0.8858 | -0.0382 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | TRKYRDGE-ER8 | 0.924 | 0.8858 | -0.0382 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | TRKYRDGE-ER8 | 0.9273 | 0.8874 | -0.0399 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | TRKYRDGE-ER8 | 0.9273 | 0.8874 | -0.0399 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | TRKYRDGE-ER8 | 0.9273 | 0.8874 | -0.0399 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | TRKYRDGE-ER8 | 0.9273 | 0.8874 | -0.0399 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | TRKYRDGE-ER8 | 0.9273 | 0.8874 | -0.0399 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | TRKYRDGE-ER8 | 0.9273 | 0.8874 | -0.0399 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | TRKYRDGE-ER8 | 0.9267 | 0.888 | -0.0387 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | TRKYRDGE-ER8 | 0.9267 | 0.888 | -0.0387 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | TRKYRDGE-ER8 | 0.9267 | 0.888 | -0.0387 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | TRKYRDGE-ER8 | 0.9267 | 0.888 | -0.0387 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | TRKYRDGE-ER8 | 0.9267 | 0.888 | -0.0387 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | TRKYRDGE-ER8 | 0.9267 | 0.888 | -0.0387 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | TRKYRDGE-ER8 | 0.9269 | 0.8885 | -0.0384 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | TRKYRDGE-ER8 | 0.9269 | 0.8885 | -0.0384 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | TRKYRDGE-ER8 | 0.9269 | 0.8885 | -0.0384 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | TRKYRDGE-ER8 | 0.9269 | 0.8885 | -0.0384 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | TRKYRDGE-ER8 | 0.9269 | 0.8885 | -0.0384 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | TRKYRDGE-ER8 | 0.9269 | 0.8885 | -0.0384 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | TRKYRDGE-ER8 | 0.9258 | 0.8891 | -0.0367 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | TRKYRDGE-ER8 | 0.9258 | 0.8891 | -0.0367 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | TRKYRDGE-ER8 | 0.9258 | 0.8891 | -0.0367 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | TRKYRDGE-ER8 | 0.9258 | 0.8891 | -0.0367 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | TRKYRDGE-ER8 | 0.9258 | 0.8891 | -0.0367 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | TRKYRDGE-ER8 | 0.9258 | 0.8891 | -0.0367 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | TRKYRDGE-ER8 | 0.9265 | 0.8904 | -0.0361 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | TRKYRDGE-ER8 | 0.9265 | 0.8904 | -0.0361 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | TRKYRDGE-ER8 | 0.9265 | 0.8904 | -0.0361 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | TRKYRDGE-ER8 | 0.9265 | 0.8904 | -0.0361 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | TRKYRDGE-ER8 | 0.9265 | 0.8904 | -0.0361 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | TRKYRDGE-ER8 | 0.9265 | 0.8904 | -0.0361 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | TRKYRDGE-ER8 | 0.9284 | 0.8909 | -0.0375 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | TRKYRDGE-ER8 | 0.9284 | 0.8909 | -0.0375 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | TRKYRDGE-ER8 | 0.9284 | 0.8909 | -0.0375 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | TRKYRDGE-ER8 | 0.9284 | 0.8909 | -0.0375 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | TRKYRDGE-ER8 | 0.9284 | 0.8909 | -0.0375 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | TRKYRDGE-ER8 | 0.9284 | 0.8909 | -0.0375 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | TRKYRDGE-ER8 | 0.9302 | 0.8931 | -0.0371 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | TRKYRDGE-ER8 | 0.9302 | 0.8931 | -0.0371 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | TRKYRDGE-ER8 | 0.9302 | 0.8931 | -0.0371 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | TRKYRDGE-ER8 | 0.9302 | 0.8931 | -0.0371 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | TRKYRDGE-ER8 | 0.9302 | 0.8931 | -0.0371 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | TRKYRDGE-ER8 | 0.9302 | 0.8931 | -0.0371 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | WILBUR-ER8 | 0.9427 | 0.8976 | -0.0451 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | WILBUR-ER8 | 0.9427 | 0.8976 | -0.0451 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | WILBUR-ER8 | 0.9427 | 0.8976 | -0.0451 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | WILBUR-ER8 | 0.9427 | 0.8976 | -0.0451 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | WILBUR-ER8 | 0.9427 | 0.8976 | -0.0451 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | WILBUR-ER8 | 0.9427 | 0.8976 | -0.0451 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | WILBUR-ER8 | 0.9423 | 0.8978 | -0.0445 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | WILBUR-ER8 | 0.9423 | 0.8978 | -0.0445 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | WILBUR-ER8 | 0.9423 | 0.8978 | -0.0445 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | WILBUR-ER8 | 0.9423 | 0.8978 | -0.0445 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | WILBUR-ER8 | 0.9423 | 0.8978 | -0.0445 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | WILBUR-ER8 | 0.9423 | 0.8978 | -0.0445 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Hanson County 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SYCAMORE-ER7 | 0.9264 | 0.8904 | -0.036 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SYCAMORE-ER7 | 0.9264 | 0.8904 | -0.036 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SYCAMORE-ER7 | 0.9264 | 0.8904 | -0.036 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SYCAMORE-ER7 | 0.9264 | 0.8904 | -0.036 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SYCAMORE-ER7 | 0.9264 | 0.8904 | -0.036 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SYCAMORE-ER7 | 0.9264 | 0.8904 | -0.036 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SYCAMORE-ER7 | 0.9263 | 0.8906 | -0.0357 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SYCAMORE-ER7 | 0.9263 | 0.8906 | -0.0357 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SYCAMORE-ER7 | 0.9263 | 0.8906 | -0.0357 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SYCAMORE-ER7 | 0.9263 | 0.8906 | -0.0357 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SYCAMORE-ER7 | 0.9263 | 0.8906 | -0.0357 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SYCAMORE-ER7 | 0.9263 | 0.8906 | -0.0357 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SYCAMORE-ER7 | 0.9272 | 0.8926 | -0.0346 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SYCAMORE-ER7 | 0.9272 | 0.8926 | -0.0346 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SYCAMORE-ER7 | 0.9272 | 0.8926 | -0.0346 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SYCAMORE-ER7 | 0.9272 | 0.8926 | -0.0346 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SYCAMORE-ER7 | 0.9272 | 0.8926 | -0.0346 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SYCAMORE-ER7 | 0.9272 | 0.8926 | -0.0346 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SYCAMORE-ER7 | 0.9279 | 0.8936 | -0.0343 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SYCAMORE-ER7 | 0.9279 | 0.8936 | -0.0343 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SYCAMORE-ER7 | 0.9279 | 0.8936 | -0.0343 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SYCAMORE-ER7 | 0.9279 | 0.8936 | -0.0343 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SYCAMORE-ER7 | 0.9279 | 0.8936 | -0.0343 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SYCAMORE-ER7 | 0.9279 | 0.8936 | -0.0343 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | SYCAMORE-ER7 | 0.9285 | 0.8946 | -0.0339 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | SYCAMORE-ER7 | 0.9285 | 0.8946 | -0.0339 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | SYCAMORE-ER7 | 0.9285 | 0.8946 | -0.0339 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | SYCAMORE-ER7 | 0.9285 | 0.8946 | -0.0339 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | SYCAMORE-ER7 | 0.9285 | 0.8946 | -0.0339 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | SYCAMORE-ER7 | 0.9285 | 0.8946 | -0.0339 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Multi - Sioux Falls 115 kV System Reconfig
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | XLSW4X1-ER8 | 0.9106 | 0.8669 | -0.0437 |  | 0.9 | 1.05 | 0.12403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | XLSW4X1-ER8 | 0.9106 | 0.8669 | -0.0437 |  | 0.9 | 1.05 | 0.0974 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | XLSW4X1-ER8 | 0.9106 | 0.8669 | -0.0437 |  | 0.9 | 1.05 | 0.14421 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | XLSW4X1-ER8 | 0.9106 | 0.8669 | -0.0437 |  | 0.9 | 1.05 | 0.29725 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | XLSW4X1-ER8 | 0.9106 | 0.8669 | -0.0437 |  | 0.9 | 1.05 | 0.20215 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | XLSW4X1-ER8 | 0.9106 | 0.8669 | -0.0437 |  | 0.9 | 1.05 | 0.13934 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | XLSW4X1-ER8 | 0.9104 | 0.8671 | -0.0433 |  | 0.9 | 1.05 | 0.12403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | XLSW4X1-ER8 | 0.9104 | 0.8671 | -0.0433 |  | 0.9 | 1.05 | 0.0974 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | XLSW4X1-ER8 | 0.9104 | 0.8671 | -0.0433 |  | 0.9 | 1.05 | 0.14421 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | XLSW4X1-ER8 | 0.9104 | 0.8671 | -0.0433 |  | 0.9 | 1.05 | 0.29725 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | XLSW4X1-ER8 | 0.9104 | 0.8671 | -0.0433 |  | 0.9 | 1.05 | 0.20215 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | XLSW4X1-ER8 | 0.9104 | 0.8671 | -0.0433 |  | 0.9 | 1.05 | 0.13934 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | XLSW4X1-ER8 | 0.9128 | 0.871 | -0.0418 |  | 0.9 | 1.05 | 0.12336 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | XLSW4X1-ER8 | 0.9128 | 0.871 | -0.0418 |  | 0.9 | 1.05 | 0.09678 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | XLSW4X1-ER8 | 0.9128 | 0.871 | -0.0418 |  | 0.9 | 1.05 | 0.1472 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | XLSW4X1-ER8 | 0.9128 | 0.871 | -0.0418 |  | 0.9 | 1.05 | 0.2965 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | XLSW4X1-ER8 | 0.9128 | 0.871 | -0.0418 |  | 0.9 | 1.05 | 0.20144 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | XLSW4X1-ER8 | 0.9128 | 0.871 | -0.0418 |  | 0.9 | 1.05 | 0.13808 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | XLSW4X1-ER8 | 0.9122 | 0.8713 | -0.0409 |  | 0.9 | 1.05 | 0.12403 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | XLSW4X1-ER8 | 0.9122 | 0.8713 | -0.0409 |  | 0.9 | 1.05 | 0.0974 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | XLSW4X1-ER8 | 0.9122 | 0.8713 | -0.0409 |  | 0.9 | 1.05 | 0.14421 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | XLSW4X1-ER8 | 0.9122 | 0.8713 | -0.0409 |  | 0.9 | 1.05 | 0.29725 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | XLSW4X1-ER8 | 0.9122 | 0.8713 | -0.0409 |  | 0.9 | 1.05 | 0.20215 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | XLSW4X1-ER8 | 0.9122 | 0.8713 | -0.0409 |  | 0.9 | 1.05 | 0.13934 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | XLSW4X1-ER8 | 0.9128 | 0.8716 | -0.0412 |  | 0.9 | 1.05 | 0.12336 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | XLSW4X1-ER8 | 0.9128 | 0.8716 | -0.0412 |  | 0.9 | 1.05 | 0.09678 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | XLSW4X1-ER8 | 0.9128 | 0.8716 | -0.0412 |  | 0.9 | 1.05 | 0.1472 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | XLSW4X1-ER8 | 0.9128 | 0.8716 | -0.0412 |  | 0.9 | 1.05 | 0.2965 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | XLSW4X1-ER8 | 0.9128 | 0.8716 | -0.0412 |  | 0.9 | 1.05 | 0.20144 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | XLSW4X1-ER8 | 0.9128 | 0.8716 | -0.0412 |  | 0.9 | 1.05 | 0.13808 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | XLSW4X1-ER8 | 0.9129 | 0.8722 | -0.0407 |  | 0.9 | 1.05 | 0.12403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | XLSW4X1-ER8 | 0.9129 | 0.8722 | -0.0407 |  | 0.9 | 1.05 | 0.0974 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | XLSW4X1-ER8 | 0.9129 | 0.8722 | -0.0407 |  | 0.9 | 1.05 | 0.14421 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | XLSW4X1-ER8 | 0.9129 | 0.8722 | -0.0407 |  | 0.9 | 1.05 | 0.29725 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | XLSW4X1-ER8 | 0.9129 | 0.8722 | -0.0407 |  | 0.9 | 1.05 | 0.20215 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | XLSW4X1-ER8 | 0.9129 | 0.8722 | -0.0407 |  | 0.9 | 1.05 | 0.13934 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-012 | XLSW4X1-ER8 | 0.9136 | 0.8735 | -0.0401 |  | 0.9 | 1.05 | 0.12403 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-082 | XLSW4X1-ER8 | 0.9136 | 0.8735 | -0.0401 |  | 0.9 | 1.05 | 0.0974 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-097 | XLSW4X1-ER8 | 0.9136 | 0.8735 | -0.0401 |  | 0.9 | 1.05 | 0.14421 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-105 | XLSW4X1-ER8 | 0.9136 | 0.8735 | -0.0401 |  | 0.9 | 1.05 | 0.29725 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-154 | XLSW4X1-ER8 | 0.9136 | 0.8735 | -0.0401 |  | 0.9 | 1.05 | 0.20215 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 24SP | GEN-2023-182 | XLSW4X1-ER8 | 0.9136 | 0.8735 | -0.0401 |  | 0.9 | 1.05 | 0.13934 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | XLSW4X1-ER8 | 0.9147 | 0.8747 | -0.04 |  | 0.9 | 1.05 | 0.12336 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | XLSW4X1-ER8 | 0.9147 | 0.8747 | -0.04 |  | 0.9 | 1.05 | 0.09678 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | XLSW4X1-ER8 | 0.9147 | 0.8747 | -0.04 |  | 0.9 | 1.05 | 0.1472 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | XLSW4X1-ER8 | 0.9147 | 0.8747 | -0.04 |  | 0.9 | 1.05 | 0.2965 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | XLSW4X1-ER8 | 0.9147 | 0.8747 | -0.04 |  | 0.9 | 1.05 | 0.20144 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | XLSW4X1-ER8 | 0.9147 | 0.8747 | -0.04 |  | 0.9 | 1.05 | 0.13808 | POI 652532_1 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | XLSW4X1-ER8 | 0.9156 | 0.8764 | -0.0392 |  | 0.9 | 1.05 | 0.12336 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | XLSW4X1-ER8 | 0.9156 | 0.8764 | -0.0392 |  | 0.9 | 1.05 | 0.09678 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | XLSW4X1-ER8 | 0.9156 | 0.8764 | -0.0392 |  | 0.9 | 1.05 | 0.1472 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | XLSW4X1-ER8 | 0.9156 | 0.8764 | -0.0392 |  | 0.9 | 1.05 | 0.2965 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | XLSW4X1-ER8 | 0.9156 | 0.8764 | -0.0392 |  | 0.9 | 1.05 | 0.20144 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | XLSW4X1-ER8 | 0.9156 | 0.8764 | -0.0392 |  | 0.9 | 1.05 | 0.13808 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-012 | XLSW4X1-ER8 | 0.9159 | 0.877 | -0.0389 |  | 0.9 | 1.05 | 0.12336 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-082 | XLSW4X1-ER8 | 0.9159 | 0.877 | -0.0389 |  | 0.9 | 1.05 | 0.09678 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-097 | XLSW4X1-ER8 | 0.9159 | 0.877 | -0.0389 |  | 0.9 | 1.05 | 0.1472 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-105 | XLSW4X1-ER8 | 0.9159 | 0.877 | -0.0389 |  | 0.9 | 1.05 | 0.2965 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-154 | XLSW4X1-ER8 | 0.9159 | 0.877 | -0.0389 |  | 0.9 | 1.05 | 0.20144 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27SP | GEN-2023-182 | XLSW4X1-ER8 | 0.9159 | 0.877 | -0.0389 |  | 0.9 | 1.05 | 0.13808 | POI 652532_2 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
Voltage | DISIS-2023-001 | 01ALL | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 | 01ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 | 02NR | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 | 01NR | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | WTCLF 3 | 0.94 | 0.8191 | -0.1209 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | WTCLF 3 | 0.9451 | 0.8191 | -0.126 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | WTCLF 3 | 0.94 | 0.8191 | -0.1209 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | WTCLF 3 | 0.9451 | 0.8191 | -0.126 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | WTCLF 3 | 0.94 | 0.8191 | -0.1209 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | WTCLF 3 | 0.9451 | 0.8191 | -0.126 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | WTCLFTP3 | 0.941 | 0.8203 | -0.1207 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | WTCLFTP3 | 0.9461 | 0.8203 | -0.1258 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | WTCLFTP3 | 0.941 | 0.8203 | -0.1207 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | WTCLFTP3 | 0.9461 | 0.8203 | -0.1258 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | WTCLFTP3 | 0.941 | 0.8203 | -0.1207 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | WTCLFTP3 | 0.9461 | 0.8203 | -0.1258 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | WTCLF 3 | 0.9534 | 0.8211 | -0.1323 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | WTCLF 3 | 0.9584 | 0.8211 | -0.1373 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | WTCLF 3 | 0.9534 | 0.8211 | -0.1323 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | WTCLF 3 | 0.9584 | 0.8211 | -0.1373 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | WTCLF 3 | 0.9534 | 0.8211 | -0.1323 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | WTCLF 3 | 0.9584 | 0.8211 | -0.1373 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | WTCLF 3 | 0.94 | 0.8213 | -0.1187 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | WTCLF 3 | 0.94 | 0.8213 | -0.1187 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | WTCLF 3 | 0.94 | 0.8213 | -0.1187 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | WTCLFTP3 | 0.9544 | 0.8223 | -0.1321 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | WTCLFTP3 | 0.9594 | 0.8223 | -0.1371 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | WTCLFTP3 | 0.9544 | 0.8223 | -0.1321 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | WTCLFTP3 | 0.9594 | 0.8223 | -0.1371 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | WTCLFTP3 | 0.9544 | 0.8223 | -0.1321 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | WTCLFTP3 | 0.9594 | 0.8223 | -0.1371 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | WTCLFTP3 | 0.941 | 0.8224 | -0.1186 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | WTCLFTP3 | 0.941 | 0.8224 | -0.1186 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | WTCLFTP3 | 0.941 | 0.8224 | -0.1186 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | CHASE 3 | 0.9355 | 0.8256 | -0.1099 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | CHASE 3 | 0.9355 | 0.8256 | -0.1099 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | CHASE 3 | 0.9355 | 0.8256 | -0.1099 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | SHARNSP3 | 0.9356 | 0.8257 | -0.1099 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | SHARNSP3 | 0.9356 | 0.8257 | -0.1099 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | SHARNSP3 | 0.9356 | 0.8257 | -0.1099 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | PILE 3 | 0.9369 | 0.8268 | -0.1101 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | PILE 3 | 0.9369 | 0.8268 | -0.1101 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | PILE 3 | 0.9369 | 0.8268 | -0.1101 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | KANARAD3 | 0.947 | 0.8272 | -0.1198 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | KANARAD3 | 0.9513 | 0.8272 | -0.1241 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | KANARAD3 | 0.947 | 0.8272 | -0.1198 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | KANARAD3 | 0.9513 | 0.8272 | -0.1241 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | KANARAD3 | 0.947 | 0.8272 | -0.1198 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | KANARAD3 | 0.9513 | 0.8272 | -0.1241 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | WTCLF 3 | 0.9534 | 0.8278 | -0.1256 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | WTCLF 3 | 0.9534 | 0.8278 | -0.1256 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | WTCLF 3 | 0.9534 | 0.8278 | -0.1256 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | KANARAD3 | 0.947 | 0.8287 | -0.1183 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | KANARAD3 | 0.947 | 0.8287 | -0.1183 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | KANARAD3 | 0.947 | 0.8287 | -0.1183 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | WTCLFTP3 | 0.9544 | 0.829 | -0.1254 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | WTCLFTP3 | 0.9544 | 0.829 | -0.1254 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | WTCLFTP3 | 0.9544 | 0.829 | -0.1254 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | CHASE 3 | 0.9489 | 0.8298 | -0.1191 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | CHASE 3 | 0.9489 | 0.8298 | -0.1191 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | CHASE 3 | 0.9489 | 0.8298 | -0.1191 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | SHARNSP3 | 0.949 | 0.8299 | -0.1191 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | SHARNSP3 | 0.949 | 0.8299 | -0.1191 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | SHARNSP3 | 0.949 | 0.8299 | -0.1191 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | PALMER3 | 0.9416 | 0.8311 | -0.1105 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | PALMER3 | 0.9416 | 0.8311 | -0.1105 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | PALMER3 | 0.9416 | 0.8311 | -0.1105 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | WTCLF 3 | 0.9361 | 0.8314 | -0.1047 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | WTCLF 3 | 0.9361 | 0.8314 | -0.1047 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | WTCLF 3 | 0.9361 | 0.8314 | -0.1047 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | KANARAD3 | 0.963 | 0.8317 | -0.1313 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | KANARAD3 | 0.9672 | 0.8317 | -0.1355 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | KANARAD3 | 0.963 | 0.8317 | -0.1313 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | KANARAD3 | 0.9672 | 0.8317 | -0.1355 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | KANARAD3 | 0.963 | 0.8317 | -0.1313 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | KANARAD3 | 0.9672 | 0.8317 | -0.1355 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | PILE 3 | 0.9479 | 0.8318 | -0.1161 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | PILE 3 | 0.9479 | 0.8318 | -0.1161 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | PILE 3 | 0.9479 | 0.8318 | -0.1161 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | CHASE 3 | 0.9532 | 0.832 | -0.1212 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | CHASE 3 | 0.959 | 0.832 | -0.127 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | CHASE 3 | 0.9532 | 0.832 | -0.1212 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | CHASE 3 | 0.959 | 0.832 | -0.127 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | CHASE 3 | 0.9532 | 0.832 | -0.1212 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | CHASE 3 | 0.959 | 0.832 | -0.127 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | SHARNSP3 | 0.9533 | 0.8321 | -0.1212 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | SHARNSP3 | 0.9591 | 0.8321 | -0.127 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | SHARNSP3 | 0.9533 | 0.8321 | -0.1212 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | SHARNSP3 | 0.9591 | 0.8321 | -0.127 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | SHARNSP3 | 0.9533 | 0.8321 | -0.1212 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | SHARNSP3 | 0.9591 | 0.8321 | -0.127 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | WTCLFTP3 | 0.9371 | 0.8325 | -0.1046 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | CHASE 3 | 0.9428 | 0.8325 | -0.1103 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | CHASE 3 | 0.9486 | 0.8325 | -0.1161 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | WTCLFTP3 | 0.9371 | 0.8325 | -0.1046 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | CHASE 3 | 0.9428 | 0.8325 | -0.1103 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | CHASE 3 | 0.9486 | 0.8325 | -0.1161 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | WTCLFTP3 | 0.9371 | 0.8325 | -0.1046 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | CHASE 3 | 0.9428 | 0.8325 | -0.1103 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | CHASE 3 | 0.9486 | 0.8325 | -0.1161 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | SHARNSP3 | 0.9428 | 0.8326 | -0.1102 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | SHARNSP3 | 0.9487 | 0.8326 | -0.1161 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | SHARNSP3 | 0.9428 | 0.8326 | -0.1102 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | SHARNSP3 | 0.9487 | 0.8326 | -0.1161 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | SHARNSP3 | 0.9428 | 0.8326 | -0.1102 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | SHARNSP3 | 0.9487 | 0.8326 | -0.1161 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | NSI | 0.9504 | 0.8343 | -0.1161 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | NSI | 0.9542 | 0.8343 | -0.1199 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | NSI | 0.9504 | 0.8343 | -0.1161 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | NSI | 0.9542 | 0.8343 | -0.1199 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | NSI | 0.9504 | 0.8343 | -0.1161 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | NSI | 0.9542 | 0.8343 | -0.1199 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | CHASE 3 | 0.9428 | 0.8346 | -0.1082 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | CHASE 3 | 0.9428 | 0.8346 | -0.1082 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | CHASE 3 | 0.9428 | 0.8346 | -0.1082 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | SHARNSP3 | 0.9428 | 0.8347 | -0.1081 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | SHARNSP3 | 0.9428 | 0.8347 | -0.1081 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | SHARNSP3 | 0.9428 | 0.8347 | -0.1081 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | TRIBUNE3 | 0.9443 | 0.8348 | -0.1095 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | TRIBUNE3 | 0.9443 | 0.8348 | -0.1095 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | TRIBUNE3 | 0.9443 | 0.8348 | -0.1095 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | TRIB SW3 | 0.9443 | 0.8351 | -0.1092 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | TRIB SW3 | 0.9443 | 0.8351 | -0.1092 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | TRIB SW3 | 0.9443 | 0.8351 | -0.1092 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | NSI | 0.9504 | 0.8352 | -0.1152 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | NSI TAP3 | 0.9511 | 0.8352 | -0.1159 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | NSI TAP3 | 0.955 | 0.8352 | -0.1198 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | PALMER3 | 0.9539 | 0.8352 | -0.1187 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | NSI | 0.9504 | 0.8352 | -0.1152 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | NSI TAP3 | 0.9511 | 0.8352 | -0.1159 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | NSI TAP3 | 0.955 | 0.8352 | -0.1198 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | PALMER3 | 0.9539 | 0.8352 | -0.1187 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | NSI | 0.9504 | 0.8352 | -0.1152 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | NSI TAP3 | 0.9511 | 0.8352 | -0.1159 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | NSI TAP3 | 0.955 | 0.8352 | -0.1198 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | PALMER3 | 0.9539 | 0.8352 | -0.1187 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | WTCLF 3 | 0.9507 | 0.8362 | -0.1145 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | NSI TAP3 | 0.9511 | 0.8362 | -0.1149 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | WTCLF 3 | 0.9507 | 0.8362 | -0.1145 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | NSI TAP3 | 0.9511 | 0.8362 | -0.1149 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | WTCLF 3 | 0.9507 | 0.8362 | -0.1145 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | NSI TAP3 | 0.9511 | 0.8362 | -0.1149 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | WTCLFTP3 | 0.9517 | 0.8373 | -0.1144 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | WTCLFTP3 | 0.9517 | 0.8373 | -0.1144 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | WTCLFTP3 | 0.9517 | 0.8373 | -0.1144 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | CHASE 3 | 0.9532 | 0.8375 | -0.1157 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | CHASE 3 | 0.9532 | 0.8375 | -0.1157 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | CHASE 3 | 0.9532 | 0.8375 | -0.1157 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | SHARNSP3 | 0.9533 | 0.8376 | -0.1157 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | SHARNSP3 | 0.9533 | 0.8376 | -0.1157 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | SHARNSP3 | 0.9533 | 0.8376 | -0.1157 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | TRIBUNE3 | 0.9561 | 0.8388 | -0.1173 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | TRIBUNE3 | 0.9561 | 0.8388 | -0.1173 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | TRIBUNE3 | 0.9561 | 0.8388 | -0.1173 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | KANARAD3 | 0.963 | 0.8389 | -0.1241 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | KANARAD3 | 0.963 | 0.8389 | -0.1241 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | KANARAD3 | 0.963 | 0.8389 | -0.1241 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | TRIB SW3 | 0.9563 | 0.8392 | -0.1171 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | TRIB SW3 | 0.9563 | 0.8392 | -0.1171 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | TRIB SW3 | 0.9563 | 0.8392 | -0.1171 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | SELKIRK3 | 0.9446 | 0.8395 | -0.1051 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | SELKIRK3 | 0.9446 | 0.8395 | -0.1051 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | SELKIRK3 | 0.9446 | 0.8395 | -0.1051 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | NSI | 0.9674 | 0.8398 | -0.1276 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | NSI | 0.9713 | 0.8398 | -0.1315 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | NSI | 0.9674 | 0.8398 | -0.1276 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | NSI | 0.9713 | 0.8398 | -0.1315 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | NSI | 0.9674 | 0.8398 | -0.1276 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | NSI | 0.9713 | 0.8398 | -0.1315 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | NSI TAP3 | 0.9682 | 0.8407 | -0.1275 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | NSI TAP3 | 0.9721 | 0.8407 | -0.1314 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | NSI TAP3 | 0.9682 | 0.8407 | -0.1275 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | NSI TAP3 | 0.9721 | 0.8407 | -0.1314 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | NSI TAP3 | 0.9682 | 0.8407 | -0.1275 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | NSI TAP3 | 0.9721 | 0.8407 | -0.1314 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | LEOTI 3 | 0.9452 | 0.8422 | -0.103 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | LEOTI 3 | 0.9452 | 0.8422 | -0.103 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | LEOTI 3 | 0.9452 | 0.8422 | -0.103 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | GANO 3 | 0.9405 | 0.8426 | -0.0979 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | GANO 3 | 0.9405 | 0.8426 | -0.0979 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | GANO 3 | 0.9405 | 0.8426 | -0.0979 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | SELKIRK3 | 0.9578 | 0.8443 | -0.1135 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | SELKIRK3 | 0.9578 | 0.8443 | -0.1135 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | SELKIRK3 | 0.9578 | 0.8443 | -0.1135 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | SCOTCTY3 | 0.9428 | 0.8447 | -0.0981 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | SCOTCTY3 | 0.9428 | 0.8447 | -0.0981 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | SCOTCTY3 | 0.9428 | 0.8447 | -0.0981 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | MANNING3 | 0.939 | 0.8459 | -0.0931 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | MANNING3 | 0.939 | 0.8459 | -0.0931 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | MANNING3 | 0.939 | 0.8459 | -0.0931 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | RULETON3 | 0.9564 | 0.8463 | -0.1101 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | RULETON3 | 0.9599 | 0.8463 | -0.1136 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | RULETON3 | 0.9564 | 0.8463 | -0.1101 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | RULETON3 | 0.9599 | 0.8463 | -0.1136 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | RULETON3 | 0.9564 | 0.8463 | -0.1101 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | RULETON3 | 0.9599 | 0.8463 | -0.1136 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | RULETON3 | 0.9564 | 0.8466 | -0.1098 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | RULETON3 | 0.9564 | 0.8466 | -0.1098 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | RULETON3 | 0.9564 | 0.8466 | -0.1098 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | NSI | 0.9674 | 0.8469 | -0.1205 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | NSI | 0.9674 | 0.8469 | -0.1205 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | NSI | 0.9674 | 0.8469 | -0.1205 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | MANNGT 3 | 0.9401 | 0.8471 | -0.093 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | MANNGT 3 | 0.9401 | 0.8471 | -0.093 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | MANNGT 3 | 0.9401 | 0.8471 | -0.093 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | LEOTI 3 | 0.9588 | 0.8472 | -0.1116 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | LEOTI 3 | 0.9588 | 0.8472 | -0.1116 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | LEOTI 3 | 0.9588 | 0.8472 | -0.1116 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | NSI TAP3 | 0.9682 | 0.8478 | -0.1204 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | NSI TAP3 | 0.9682 | 0.8478 | -0.1204 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | NSI TAP3 | 0.9682 | 0.8478 | -0.1204 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | GANO 3 | 0.9494 | 0.8482 | -0.1012 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | GANO 3 | 0.9494 | 0.8482 | -0.1012 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | GANO 3 | 0.9494 | 0.8482 | -0.1012 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | KANARAD3 | 0.944 | 0.8489 | -0.0951 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | KANARAD3 | 0.944 | 0.8489 | -0.0951 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | KANARAD3 | 0.944 | 0.8489 | -0.0951 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | LAWNRID3 | 0.953 | 0.8497 | -0.1033 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | LAWNRID3 | 0.953 | 0.8497 | -0.1033 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | LAWNRID3 | 0.953 | 0.8497 | -0.1033 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | LAWNRID3 | 0.953 | 0.8498 | -0.1032 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | LAWNRID3 | 0.9562 | 0.8498 | -0.1064 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | LAWNRID3 | 0.953 | 0.8498 | -0.1032 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | LAWNRID3 | 0.9562 | 0.8498 | -0.1064 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | LAWNRID3 | 0.953 | 0.8498 | -0.1032 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | LAWNRID3 | 0.9562 | 0.8498 | -0.1064 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | SCOTCTY3 | 0.9571 | 0.85 | -0.1071 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | SCOTCTY3 | 0.9571 | 0.85 | -0.1071 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | SCOTCTY3 | 0.9571 | 0.85 | -0.1071 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | MANNING3 | 0.953 | 0.851 | -0.102 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | MANNING3 | 0.953 | 0.851 | -0.102 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | MANNING3 | 0.953 | 0.851 | -0.102 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | MANNGT 3 | 0.954 | 0.8522 | -0.1018 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | MANNGT 3 | 0.954 | 0.8522 | -0.1018 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | MANNGT 3 | 0.954 | 0.8522 | -0.1018 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | DIGHTON3 | 0.9378 | 0.8526 | -0.0852 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | DIGHTON3 | 0.9378 | 0.8526 | -0.0852 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | DIGHTON3 | 0.9378 | 0.8526 | -0.0852 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | RULETON3 | 0.9746 | 0.8528 | -0.1218 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | RULETON3 | 0.978 | 0.8528 | -0.1252 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | RULETON3 | 0.9746 | 0.8528 | -0.1218 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | RULETON3 | 0.978 | 0.8528 | -0.1252 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | RULETON3 | 0.9746 | 0.8528 | -0.1218 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | RULETON3 | 0.978 | 0.8528 | -0.1252 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | JAGGER 3 | 0.9385 | 0.8533 | -0.0852 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | JAGGER 3 | 0.9385 | 0.8533 | -0.0852 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | JAGGER 3 | 0.9385 | 0.8533 | -0.0852 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | CNTRLPL3 | 0.9511 | 0.854 | -0.0971 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | CNTRLPL3 | 0.9511 | 0.854 | -0.0971 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | CNTRLPL3 | 0.9511 | 0.854 | -0.0971 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | KANARAD3 | 0.9596 | 0.8543 | -0.1053 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | KANARAD3 | 0.9596 | 0.8543 | -0.1053 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | KANARAD3 | 0.9596 | 0.8543 | -0.1053 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | LIBERTY3 | 0.9341 | 0.8553 | -0.0788 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | LIBERTY3 | 0.9341 | 0.8553 | -0.0788 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | LIBERTY3 | 0.9341 | 0.8553 | -0.0788 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | ELLIS 2 | 0.9466 | 0.8564 | -0.0902 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | ELLIS 2 | 0.9516 | 0.8564 | -0.0952 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | ELLIS 2 | 0.9466 | 0.8564 | -0.0902 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | ELLIS 2 | 0.9516 | 0.8564 | -0.0952 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | ELLIS 2 | 0.9466 | 0.8564 | -0.0902 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | ELLIS 2 | 0.9516 | 0.8564 | -0.0952 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | NSI | 0.9469 | 0.8568 | -0.0901 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | NSI | 0.9469 | 0.8568 | -0.0901 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | NSI | 0.9469 | 0.8568 | -0.0901 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | LAWNRID3 | 0.9713 | 0.8569 | -0.1144 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | LAWNRID3 | 0.9744 | 0.8569 | -0.1175 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | LAWNRID3 | 0.9713 | 0.8569 | -0.1144 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | LAWNRID3 | 0.9744 | 0.8569 | -0.1175 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | LAWNRID3 | 0.9713 | 0.8569 | -0.1144 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | LAWNRID3 | 0.9744 | 0.8569 | -0.1175 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | DIGHTON3 | 0.9513 | 0.8576 | -0.0937 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | DIGHTON3 | 0.9513 | 0.8576 | -0.0937 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | DIGHTON3 | 0.9513 | 0.8576 | -0.0937 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | NSI TAP3 | 0.9477 | 0.8577 | -0.09 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | SETAB 3 | 0.9484 | 0.8577 | -0.0907 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | NSI TAP3 | 0.9477 | 0.8577 | -0.09 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | SETAB 3 | 0.9484 | 0.8577 | -0.0907 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | NSI TAP3 | 0.9477 | 0.8577 | -0.09 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | SETAB 3 | 0.9484 | 0.8577 | -0.0907 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | CSTFRAN3 | 0.9527 | 0.8578 | -0.0949 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | CSTFRAN3 | 0.9527 | 0.8578 | -0.0949 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | CSTFRAN3 | 0.9527 | 0.8578 | -0.0949 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | STFRANT3 | 0.9529 | 0.858 | -0.0949 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | STFRANT3 | 0.9529 | 0.858 | -0.0949 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | STFRANT3 | 0.9529 | 0.858 | -0.0949 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | ELLIS 2 | 0.9466 | 0.8581 | -0.0885 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | ELLIS 2 | 0.9466 | 0.8581 | -0.0885 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | ELLIS 2 | 0.9466 | 0.8581 | -0.0885 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | JAGGER 3 | 0.9519 | 0.8583 | -0.0936 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | JAGGER 3 | 0.9519 | 0.8583 | -0.0936 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | JAGGER 3 | 0.9519 | 0.8583 | -0.0936 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | CSTFRAN3 | 0.9527 | 0.8585 | -0.0942 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | CSTFRAN3 | 0.9557 | 0.8585 | -0.0972 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | CSTFRAN3 | 0.9527 | 0.8585 | -0.0942 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | CSTFRAN3 | 0.9557 | 0.8585 | -0.0972 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | CSTFRAN3 | 0.9527 | 0.8585 | -0.0942 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | CSTFRAN3 | 0.9557 | 0.8585 | -0.0972 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | STFRANT3 | 0.9529 | 0.8586 | -0.0943 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | STFRANT3 | 0.9558 | 0.8586 | -0.0972 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | STFRANT3 | 0.9529 | 0.8586 | -0.0943 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | STFRANT3 | 0.9558 | 0.8586 | -0.0972 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | STFRANT3 | 0.9529 | 0.8586 | -0.0943 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | STFRANT3 | 0.9558 | 0.8586 | -0.0972 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | CNTRLPL3 | 0.9657 | 0.8596 | -0.1061 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | CNTRLPL3 | 0.9657 | 0.8596 | -0.1061 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | CNTRLPL3 | 0.9657 | 0.8596 | -0.1061 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | RULETON3 | 0.9746 | 0.8598 | -0.1148 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | RULETON3 | 0.9746 | 0.8598 | -0.1148 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | RULETON3 | 0.9746 | 0.8598 | -0.1148 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | STFRAN 3 | 0.9531 | 0.8599 | -0.0932 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | ELLIS 2 | 0.9568 | 0.8599 | -0.0969 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | ELLIS 2 | 0.962 | 0.8599 | -0.1021 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | STFRAN 3 | 0.9531 | 0.8599 | -0.0932 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | ELLIS 2 | 0.9568 | 0.8599 | -0.0969 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | ELLIS 2 | 0.962 | 0.8599 | -0.1021 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | STFRAN 3 | 0.9531 | 0.8599 | -0.0932 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | ELLIS 2 | 0.9568 | 0.8599 | -0.0969 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | ELLIS 2 | 0.962 | 0.8599 | -0.1021 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | LIBERTYT | 0.9383 | 0.86 | -0.0783 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | LIBERTY3 | 0.9468 | 0.86 | -0.0868 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | LIBERTYT | 0.9383 | 0.86 | -0.0783 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | LIBERTY3 | 0.9468 | 0.86 | -0.0868 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | LIBERTYT | 0.9383 | 0.86 | -0.0783 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | LIBERTY3 | 0.9468 | 0.86 | -0.0868 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | STFRAN 3 | 0.9531 | 0.8607 | -0.0924 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | STFRAN 3 | 0.956 | 0.8607 | -0.0953 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | STFRAN 3 | 0.9531 | 0.8607 | -0.0924 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | STFRAN 3 | 0.956 | 0.8607 | -0.0953 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | STFRAN 3 | 0.9531 | 0.8607 | -0.0924 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | STFRAN 3 | 0.956 | 0.8607 | -0.0953 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | NSI | 0.963 | 0.8625 | -0.1005 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | NSI | 0.963 | 0.8625 | -0.1005 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | NSI | 0.963 | 0.8625 | -0.1005 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | RANSOM 2 | 0.9527 | 0.8633 | -0.0894 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | RANSOM 2 | 0.9577 | 0.8633 | -0.0944 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | RANSOM 2 | 0.9527 | 0.8633 | -0.0894 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | RANSOM 2 | 0.9577 | 0.8633 | -0.0944 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | RANSOM 2 | 0.9527 | 0.8633 | -0.0894 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | RANSOM 2 | 0.9577 | 0.8633 | -0.0944 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | NSI TAP3 | 0.9638 | 0.8634 | -0.1004 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | SETAB 3 | 0.9637 | 0.8634 | -0.1003 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | NSI TAP3 | 0.9638 | 0.8634 | -0.1004 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | SETAB 3 | 0.9637 | 0.8634 | -0.1003 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | NSI TAP3 | 0.9638 | 0.8634 | -0.1004 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | SETAB 3 | 0.9637 | 0.8634 | -0.1003 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | LAWNRID3 | 0.9713 | 0.8636 | -0.1077 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | LAWNRID3 | 0.9713 | 0.8636 | -0.1077 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | LAWNRID3 | 0.9713 | 0.8636 | -0.1077 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | GOODCTY3 | 0.9606 | 0.8638 | -0.0968 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | GOODCTY3 | 0.9606 | 0.8638 | -0.0968 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | GOODCTY3 | 0.9606 | 0.8638 | -0.0968 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | LIBERTYT | 0.9509 | 0.8646 | -0.0863 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | LIBERTYT | 0.9509 | 0.8646 | -0.0863 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | LIBERTYT | 0.9509 | 0.8646 | -0.0863 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | ELLIS 2 | 0.9568 | 0.8648 | -0.092 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | ELLIS 2 | 0.9568 | 0.8648 | -0.092 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | ELLIS 2 | 0.9568 | 0.8648 | -0.092 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | GOODCTY3 | 0.9606 | 0.8649 | -0.0957 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | GOODCTY3 | 0.9636 | 0.8649 | -0.0987 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | GOODCTY3 | 0.9606 | 0.8649 | -0.0957 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | GOODCTY3 | 0.9636 | 0.8649 | -0.0987 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | GOODCTY3 | 0.9606 | 0.8649 | -0.0957 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | GOODCTY3 | 0.9636 | 0.8649 | -0.0987 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | RANSOM 2 | 0.9527 | 0.865 | -0.0877 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | RANSOM 2 | 0.9527 | 0.865 | -0.0877 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | RANSOM 2 | 0.9527 | 0.865 | -0.0877 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | ARNOLD3 | 0.9557 | 0.8658 | -0.0899 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | ARNOLD3 | 0.9604 | 0.8658 | -0.0946 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | RANSOM 3 | 0.9548 | 0.8658 | -0.089 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | RANSOM 3 | 0.9597 | 0.8658 | -0.0939 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | ARNOLD3 | 0.9557 | 0.8658 | -0.0899 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | ARNOLD3 | 0.9604 | 0.8658 | -0.0946 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | RANSOM 3 | 0.9548 | 0.8658 | -0.089 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | RANSOM 3 | 0.9597 | 0.8658 | -0.0939 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | ARNOLD3 | 0.9557 | 0.8658 | -0.0899 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | ARNOLD3 | 0.9604 | 0.8658 | -0.0946 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | RANSOM 3 | 0.9548 | 0.8658 | -0.089 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | RANSOM 3 | 0.9597 | 0.8658 | -0.0939 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | CSTFRAN3 | 0.971 | 0.8659 | -0.1051 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | CSTFRAN3 | 0.9739 | 0.8659 | -0.108 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | CSTFRAN3 | 0.971 | 0.8659 | -0.1051 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | CSTFRAN3 | 0.9739 | 0.8659 | -0.108 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | CSTFRAN3 | 0.971 | 0.8659 | -0.1051 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | CSTFRAN3 | 0.9739 | 0.8659 | -0.108 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | STFRANT3 | 0.9711 | 0.8661 | -0.105 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | STFRANT3 | 0.974 | 0.8661 | -0.1079 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | STFRANT3 | 0.9711 | 0.8661 | -0.105 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | STFRANT3 | 0.974 | 0.8661 | -0.1079 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | STFRANT3 | 0.9711 | 0.8661 | -0.105 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | STFRANT3 | 0.974 | 0.8661 | -0.1079 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | SYRACUS3 | 0.9532 | 0.8668 | -0.0864 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | RANSOM 2 | 0.9629 | 0.8668 | -0.0961 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | RANSOM 2 | 0.968 | 0.8668 | -0.1012 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | SYRACUS3 | 0.9532 | 0.8668 | -0.0864 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | RANSOM 2 | 0.9629 | 0.8668 | -0.0961 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | RANSOM 2 | 0.968 | 0.8668 | -0.1012 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | SYRACUS3 | 0.9532 | 0.8668 | -0.0864 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | RANSOM 2 | 0.9629 | 0.8668 | -0.0961 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | RANSOM 2 | 0.968 | 0.8668 | -0.1012 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | ARNOLD3 | 0.9557 | 0.8673 | -0.0884 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | ARNOLD3 | 0.9557 | 0.8673 | -0.0884 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | ARNOLD3 | 0.9557 | 0.8673 | -0.0884 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | RANSOM 3 | 0.9548 | 0.8675 | -0.0873 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | RANSOM 3 | 0.9548 | 0.8675 | -0.0873 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | RANSOM 3 | 0.9548 | 0.8675 | -0.0873 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | RULETON3 | 0.9521 | 0.8678 | -0.0843 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | RULETON3 | 0.9521 | 0.8678 | -0.0843 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | RULETON3 | 0.9521 | 0.8678 | -0.0843 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | GODLNDT3 | 0.9644 | 0.8681 | -0.0963 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | GODLNDT3 | 0.9644 | 0.8681 | -0.0963 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | GODLNDT3 | 0.9644 | 0.8681 | -0.0963 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | STFRAN 3 | 0.9713 | 0.8682 | -0.1031 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | STFRAN 3 | 0.9742 | 0.8682 | -0.106 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | STFRAN 3 | 0.9713 | 0.8682 | -0.1031 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | STFRAN 3 | 0.9742 | 0.8682 | -0.106 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | STFRAN 3 | 0.9713 | 0.8682 | -0.1031 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | STFRAN 3 | 0.9742 | 0.8682 | -0.106 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | GODLNDT3 | 0.9644 | 0.8691 | -0.0953 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | GODLNDT3 | 0.9674 | 0.8691 | -0.0983 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | GODLNDT3 | 0.9644 | 0.8691 | -0.0953 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | GODLNDT3 | 0.9674 | 0.8691 | -0.0983 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | GODLNDT3 | 0.9644 | 0.8691 | -0.0953 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | GODLNDT3 | 0.9674 | 0.8691 | -0.0983 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | BEELER 3 | 0.9423 | 0.8692 | -0.0731 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | BEELER 3 | 0.9423 | 0.8692 | -0.0731 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | BEELER 3 | 0.9423 | 0.8692 | -0.0731 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | LAWNRID3 | 0.948 | 0.8693 | -0.0787 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | LAWNRID3 | 0.948 | 0.8693 | -0.0787 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | LAWNRID3 | 0.948 | 0.8693 | -0.0787 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | RANSOM 3 | 0.965 | 0.8694 | -0.0956 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | RANSOM 3 | 0.97 | 0.8694 | -0.1006 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | RANSOM 3 | 0.965 | 0.8694 | -0.0956 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | RANSOM 3 | 0.97 | 0.8694 | -0.1006 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | RANSOM 3 | 0.965 | 0.8694 | -0.0956 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | RANSOM 3 | 0.97 | 0.8694 | -0.1006 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | SYRACUS3 | 0.9597 | 0.8695 | -0.0902 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | SYRACUS3 | 0.9597 | 0.8695 | -0.0902 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | SYRACUS3 | 0.9597 | 0.8695 | -0.0902 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | ARNOLD3 | 0.9667 | 0.8698 | -0.0969 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | ARNOLD3 | 0.9716 | 0.8698 | -0.1018 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | ARNOLD3 | 0.9667 | 0.8698 | -0.0969 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | ARNOLD3 | 0.9716 | 0.8698 | -0.1018 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | ARNOLD3 | 0.9667 | 0.8698 | -0.0969 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | ARNOLD3 | 0.9716 | 0.8698 | -0.1018 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | GOODLND3 | 0.9652 | 0.8699 | -0.0953 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | GOODLND3 | 0.9652 | 0.8699 | -0.0953 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | GOODLND3 | 0.9652 | 0.8699 | -0.0953 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | BIRDCTY3 | 0.9565 | 0.8701 | -0.0864 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | BIRDCTY3 | 0.9565 | 0.8701 | -0.0864 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | BIRDCTY3 | 0.9565 | 0.8701 | -0.0864 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | GOODLND3 | 0.9652 | 0.8711 | -0.0941 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | GOODLND3 | 0.9682 | 0.8711 | -0.0971 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | GOODLND3 | 0.9652 | 0.8711 | -0.0941 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | GOODLND3 | 0.9682 | 0.8711 | -0.0971 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | GOODLND3 | 0.9652 | 0.8711 | -0.0941 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | GOODLND3 | 0.9682 | 0.8711 | -0.0971 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | BIRDCTY3 | 0.9565 | 0.8712 | -0.0853 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | BIRDCTY3 | 0.9592 | 0.8712 | -0.088 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | BIRDCTY3 | 0.9565 | 0.8712 | -0.0853 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | BIRDCTY3 | 0.9592 | 0.8712 | -0.088 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | BIRDCTY3 | 0.9565 | 0.8712 | -0.0853 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | BIRDCTY3 | 0.9592 | 0.8712 | -0.088 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | RANSOM 2 | 0.9629 | 0.8716 | -0.0913 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | RANSOM 2 | 0.9629 | 0.8716 | -0.0913 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | RANSOM 2 | 0.9629 | 0.8716 | -0.0913 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | NESSCTY3 | 0.9535 | 0.872 | -0.0815 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | NESSCTY3 | 0.9591 | 0.872 | -0.0871 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | NESSCTY3 | 0.9535 | 0.872 | -0.0815 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | NESSCTY3 | 0.9591 | 0.872 | -0.0871 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | NESSCTY3 | 0.9535 | 0.872 | -0.0815 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | NESSCTY3 | 0.9591 | 0.872 | -0.0871 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | NESCTY 3 | 0.9535 | 0.8721 | -0.0814 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | NESCTY 3 | 0.9592 | 0.8721 | -0.0871 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | CSTFRAN3 | 0.971 | 0.8721 | -0.0989 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | NESCTY 3 | 0.9535 | 0.8721 | -0.0814 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | NESCTY 3 | 0.9592 | 0.8721 | -0.0871 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | CSTFRAN3 | 0.971 | 0.8721 | -0.0989 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | NESCTY 3 | 0.9535 | 0.8721 | -0.0814 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | NESCTY 3 | 0.9592 | 0.8721 | -0.0871 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | CSTFRAN3 | 0.971 | 0.8721 | -0.0989 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | STFRANT3 | 0.9711 | 0.8723 | -0.0988 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | STFRANT3 | 0.9711 | 0.8723 | -0.0988 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | STFRANT3 | 0.9711 | 0.8723 | -0.0988 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | GOODCTY3 | 0.9802 | 0.8727 | -0.1075 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | GOODCTY3 | 0.9832 | 0.8727 | -0.1105 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | GOODCTY3 | 0.9802 | 0.8727 | -0.1075 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | GOODCTY3 | 0.9832 | 0.8727 | -0.1105 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | GOODCTY3 | 0.9802 | 0.8727 | -0.1075 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | GOODCTY3 | 0.9832 | 0.8727 | -0.1105 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | CHASE 3 | 0.943 | 0.8735 | -0.0695 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | BEELER 3 | 0.9542 | 0.8735 | -0.0807 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | CHASE 3 | 0.943 | 0.8735 | -0.0695 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | BEELER 3 | 0.9542 | 0.8735 | -0.0807 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | CHASE 3 | 0.943 | 0.8735 | -0.0695 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | BEELER 3 | 0.9542 | 0.8735 | -0.0807 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | SHARNSP3 | 0.9431 | 0.8736 | -0.0695 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | SHARNSP3 | 0.9431 | 0.8736 | -0.0695 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | SHARNSP3 | 0.9431 | 0.8736 | -0.0695 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | CSTFRAN3 | 0.9459 | 0.8737 | -0.0722 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | CSTFRAN3 | 0.9459 | 0.8737 | -0.0722 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | CSTFRAN3 | 0.9459 | 0.8737 | -0.0722 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | RULETON3 | 0.9687 | 0.8738 | -0.0949 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | RULETON3 | 0.9687 | 0.8738 | -0.0949 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | RULETON3 | 0.9687 | 0.8738 | -0.0949 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | STFRANT3 | 0.9461 | 0.8739 | -0.0722 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | STFRANT3 | 0.9461 | 0.8739 | -0.0722 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | STFRANT3 | 0.9461 | 0.8739 | -0.0722 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | NESSCTY3 | 0.9535 | 0.874 | -0.0795 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | NESSCTY3 | 0.9535 | 0.874 | -0.0795 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | NESSCTY3 | 0.9535 | 0.874 | -0.0795 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | NESCTY 3 | 0.9535 | 0.8741 | -0.0794 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | NESCTY 3 | 0.9535 | 0.8741 | -0.0794 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | NESCTY 3 | 0.9535 | 0.8741 | -0.0794 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | PILE 3 | 0.9453 | 0.8742 | -0.0711 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | RANSOM 3 | 0.965 | 0.8742 | -0.0908 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | NESSCTY3 | 0.961 | 0.8742 | -0.0868 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | NESSCTY3 | 0.9669 | 0.8742 | -0.0927 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | PILE 3 | 0.9453 | 0.8742 | -0.0711 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | RANSOM 3 | 0.965 | 0.8742 | -0.0908 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | NESSCTY3 | 0.961 | 0.8742 | -0.0868 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | NESSCTY3 | 0.9669 | 0.8742 | -0.0927 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | PILE 3 | 0.9453 | 0.8742 | -0.0711 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | RANSOM 3 | 0.965 | 0.8742 | -0.0908 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | NESSCTY3 | 0.961 | 0.8742 | -0.0868 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | NESSCTY3 | 0.9669 | 0.8742 | -0.0927 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | NESCTY 3 | 0.9611 | 0.8743 | -0.0868 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | NESCTY 3 | 0.9669 | 0.8743 | -0.0926 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | STFRAN 3 | 0.9713 | 0.8743 | -0.097 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | NESCTY 3 | 0.9611 | 0.8743 | -0.0868 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | NESCTY 3 | 0.9669 | 0.8743 | -0.0926 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | STFRAN 3 | 0.9713 | 0.8743 | -0.097 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | NESCTY 3 | 0.9611 | 0.8743 | -0.0868 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | NESCTY 3 | 0.9669 | 0.8743 | -0.0926 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | STFRAN 3 | 0.9713 | 0.8743 | -0.097 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | ARNOLD3 | 0.9667 | 0.8748 | -0.0919 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | PALMER3 | 0.9642 | 0.8748 | -0.0894 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | PALMER3 | 0.9709 | 0.8748 | -0.0961 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | ARNOLD3 | 0.9667 | 0.8748 | -0.0919 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | PALMER3 | 0.9642 | 0.8748 | -0.0894 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | PALMER3 | 0.9709 | 0.8748 | -0.0961 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | ARNOLD3 | 0.9667 | 0.8748 | -0.0919 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | PALMER3 | 0.9642 | 0.8748 | -0.0894 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | PALMER3 | 0.9709 | 0.8748 | -0.0961 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | STFRAN 3 | 0.9459 | 0.875 | -0.0709 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | STFRAN 3 | 0.9459 | 0.875 | -0.0709 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | STFRAN 3 | 0.9459 | 0.875 | -0.0709 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | LAWNRID3 | 0.9645 | 0.8754 | -0.0891 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | LAWNRID3 | 0.9645 | 0.8754 | -0.0891 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | LAWNRID3 | 0.9645 | 0.8754 | -0.0891 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | BEELER 3 | 0.9513 | 0.8758 | -0.0755 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | BEELER 3 | 0.9583 | 0.8758 | -0.0825 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | BEELER 3 | 0.9513 | 0.8758 | -0.0755 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | BEELER 3 | 0.9583 | 0.8758 | -0.0825 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | BEELER 3 | 0.9513 | 0.8758 | -0.0755 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | BEELER 3 | 0.9583 | 0.8758 | -0.0825 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | GODLNDT3 | 0.9839 | 0.8769 | -0.107 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | GODLNDT3 | 0.9868 | 0.8769 | -0.1099 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | GODLNDT3 | 0.9839 | 0.8769 | -0.107 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | GODLNDT3 | 0.9868 | 0.8769 | -0.1099 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | GODLNDT3 | 0.9839 | 0.8769 | -0.107 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | GODLNDT3 | 0.9868 | 0.8769 | -0.1099 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | GOODCTY3 | 0.9517 | 0.8771 | -0.0746 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | GOODCTY3 | 0.9517 | 0.8771 | -0.0746 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | GOODCTY3 | 0.9517 | 0.8771 | -0.0746 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | GOVE 3 | 0.963 | 0.8772 | -0.0858 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | GOVE 3 | 0.963 | 0.8772 | -0.0858 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | GOVE 3 | 0.9665 | 0.8772 | -0.0893 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | GOVE 3 | 0.963 | 0.8772 | -0.0858 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | GOVE 3 | 0.963 | 0.8772 | -0.0858 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | GOVE 3 | 0.9665 | 0.8772 | -0.0893 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | GOVE 3 | 0.963 | 0.8772 | -0.0858 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | GOVE 3 | 0.963 | 0.8772 | -0.0858 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | GOVE 3 | 0.9665 | 0.8772 | -0.0893 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | BEELER 3 | 0.9513 | 0.8773 | -0.074 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | BEELER 3 | 0.9513 | 0.8773 | -0.074 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | BEELER 3 | 0.9513 | 0.8773 | -0.074 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | BEELER 3 | 0.9578 | 0.8775 | -0.0803 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | BEELER 3 | 0.965 | 0.8775 | -0.0875 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | BEELER 3 | 0.9578 | 0.8775 | -0.0803 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | BEELER 3 | 0.965 | 0.8775 | -0.0875 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | BEELER 3 | 0.9578 | 0.8775 | -0.0803 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | BEELER 3 | 0.965 | 0.8775 | -0.0875 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | WTCLF 3 | 0.9432 | 0.8776 | -0.0656 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | WTCLF 3 | 0.9432 | 0.8776 | -0.0656 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | WTCLF 3 | 0.9432 | 0.8776 | -0.0656 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | PALMER3 | 0.9642 | 0.8777 | -0.0865 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | PALMER3 | 0.9642 | 0.8777 | -0.0865 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | PALMER3 | 0.9642 | 0.8777 | -0.0865 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | PALMER3 | 0.9575 | 0.8779 | -0.0796 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | PALMER3 | 0.9642 | 0.8779 | -0.0863 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | PALMER3 | 0.9575 | 0.8779 | -0.0796 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | PALMER3 | 0.9642 | 0.8779 | -0.0863 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | PALMER3 | 0.9575 | 0.8779 | -0.0796 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | PALMER3 | 0.9642 | 0.8779 | -0.0863 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | NESCTY 3 | 0.9611 | 0.8783 | -0.0828 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | NESSCTY3 | 0.961 | 0.8783 | -0.0827 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | NESCTY 3 | 0.9611 | 0.8783 | -0.0828 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | NESSCTY3 | 0.961 | 0.8783 | -0.0827 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | NESCTY 3 | 0.9611 | 0.8783 | -0.0828 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | NESSCTY3 | 0.961 | 0.8783 | -0.0827 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | PALMER3 | 0.9492 | 0.8785 | -0.0707 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | PALMER3 | 0.9492 | 0.8785 | -0.0707 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | PALMER3 | 0.9492 | 0.8785 | -0.0707 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | WTCLFTP3 | 0.9442 | 0.8786 | -0.0656 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | WTCLFTP3 | 0.9442 | 0.8786 | -0.0656 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | WTCLFTP3 | 0.9442 | 0.8786 | -0.0656 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | PALMER3 | 0.9575 | 0.8787 | -0.0788 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | PALMER3 | 0.9575 | 0.8787 | -0.0788 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | PALMER3 | 0.9575 | 0.8787 | -0.0788 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | GOODLND3 | 0.9848 | 0.8789 | -0.1059 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | GOODLND3 | 0.9877 | 0.8789 | -0.1088 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | BIRDCTY3 | 0.9746 | 0.8789 | -0.0957 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | BIRDCTY3 | 0.9773 | 0.8789 | -0.0984 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | GOODLND3 | 0.9848 | 0.8789 | -0.1059 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | GOODLND3 | 0.9877 | 0.8789 | -0.1088 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | BIRDCTY3 | 0.9746 | 0.8789 | -0.0957 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | BIRDCTY3 | 0.9773 | 0.8789 | -0.0984 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | GOODLND3 | 0.9848 | 0.8789 | -0.1059 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | GOODLND3 | 0.9877 | 0.8789 | -0.1088 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | BIRDCTY3 | 0.9746 | 0.8789 | -0.0957 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | BIRDCTY3 | 0.9773 | 0.8789 | -0.0984 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | GOODCTY3 | 0.9802 | 0.8791 | -0.1011 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | GOODCTY3 | 0.9802 | 0.8791 | -0.1011 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | GOODCTY3 | 0.9802 | 0.8791 | -0.1011 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | LIBERTY3 | 0.9377 | 0.8798 | -0.0579 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | LIBERTY3 | 0.9377 | 0.8798 | -0.0579 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | LIBERTY3 | 0.9377 | 0.8798 | -0.0579 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | CSTFRAN3 | 0.9622 | 0.8799 | -0.0823 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | CSTFRAN3 | 0.9622 | 0.8799 | -0.0823 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | CSTFRAN3 | 0.9622 | 0.8799 | -0.0823 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | STFRANT3 | 0.9624 | 0.88 | -0.0824 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | STFRANT3 | 0.9624 | 0.88 | -0.0824 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | STFRANT3 | 0.9624 | 0.88 | -0.0824 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | CHASE 3 | 0.9585 | 0.8803 | -0.0782 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | SHARNSP3 | 0.9586 | 0.8803 | -0.0783 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | CHASE 3 | 0.9585 | 0.8803 | -0.0782 |  | 0.9 | 1.05 | 0.03912 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | SHARNSP3 | 0.9586 | 0.8803 | -0.0783 |  | 0.9 | 1.05 | 0.03912 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | CHASE 3 | 0.9585 | 0.8803 | -0.0782 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | SHARNSP3 | 0.9586 | 0.8803 | -0.0783 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | LIBERTY3 | 0.949 | 0.8805 | -0.0685 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | LIBERTY3 | 0.9569 | 0.8805 | -0.0764 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | LIBERTY3 | 0.949 | 0.8805 | -0.0685 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | LIBERTY3 | 0.9569 | 0.8805 | -0.0764 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | LIBERTY3 | 0.949 | 0.8805 | -0.0685 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | LIBERTY3 | 0.9569 | 0.8805 | -0.0764 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | BEELER 3 | 0.9578 | 0.8807 | -0.0771 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | BEELER 3 | 0.9578 | 0.8807 | -0.0771 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | BEELER 3 | 0.9578 | 0.8807 | -0.0771 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | MCDONLD3 | 0.9603 | 0.881 | -0.0793 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | MCDONLD3 | 0.9603 | 0.881 | -0.0793 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | MCDONLD3 | 0.9603 | 0.881 | -0.0793 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | STFRAN 3 | 0.9621 | 0.8812 | -0.0809 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | STFRAN 3 | 0.9621 | 0.8812 | -0.0809 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | STFRAN 3 | 0.9621 | 0.8812 | -0.0809 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | GODLNDT3 | 0.9556 | 0.8813 | -0.0743 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | GODLNDT3 | 0.9556 | 0.8813 | -0.0743 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | GODLNDT3 | 0.9556 | 0.8813 | -0.0743 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | LIBERTY3 | 0.949 | 0.8814 | -0.0676 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | LIBERTY3 | 0.949 | 0.8814 | -0.0676 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | LIBERTY3 | 0.949 | 0.8814 | -0.0676 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | TRIBUNE3 | 0.9519 | 0.8815 | -0.0704 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | ELLIS 2 | 0.9455 | 0.8815 | -0.064 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | TRIBUNE3 | 0.9519 | 0.8815 | -0.0704 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | ELLIS 2 | 0.9455 | 0.8815 | -0.064 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | TRIBUNE3 | 0.9519 | 0.8815 | -0.0704 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | ELLIS 2 | 0.9455 | 0.8815 | -0.064 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | TRIB SW3 | 0.9519 | 0.8817 | -0.0702 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | PILE 3 | 0.9585 | 0.8817 | -0.0768 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | TRIB SW3 | 0.9519 | 0.8817 | -0.0702 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | PILE 3 | 0.9585 | 0.8817 | -0.0768 |  | 0.9 | 1.05 | 0.03912 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | TRIB SW3 | 0.9519 | 0.8817 | -0.0702 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | PILE 3 | 0.9585 | 0.8817 | -0.0768 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | LIBERTY3 | 0.9547 | 0.8818 | -0.0729 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | LIBERTY3 | 0.9629 | 0.8818 | -0.0811 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | LIBERTY3 | 0.9547 | 0.8818 | -0.0729 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | LIBERTY3 | 0.9629 | 0.8818 | -0.0811 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | LIBERTY3 | 0.9547 | 0.8818 | -0.0729 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | LIBERTY3 | 0.9629 | 0.8818 | -0.0811 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | DIGHTON3 | 0.9424 | 0.8819 | -0.0605 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | DIGHTON3 | 0.9424 | 0.8819 | -0.0605 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | DIGHTON3 | 0.9424 | 0.8819 | -0.0605 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | BIRDCTY3 | 0.948 | 0.8822 | -0.0658 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | BIRDCTY3 | 0.948 | 0.8822 | -0.0658 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | BIRDCTY3 | 0.948 | 0.8822 | -0.0658 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | CHASE 3 | 0.943 | 0.8823 | -0.0607 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | CHASE 3 | 0.943 | 0.8823 | -0.0607 |  | 0.9 | 1.05 | 0.03922 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | CHASE 3 | 0.943 | 0.8823 | -0.0607 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | SHARNSP3 | 0.9431 | 0.8824 | -0.0607 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | SHARNSP3 | 0.9431 | 0.8824 | -0.0607 |  | 0.9 | 1.05 | 0.03922 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | SHARNSP3 | 0.9431 | 0.8824 | -0.0607 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | GOODLND3 | 0.9561 | 0.8825 | -0.0736 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | GOODLND3 | 0.9561 | 0.8825 | -0.0736 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | GOODLND3 | 0.9561 | 0.8825 | -0.0736 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | JAGGER 3 | 0.9431 | 0.8826 | -0.0605 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | MCDONLD3 | 0.9603 | 0.8826 | -0.0777 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | MCDONLD3 | 0.9628 | 0.8826 | -0.0802 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | JAGGER 3 | 0.9431 | 0.8826 | -0.0605 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | MCDONLD3 | 0.9603 | 0.8826 | -0.0777 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | MCDONLD3 | 0.9628 | 0.8826 | -0.0802 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | JAGGER 3 | 0.9431 | 0.8826 | -0.0605 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | MCDONLD3 | 0.9603 | 0.8826 | -0.0777 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | MCDONLD3 | 0.9628 | 0.8826 | -0.0802 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | MANNING3 | 0.9454 | 0.883 | -0.0624 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | MANNING3 | 0.9454 | 0.883 | -0.0624 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | MANNING3 | 0.9454 | 0.883 | -0.0624 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | GODLNDT3 | 0.9839 | 0.8833 | -0.1006 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | GODLNDT3 | 0.9839 | 0.8833 | -0.1006 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | GODLNDT3 | 0.9839 | 0.8833 | -0.1006 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | GOVE 3 | 0.9779 | 0.8835 | -0.0944 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | GOVE 3 | 0.9815 | 0.8835 | -0.098 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | GOVE 3 | 0.9779 | 0.8835 | -0.0944 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | GOVE 3 | 0.9815 | 0.8835 | -0.098 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | GOVE 3 | 0.9779 | 0.8835 | -0.0944 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | GOVE 3 | 0.9815 | 0.8835 | -0.098 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | ONEOK 3 | 0.9608 | 0.8838 | -0.077 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | GOODCTY3 | 0.9693 | 0.8838 | -0.0855 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | ONEOK 3 | 0.9608 | 0.8838 | -0.077 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | GOODCTY3 | 0.9693 | 0.8838 | -0.0855 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | ONEOK 3 | 0.9608 | 0.8838 | -0.077 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | GOODCTY3 | 0.9693 | 0.8838 | -0.0855 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | MANNGT 3 | 0.9464 | 0.8841 | -0.0623 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | MANNGT 3 | 0.9464 | 0.8841 | -0.0623 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | MANNGT 3 | 0.9464 | 0.8841 | -0.0623 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | LIBERTYT | 0.9419 | 0.8843 | -0.0576 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | LIBERTY3 | 0.9547 | 0.8843 | -0.0704 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | LIBERTYT | 0.9419 | 0.8843 | -0.0576 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | LIBERTY3 | 0.9547 | 0.8843 | -0.0704 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | LIBERTYT | 0.9419 | 0.8843 | -0.0576 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | LIBERTY3 | 0.9547 | 0.8843 | -0.0704 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | SELKIRK3 | 0.9521 | 0.8844 | -0.0677 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | SELKIRK3 | 0.9521 | 0.8844 | -0.0677 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | SELKIRK3 | 0.9521 | 0.8844 | -0.0677 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | WTCLF 3 | 0.9432 | 0.8846 | -0.0586 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | BIRDCTY3 | 0.9746 | 0.8846 | -0.09 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | WTCLF 3 | 0.9432 | 0.8846 | -0.0586 |  | 0.9 | 1.05 | 0.03922 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | BIRDCTY3 | 0.9746 | 0.8846 | -0.09 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | WTCLF 3 | 0.9432 | 0.8846 | -0.0586 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | BIRDCTY3 | 0.9746 | 0.8846 | -0.09 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | WTCLF 3 | 0.9598 | 0.8847 | -0.0751 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | GANO 3 | 0.9481 | 0.8847 | -0.0634 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | WTCLF 3 | 0.9598 | 0.8847 | -0.0751 |  | 0.9 | 1.05 | 0.03912 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | GANO 3 | 0.9481 | 0.8847 | -0.0634 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | WTCLF 3 | 0.9598 | 0.8847 | -0.0751 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | GANO 3 | 0.9481 | 0.8847 | -0.0634 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | BVERVLLY | 0.9617 | 0.8848 | -0.0769 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | BVERVLLY | 0.9617 | 0.8848 | -0.0769 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | BVERVLLY | 0.9617 | 0.8848 | -0.0769 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | LIBERTYT | 0.9532 | 0.885 | -0.0682 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | LIBERTYT | 0.9611 | 0.885 | -0.0761 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | LIBERTYT | 0.9532 | 0.885 | -0.0682 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | LIBERTYT | 0.9611 | 0.885 | -0.0761 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | LIBERTYT | 0.9532 | 0.885 | -0.0682 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | LIBERTYT | 0.9611 | 0.885 | -0.0761 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | GOODLND3 | 0.9848 | 0.8852 | -0.0996 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | GOODLND3 | 0.9848 | 0.8852 | -0.0996 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | GOODLND3 | 0.9848 | 0.8852 | -0.0996 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | PALMER3 | 0.9637 | 0.8853 | -0.0784 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | PALMER3 | 0.9637 | 0.8853 | -0.0784 |  | 0.9 | 1.05 | 0.03912 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | PALMER3 | 0.9637 | 0.8853 | -0.0784 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | ONEOK 3 | 0.9608 | 0.8855 | -0.0753 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | ONEOK 3 | 0.9632 | 0.8855 | -0.0777 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | ONEOK 3 | 0.9608 | 0.8855 | -0.0753 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | ONEOK 3 | 0.9632 | 0.8855 | -0.0777 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | ONEOK 3 | 0.9608 | 0.8855 | -0.0753 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | ONEOK 3 | 0.9632 | 0.8855 | -0.0777 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | WTCLFTP3 | 0.9442 | 0.8856 | -0.0586 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | WTCLFTP3 | 0.9442 | 0.8856 | -0.0586 |  | 0.9 | 1.05 | 0.03922 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | WTCLFTP3 | 0.9442 | 0.8856 | -0.0586 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | WTCLFTP3 | 0.9608 | 0.8858 | -0.075 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | WTCLFTP3 | 0.9608 | 0.8858 | -0.075 |  | 0.9 | 1.05 | 0.03912 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | WTCLFTP3 | 0.9608 | 0.8858 | -0.075 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | LIBERTYT | 0.9532 | 0.8859 | -0.0673 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | LIBERTY3 | 0.9516 | 0.8859 | -0.0657 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | ELLIS 2 | 0.9577 | 0.8859 | -0.0718 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | LIBERTYT | 0.9532 | 0.8859 | -0.0673 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | LIBERTY3 | 0.9516 | 0.8859 | -0.0657 |  | 0.9 | 1.05 | 0.03912 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | ELLIS 2 | 0.9577 | 0.8859 | -0.0718 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | LIBERTYT | 0.9532 | 0.8859 | -0.0673 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | LIBERTY3 | 0.9516 | 0.8859 | -0.0657 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | ELLIS 2 | 0.9577 | 0.8859 | -0.0718 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | LEOTI 3 | 0.9526 | 0.8861 | -0.0665 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | LEOTI 3 | 0.9526 | 0.8861 | -0.0665 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | LEOTI 3 | 0.9526 | 0.8861 | -0.0665 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | NESSCTY3 | 0.9514 | 0.8862 | -0.0652 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | NESSCTY3 | 0.9514 | 0.8862 | -0.0652 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | NESSCTY3 | 0.9514 | 0.8862 | -0.0652 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | NESCTY 3 | 0.9514 | 0.8863 | -0.0651 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | LIBERTYT | 0.9588 | 0.8863 | -0.0725 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | LIBERTYT | 0.967 | 0.8863 | -0.0807 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | NESCTY 3 | 0.9514 | 0.8863 | -0.0651 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | LIBERTYT | 0.9588 | 0.8863 | -0.0725 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | LIBERTYT | 0.967 | 0.8863 | -0.0807 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | NESCTY 3 | 0.9514 | 0.8863 | -0.0651 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | LIBERTYT | 0.9588 | 0.8863 | -0.0725 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | LIBERTYT | 0.967 | 0.8863 | -0.0807 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | BVERVLLY | 0.9617 | 0.8865 | -0.0752 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | BVERVLLY | 0.9641 | 0.8865 | -0.0776 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | BVERVLLY | 0.9617 | 0.8865 | -0.0752 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | BVERVLLY | 0.9641 | 0.8865 | -0.0776 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | BVERVLLY | 0.9617 | 0.8865 | -0.0752 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | BVERVLLY | 0.9641 | 0.8865 | -0.0776 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | SCOTCTY3 | 0.9503 | 0.8867 | -0.0636 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | SCOTCTY3 | 0.9503 | 0.8867 | -0.0636 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | SCOTCTY3 | 0.9503 | 0.8867 | -0.0636 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | CHASE 3 | 0.943 | 0.8876 | -0.0554 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | CHASE 3 | 0.943 | 0.8876 | -0.0554 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | CHASE 3 | 0.943 | 0.8876 | -0.0554 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | SHARNSP3 | 0.9431 | 0.8877 | -0.0554 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | SHARNSP3 | 0.9431 | 0.8877 | -0.0554 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | SHARNSP3 | 0.9431 | 0.8877 | -0.0554 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | PILE 3 | 0.9453 | 0.8878 | -0.0575 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | PILE 3 | 0.9453 | 0.8878 | -0.0575 |  | 0.9 | 1.05 | 0.03922 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | PILE 3 | 0.9453 | 0.8878 | -0.0575 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | GODLNDT3 | 0.973 | 0.8879 | -0.0851 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | GODLNDT3 | 0.973 | 0.8879 | -0.0851 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | GODLNDT3 | 0.973 | 0.8879 | -0.0851 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | RANSOM 2 | 0.9515 | 0.8881 | -0.0634 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | RANSOM 2 | 0.9515 | 0.8881 | -0.0634 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | RANSOM 2 | 0.9515 | 0.8881 | -0.0634 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | TRIBUNE3 | 0.9659 | 0.8882 | -0.0777 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | TRIBUNE3 | 0.9659 | 0.8882 | -0.0777 |  | 0.9 | 1.05 | 0.03912 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | TRIBUNE3 | 0.9659 | 0.8882 | -0.0777 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | BIRDCTY3 | 0.964 | 0.8883 | -0.0757 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | BIRDCTY3 | 0.964 | 0.8883 | -0.0757 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | BIRDCTY3 | 0.964 | 0.8883 | -0.0757 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | TRIB SW3 | 0.9661 | 0.8885 | -0.0776 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | TRIB SW3 | 0.9661 | 0.8885 | -0.0776 |  | 0.9 | 1.05 | 0.03912 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | TRIB SW3 | 0.9661 | 0.8885 | -0.0776 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | DIGHTON3 | 0.9573 | 0.8887 | -0.0686 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | GOVE 3 | 0.9779 | 0.8887 | -0.0892 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | DIGHTON3 | 0.9573 | 0.8887 | -0.0686 |  | 0.9 | 1.05 | 0.03912 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | GOVE 3 | 0.9779 | 0.8887 | -0.0892 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | DIGHTON3 | 0.9573 | 0.8887 | -0.0686 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | GOVE 3 | 0.9779 | 0.8887 | -0.0892 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | LIBERTYT | 0.9588 | 0.8888 | -0.07 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | LIBERTYT | 0.9588 | 0.8888 | -0.07 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | LIBERTYT | 0.9588 | 0.8888 | -0.07 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | GOODLND3 | 0.9736 | 0.8892 | -0.0844 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | GOODLND3 | 0.9736 | 0.8892 | -0.0844 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | GOODLND3 | 0.9736 | 0.8892 | -0.0844 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | PALMER3 | 0.9492 | 0.8894 | -0.0598 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | JAGGER 3 | 0.958 | 0.8894 | -0.0686 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | PALMER3 | 0.9492 | 0.8894 | -0.0598 |  | 0.9 | 1.05 | 0.03922 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | JAGGER 3 | 0.958 | 0.8894 | -0.0686 |  | 0.9 | 1.05 | 0.03912 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | PALMER3 | 0.9492 | 0.8894 | -0.0598 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | JAGGER 3 | 0.958 | 0.8894 | -0.0686 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | BEELER 3 | 0.9452 | 0.8898 | -0.0554 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | BEELER 3 | 0.9452 | 0.8898 | -0.0554 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | BEELER 3 | 0.9452 | 0.8898 | -0.0554 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | WTCLF 3 | 0.9432 | 0.8899 | -0.0533 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | WTCLF 3 | 0.9432 | 0.8899 | -0.0533 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | WTCLF 3 | 0.9432 | 0.8899 | -0.0533 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | MCDONLD3 | 0.9503 | 0.89 | -0.0603 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | MCDONLD3 | 0.9503 | 0.89 | -0.0603 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | MCDONLD3 | 0.9503 | 0.89 | -0.0603 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | NESSCTY3 | 0.9624 | 0.8902 | -0.0722 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | NESSCTY3 | 0.9624 | 0.8902 | -0.0722 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | NESSCTY3 | 0.9624 | 0.8902 | -0.0722 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | NESCTY 3 | 0.9624 | 0.8903 | -0.0721 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | NESCTY 3 | 0.9624 | 0.8903 | -0.0721 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | NESCTY 3 | 0.9624 | 0.8903 | -0.0721 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | MANNING3 | 0.9611 | 0.8904 | -0.0707 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | MCDONLD3 | 0.9782 | 0.8904 | -0.0878 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | MCDONLD3 | 0.9807 | 0.8904 | -0.0903 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | LIBERTYT | 0.9558 | 0.8904 | -0.0654 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | MANNING3 | 0.9611 | 0.8904 | -0.0707 |  | 0.9 | 1.05 | 0.03912 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | MCDONLD3 | 0.9782 | 0.8904 | -0.0878 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | MCDONLD3 | 0.9807 | 0.8904 | -0.0903 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | LIBERTYT | 0.9558 | 0.8904 | -0.0654 |  | 0.9 | 1.05 | 0.03912 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | MANNING3 | 0.9611 | 0.8904 | -0.0707 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | MCDONLD3 | 0.9782 | 0.8904 | -0.0878 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | MCDONLD3 | 0.9807 | 0.8904 | -0.0903 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | LIBERTYT | 0.9558 | 0.8904 | -0.0654 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | RANSOM 3 | 0.9536 | 0.8905 | -0.0631 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | RANSOM 3 | 0.9536 | 0.8905 | -0.0631 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | RANSOM 3 | 0.9536 | 0.8905 | -0.0631 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | LIBERTY3 | 0.9377 | 0.8909 | -0.0468 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | LIBERTY3 | 0.9377 | 0.8909 | -0.0468 |  | 0.9 | 1.05 | 0.03922 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | LIBERTY3 | 0.9377 | 0.8909 | -0.0468 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | WTCLFTP3 | 0.9442 | 0.891 | -0.0532 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | WTCLFTP3 | 0.9442 | 0.891 | -0.0532 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | WTCLFTP3 | 0.9442 | 0.891 | -0.0532 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | KANARAD3 | 0.9504 | 0.8914 | -0.059 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | KANARAD3 | 0.9504 | 0.8914 | -0.059 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | KANARAD3 | 0.9504 | 0.8914 | -0.059 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | MANNGT 3 | 0.9621 | 0.8915 | -0.0706 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | MANNGT 3 | 0.9621 | 0.8915 | -0.0706 |  | 0.9 | 1.05 | 0.03912 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | MANNGT 3 | 0.9621 | 0.8915 | -0.0706 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | ONEOK 3 | 0.9503 | 0.8917 | -0.0586 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | ONEOK 3 | 0.9503 | 0.8917 | -0.0586 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | ONEOK 3 | 0.9503 | 0.8917 | -0.0586 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | SELKIRK3 | 0.9674 | 0.8918 | -0.0756 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | SELKIRK3 | 0.9674 | 0.8918 | -0.0756 |  | 0.9 | 1.05 | 0.03912 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | SELKIRK3 | 0.9674 | 0.8918 | -0.0756 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | WILLIAM3 | 0.9612 | 0.8921 | -0.0691 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | GANO 3 | 0.959 | 0.8921 | -0.0669 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | WILLIAM3 | 0.9612 | 0.8921 | -0.0691 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | GANO 3 | 0.959 | 0.8921 | -0.0669 |  | 0.9 | 1.05 | 0.03912 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | WILLIAM3 | 0.9612 | 0.8921 | -0.0691 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | GANO 3 | 0.959 | 0.8921 | -0.0669 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | ARNOLD3 | 0.9545 | 0.8923 | -0.0622 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | PILE 3 | 0.9453 | 0.8923 | -0.053 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | ARNOLD3 | 0.9545 | 0.8923 | -0.0622 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | PILE 3 | 0.9453 | 0.8923 | -0.053 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | ARNOLD3 | 0.9545 | 0.8923 | -0.0622 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | PILE 3 | 0.9453 | 0.8923 | -0.053 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | BVERVLLY | 0.9512 | 0.8926 | -0.0586 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | RANSOM 2 | 0.9638 | 0.8926 | -0.0712 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | BVERVLLY | 0.9512 | 0.8926 | -0.0586 |  | 0.9 | 1.05 | 0.04055 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | RANSOM 2 | 0.9638 | 0.8926 | -0.0712 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | BVERVLLY | 0.9512 | 0.8926 | -0.0586 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | RANSOM 2 | 0.9638 | 0.8926 | -0.0712 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | TRIBUNE3 | 0.9519 | 0.893 | -0.0589 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | TRIBUNE3 | 0.9519 | 0.893 | -0.0589 |  | 0.9 | 1.05 | 0.03922 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | TRIBUNE3 | 0.9519 | 0.893 | -0.0589 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | TRIB SW3 | 0.9519 | 0.8932 | -0.0587 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | TRIB SW3 | 0.9693 | 0.8932 | -0.0761 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | TRIB SW3 | 0.9763 | 0.8932 | -0.0831 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | TRIB SW3 | 0.9519 | 0.8932 | -0.0587 |  | 0.9 | 1.05 | 0.03922 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | TRIB SW3 | 0.9693 | 0.8932 | -0.0761 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | TRIB SW3 | 0.9763 | 0.8932 | -0.0831 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | TRIB SW3 | 0.9519 | 0.8932 | -0.0587 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | TRIB SW3 | 0.9693 | 0.8932 | -0.0761 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | TRIB SW3 | 0.9763 | 0.8932 | -0.0831 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | ONEOK 3 | 0.9787 | 0.8933 | -0.0854 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | ONEOK 3 | 0.9811 | 0.8933 | -0.0878 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | ONEOK 3 | 0.9787 | 0.8933 | -0.0854 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | ONEOK 3 | 0.9811 | 0.8933 | -0.0878 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | ONEOK 3 | 0.9787 | 0.8933 | -0.0854 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | ONEOK 3 | 0.9811 | 0.8933 | -0.0878 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | LEOTI 3 | 0.9683 | 0.8938 | -0.0745 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | LEOTI 3 | 0.9683 | 0.8938 | -0.0745 |  | 0.9 | 1.05 | 0.03912 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | LEOTI 3 | 0.9683 | 0.8938 | -0.0745 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | DIGHTON3 | 0.9424 | 0.8943 | -0.0481 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | BVERVLLY | 0.9796 | 0.8943 | -0.0853 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | BVERVLLY | 0.9819 | 0.8943 | -0.0876 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | DIGHTON3 | 0.9424 | 0.8943 | -0.0481 |  | 0.9 | 1.05 | 0.03922 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | BVERVLLY | 0.9796 | 0.8943 | -0.0853 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | BVERVLLY | 0.9819 | 0.8943 | -0.0876 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | DIGHTON3 | 0.9424 | 0.8943 | -0.0481 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | BVERVLLY | 0.9796 | 0.8943 | -0.0853 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | BVERVLLY | 0.9819 | 0.8943 | -0.0876 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | PALMER3 | 0.9492 | 0.8944 | -0.0548 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | PALMER3 | 0.9492 | 0.8944 | -0.0548 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | PALMER3 | 0.9492 | 0.8944 | -0.0548 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | TRIBUNE3 | 0.9695 | 0.8945 | -0.075 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | TRIBUNE3 | 0.9764 | 0.8945 | -0.0819 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | TRIBUNE3 | 0.9695 | 0.8945 | -0.075 |  | 0.9 | 1.05 | 0.03839 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | TRIBUNE3 | 0.9764 | 0.8945 | -0.0819 |  | 0.9 | 1.05 | 0.03839 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | TRIBUNE3 | 0.9695 | 0.8945 | -0.075 |  | 0.9 | 1.05 | 0.03208 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | TRIBUNE3 | 0.9764 | 0.8945 | -0.0819 |  | 0.9 | 1.05 | 0.03208 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | SCOTCTY3 | 0.9665 | 0.8946 | -0.0719 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | WILLIAM3 | 0.9662 | 0.8946 | -0.0716 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | SCOTCTY3 | 0.9665 | 0.8946 | -0.0719 |  | 0.9 | 1.05 | 0.03912 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | WILLIAM3 | 0.9662 | 0.8946 | -0.0716 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | SCOTCTY3 | 0.9665 | 0.8946 | -0.0719 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | WILLIAM3 | 0.9662 | 0.8946 | -0.0716 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | LIBERTY3 | 0.9377 | 0.895 | -0.0427 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | RANSOM 3 | 0.9658 | 0.895 | -0.0708 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | LIBERTY3 | 0.9377 | 0.895 | -0.0427 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | RANSOM 3 | 0.9658 | 0.895 | -0.0708 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | LIBERTY3 | 0.9377 | 0.895 | -0.0427 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | RANSOM 3 | 0.9658 | 0.895 | -0.0708 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | JAGGER 3 | 0.9431 | 0.8951 | -0.048 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | CHASE 3 | 0.9585 | 0.8951 | -0.0634 |  | 0.9 | 1.05 | 0.033 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | JAGGER 3 | 0.9431 | 0.8951 | -0.048 |  | 0.9 | 1.05 | 0.03922 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | CHASE 3 | 0.9585 | 0.8951 | -0.0634 |  | 0.9 | 1.05 | 0.03912 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | JAGGER 3 | 0.9431 | 0.8951 | -0.048 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | CHASE 3 | 0.9585 | 0.8951 | -0.0634 |  | 0.9 | 1.05 | 0.033 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | SHARNSP3 | 0.9586 | 0.8952 | -0.0634 |  | 0.9 | 1.05 | 0.033 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | TRIB SW3 | 0.9693 | 0.8952 | -0.0741 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | SHARNSP3 | 0.9586 | 0.8952 | -0.0634 |  | 0.9 | 1.05 | 0.03912 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | TRIB SW3 | 0.9693 | 0.8952 | -0.0741 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | SHARNSP3 | 0.9586 | 0.8952 | -0.0634 |  | 0.9 | 1.05 | 0.033 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | TRIB SW3 | 0.9693 | 0.8952 | -0.0741 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | LIBERTYT | 0.9419 | 0.8954 | -0.0465 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | BEELER 3 | 0.9582 | 0.8954 | -0.0628 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27WP | GEN-2023-100 | RUSHMORE-RM8 | 0.9164 | 0.8954 | -0.021 |  | 0.9 | 1.05 | 0.04845 | P42:345:NPPD:BKR-MOR-3312:::: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | LIBERTYT | 0.9419 | 0.8954 | -0.0465 |  | 0.9 | 1.05 | 0.03922 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | BEELER 3 | 0.9582 | 0.8954 | -0.0628 |  | 0.9 | 1.05 | 0.03912 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27WP | GEN-2023-101 | RUSHMORE-RM8 | 0.9164 | 0.8954 | -0.021 |  | 0.9 | 1.05 | 0.04035 | P42:345:NPPD:BKR-MOR-3312:::: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | LIBERTYT | 0.9419 | 0.8954 | -0.0465 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | BEELER 3 | 0.9582 | 0.8954 | -0.0628 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27WP | GEN-2023-102 | RUSHMORE-RM8 | 0.9164 | 0.8954 | -0.021 |  | 0.9 | 1.05 | 0.04845 | P42:345:NPPD:BKR-MOR-3312:::: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | CNTRLPL3 | 0.9584 | 0.8956 | -0.0628 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | CNTRLPL3 | 0.9584 | 0.8956 | -0.0628 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | CNTRLPL3 | 0.9584 | 0.8956 | -0.0628 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | MCDONLD3 | 0.9782 | 0.8957 | -0.0825 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | MCDONLD3 | 0.9782 | 0.8957 | -0.0825 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | MCDONLD3 | 0.9782 | 0.8957 | -0.0825 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27WP | GEN-2023-100 | RUSHMORE-RM8 | 0.9168 | 0.8958 | -0.021 |  | 0.9 | 1.05 | 0.04845 | 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27WP | GEN-2023-100 | RUSHMORE-RM8 | 0.9168 | 0.8958 | -0.021 |  | 0.9 | 1.05 | 0.04845 | EPE Potential P4 Event | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27WP | GEN-2023-101 | RUSHMORE-RM8 | 0.9168 | 0.8958 | -0.021 |  | 0.9 | 1.05 | 0.04035 | 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27WP | GEN-2023-101 | RUSHMORE-RM8 | 0.9168 | 0.8958 | -0.021 |  | 0.9 | 1.05 | 0.04035 | EPE Potential P4 Event | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27WP | GEN-2023-102 | RUSHMORE-RM8 | 0.9168 | 0.8958 | -0.021 |  | 0.9 | 1.05 | 0.04845 | 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27WP | GEN-2023-102 | RUSHMORE-RM8 | 0.9168 | 0.8958 | -0.021 |  | 0.9 | 1.05 | 0.04845 | EPE Potential P4 Event | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | MANNING3 | 0.9454 | 0.896 | -0.0494 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | MCDONLD3 | 0.966 | 0.896 | -0.07 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | MANNING3 | 0.9454 | 0.896 | -0.0494 |  | 0.9 | 1.05 | 0.03922 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | MCDONLD3 | 0.966 | 0.896 | -0.07 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | MANNING3 | 0.9454 | 0.896 | -0.0494 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | MCDONLD3 | 0.966 | 0.896 | -0.07 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | KANARAD3 | 0.9504 | 0.8964 | -0.054 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | GANO 3 | 0.9481 | 0.8964 | -0.0517 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | TRIBUNE3 | 0.9695 | 0.8964 | -0.0731 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | KANARAD3 | 0.9504 | 0.8964 | -0.054 |  | 0.9 | 1.05 | 0.03922 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | GANO 3 | 0.9481 | 0.8964 | -0.0517 |  | 0.9 | 1.05 | 0.03922 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | TRIBUNE3 | 0.9695 | 0.8964 | -0.0731 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | KANARAD3 | 0.9504 | 0.8964 | -0.054 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | GANO 3 | 0.9481 | 0.8964 | -0.0517 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | TRIBUNE3 | 0.9695 | 0.8964 | -0.0731 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | SELKIRK3 | 0.9521 | 0.8967 | -0.0554 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | SELKIRK3 | 0.9521 | 0.8967 | -0.0554 |  | 0.9 | 1.05 | 0.03922 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | SELKIRK3 | 0.9521 | 0.8967 | -0.0554 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | TRIB SW3 | 0.9638 | 0.897 | -0.0668 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | TRIB SW3 | 0.9708 | 0.897 | -0.0738 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | ARNOLD3 | 0.9671 | 0.897 | -0.0701 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | TRIB SW3 | 0.9638 | 0.897 | -0.0668 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | TRIB SW3 | 0.9708 | 0.897 | -0.0738 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | ARNOLD3 | 0.9671 | 0.897 | -0.0701 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | TRIB SW3 | 0.9638 | 0.897 | -0.0668 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | TRIB SW3 | 0.9708 | 0.897 | -0.0738 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | ARNOLD3 | 0.9671 | 0.897 | -0.0701 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | MANNGT 3 | 0.9464 | 0.8972 | -0.0492 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | TRIB SW3 | 0.9638 | 0.8972 | -0.0666 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | MANNGT 3 | 0.9464 | 0.8972 | -0.0492 |  | 0.9 | 1.05 | 0.03922 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | TRIB SW3 | 0.9638 | 0.8972 | -0.0666 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | MANNGT 3 | 0.9464 | 0.8972 | -0.0492 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | TRIB SW3 | 0.9638 | 0.8972 | -0.0666 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | NSI | 0.953 | 0.8974 | -0.0556 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | SETAB 3 | 0.9556 | 0.8974 | -0.0582 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | NSI | 0.953 | 0.8974 | -0.0556 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | SETAB 3 | 0.9556 | 0.8974 | -0.0582 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | NSI | 0.953 | 0.8974 | -0.0556 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | SETAB 3 | 0.9556 | 0.8974 | -0.0582 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | ELLIS 2 | 0.9474 | 0.8975 | -0.0499 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | ELLIS 2 | 0.9474 | 0.8975 | -0.0499 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | ELLIS 2 | 0.9474 | 0.8975 | -0.0499 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | ONEOK 3 | 0.966 | 0.8977 | -0.0683 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | ONEOK 3 | 0.966 | 0.8977 | -0.0683 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | ONEOK 3 | 0.966 | 0.8977 | -0.0683 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | TRIBUNE3 | 0.9519 | 0.8979 | -0.054 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | TRIBUNE3 | 0.9519 | 0.8979 | -0.054 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | TRIBUNE3 | 0.9519 | 0.8979 | -0.054 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | TRIB SW3 | 0.9519 | 0.8981 | -0.0538 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | TRIB SW3 | 0.9519 | 0.8981 | -0.0538 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | TRIB SW3 | 0.9519 | 0.8981 | -0.0538 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | NSI TAP3 | 0.9538 | 0.8983 | -0.0555 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | NSI TAP3 | 0.9538 | 0.8983 | -0.0555 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | NSI TAP3 | 0.9538 | 0.8983 | -0.0555 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | BREWSTR3 | 0.978 | 0.8984 | -0.0796 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | BREWSTR3 | 0.978 | 0.8984 | -0.0796 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | BREWSTR3 | 0.978 | 0.8984 | -0.0796 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | ONEOK 3 | 0.9787 | 0.8985 | -0.0802 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | ONEOK 3 | 0.9787 | 0.8985 | -0.0802 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | ONEOK 3 | 0.9787 | 0.8985 | -0.0802 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | TRIBUNE3 | 0.9641 | 0.8986 | -0.0655 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | TRIBUNE3 | 0.9711 | 0.8986 | -0.0725 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | TRIBUNE3 | 0.9641 | 0.8986 | -0.0655 |  | 0.9 | 1.05 | 0.03887 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | TRIBUNE3 | 0.9711 | 0.8986 | -0.0725 |  | 0.9 | 1.05 | 0.03887 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | TRIBUNE3 | 0.9641 | 0.8986 | -0.0655 |  | 0.9 | 1.05 | 0.03269 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | TRIBUNE3 | 0.9711 | 0.8986 | -0.0725 |  | 0.9 | 1.05 | 0.03269 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | LEOTI 3 | 0.9526 | 0.8987 | -0.0539 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | TRIBUNE3 | 0.9641 | 0.8987 | -0.0654 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | BVERVLLY | 0.9669 | 0.8987 | -0.0682 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | LEOTI 3 | 0.9526 | 0.8987 | -0.0539 |  | 0.9 | 1.05 | 0.03922 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | TRIBUNE3 | 0.9641 | 0.8987 | -0.0654 |  | 0.9 | 1.05 | 0.03887 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | BVERVLLY | 0.9669 | 0.8987 | -0.0682 |  | 0.9 | 1.05 | 0.0396 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | LEOTI 3 | 0.9526 | 0.8987 | -0.0539 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | TRIBUNE3 | 0.9641 | 0.8987 | -0.0654 |  | 0.9 | 1.05 | 0.03269 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | BVERVLLY | 0.9669 | 0.8987 | -0.0682 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531449_3 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | DIGHTON3 | 0.9424 | 0.8988 | -0.0436 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | DIGHTON3 | 0.9424 | 0.8988 | -0.0436 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | DIGHTON3 | 0.9424 | 0.8988 | -0.0436 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | KANARAD3 | 0.9679 | 0.8989 | -0.069 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | KANARAD3 | 0.9679 | 0.8989 | -0.069 |  | 0.9 | 1.05 | 0.03912 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | KANARAD3 | 0.9679 | 0.8989 | -0.069 |  | 0.9 | 1.05 | 0.033 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | CHASE 3 | 0.9469 | 0.8991 | -0.0478 |  | 0.9 | 1.05 | 0.03323 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | CHASE 3 | 0.9469 | 0.8991 | -0.0478 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | SHARNSP3 | 0.947 | 0.8991 | -0.0479 |  | 0.9 | 1.05 | 0.03323 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | SHARNSP3 | 0.947 | 0.8991 | -0.0479 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | PILE 3 | 0.9585 | 0.8991 | -0.0594 |  | 0.9 | 1.05 | 0.033 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | CHASE 3 | 0.9469 | 0.8991 | -0.0478 |  | 0.9 | 1.05 | 0.07901 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | CHASE 3 | 0.9469 | 0.8991 | -0.0478 |  | 0.9 | 1.05 | 0.07901 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | SHARNSP3 | 0.947 | 0.8991 | -0.0479 |  | 0.9 | 1.05 | 0.07901 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | SHARNSP3 | 0.947 | 0.8991 | -0.0479 |  | 0.9 | 1.05 | 0.07901 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | PILE 3 | 0.9585 | 0.8991 | -0.0594 |  | 0.9 | 1.05 | 0.03912 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-150 | CHASE 3 | 0.9469 | 0.8991 | -0.0478 |  | 0.9 | 1.05 | 0.03531 | P23:345:SUNC:HLC_BRK282:::EHV: | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-150 | CHASE 3 | 0.9469 | 0.8991 | -0.0478 |  | 0.9 | 1.05 | 0.03531 | Potential P4 Event - POI 531449_0 | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-150 | SHARNSP3 | 0.947 | 0.8991 | -0.0479 |  | 0.9 | 1.05 | 0.03531 | P23:345:SUNC:HLC_BRK282:::EHV: | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-150 | SHARNSP3 | 0.947 | 0.8991 | -0.0479 |  | 0.9 | 1.05 | 0.03531 | Potential P4 Event - POI 531449_0 | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-161 | CHASE 3 | 0.9469 | 0.8991 | -0.0478 |  | 0.9 | 1.05 | 0.03273 | P23:345:SUNC:HLC_BRK282:::EHV: | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-161 | CHASE 3 | 0.9469 | 0.8991 | -0.0478 |  | 0.9 | 1.05 | 0.03273 | Potential P4 Event - POI 531449_0 | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-161 | SHARNSP3 | 0.947 | 0.8991 | -0.0479 |  | 0.9 | 1.05 | 0.03273 | P23:345:SUNC:HLC_BRK282:::EHV: | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-161 | SHARNSP3 | 0.947 | 0.8991 | -0.0479 |  | 0.9 | 1.05 | 0.03273 | Potential P4 Event - POI 531449_0 | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-164 | CHASE 3 | 0.9469 | 0.8991 | -0.0478 |  | 0.9 | 1.05 | 0.03724 | P23:345:SUNC:HLC_BRK282:::EHV: | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-164 | CHASE 3 | 0.9469 | 0.8991 | -0.0478 |  | 0.9 | 1.05 | 0.03724 | Potential P4 Event - POI 531449_0 | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-164 | SHARNSP3 | 0.947 | 0.8991 | -0.0479 |  | 0.9 | 1.05 | 0.03724 | P23:345:SUNC:HLC_BRK282:::EHV: | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-164 | SHARNSP3 | 0.947 | 0.8991 | -0.0479 |  | 0.9 | 1.05 | 0.03724 | Potential P4 Event - POI 531449_0 | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-165 | CHASE 3 | 0.9469 | 0.8991 | -0.0478 |  | 0.9 | 1.05 | 0.03724 | P23:345:SUNC:HLC_BRK282:::EHV: | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-165 | CHASE 3 | 0.9469 | 0.8991 | -0.0478 |  | 0.9 | 1.05 | 0.03724 | Potential P4 Event - POI 531449_0 | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-165 | SHARNSP3 | 0.947 | 0.8991 | -0.0479 |  | 0.9 | 1.05 | 0.03724 | P23:345:SUNC:HLC_BRK282:::EHV: | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-165 | SHARNSP3 | 0.947 | 0.8991 | -0.0479 |  | 0.9 | 1.05 | 0.03724 | Potential P4 Event - POI 531449_0 | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-229 | CHASE 3 | 0.9469 | 0.8991 | -0.0478 |  | 0.9 | 1.05 | 0.03514 | P23:345:SUNC:HLC_BRK282:::EHV: | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-229 | CHASE 3 | 0.9469 | 0.8991 | -0.0478 |  | 0.9 | 1.05 | 0.03514 | Potential P4 Event - POI 531449_0 | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-229 | SHARNSP3 | 0.947 | 0.8991 | -0.0479 |  | 0.9 | 1.05 | 0.03514 | P23:345:SUNC:HLC_BRK282:::EHV: | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-229 | SHARNSP3 | 0.947 | 0.8991 | -0.0479 |  | 0.9 | 1.05 | 0.03514 | Potential P4 Event - POI 531449_0 | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | CHASE 3 | 0.9469 | 0.8991 | -0.0478 |  | 0.9 | 1.05 | 0.03323 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | CHASE 3 | 0.9469 | 0.8991 | -0.0478 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | SHARNSP3 | 0.947 | 0.8991 | -0.0479 |  | 0.9 | 1.05 | 0.03323 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | SHARNSP3 | 0.947 | 0.8991 | -0.0479 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | PILE 3 | 0.9585 | 0.8991 | -0.0594 |  | 0.9 | 1.05 | 0.033 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | PALMER3 | 0.9637 | 0.8992 | -0.0645 |  | 0.9 | 1.05 | 0.033 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | PALMER3 | 0.9637 | 0.8992 | -0.0645 |  | 0.9 | 1.05 | 0.03912 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | PALMER3 | 0.9637 | 0.8992 | -0.0645 |  | 0.9 | 1.05 | 0.033 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | JAGGER 3 | 0.9431 | 0.8995 | -0.0436 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | LIBERTYT | 0.9419 | 0.8995 | -0.0424 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-100 | BVERVLLY | 0.9796 | 0.8995 | -0.0801 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | JAGGER 3 | 0.9431 | 0.8995 | -0.0436 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | LIBERTYT | 0.9419 | 0.8995 | -0.0424 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-101 | BVERVLLY | 0.9796 | 0.8995 | -0.0801 |  | 0.9 | 1.05 | 0.03839 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | JAGGER 3 | 0.9431 | 0.8995 | -0.0436 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | LIBERTYT | 0.9419 | 0.8995 | -0.0424 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 27SP | GEN-2023-102 | BVERVLLY | 0.9796 | 0.8995 | -0.0801 |  | 0.9 | 1.05 | 0.03208 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | BEELER 3 | 0.9452 | 0.8999 | -0.0453 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-100 | GANO 3 | 0.9481 | 0.8999 | -0.0482 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | BEELER 3 | 0.9452 | 0.8999 | -0.0453 |  | 0.9 | 1.05 | 0.03922 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-101 | GANO 3 | 0.9481 | 0.8999 | -0.0482 |  | 0.9 | 1.05 | 0.03922 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | BEELER 3 | 0.9452 | 0.8999 | -0.0453 |  | 0.9 | 1.05 | 0.03323 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 04ALL | 2 | 24SP | GEN-2023-102 | GANO 3 | 0.9481 | 0.8999 | -0.0482 |  | 0.9 | 1.05 | 0.03323 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | WTCLF 3 | 0.9586 | 0.8142 | -0.1444 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | WTCLF 3 | 0.9655 | 0.8142 | -0.1513 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | WTCLF 3 | 0.9586 | 0.8142 | -0.1444 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | WTCLF 3 | 0.9655 | 0.8142 | -0.1513 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | WTCLF 3 | 0.9586 | 0.8142 | -0.1444 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | WTCLF 3 | 0.9655 | 0.8142 | -0.1513 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | WTCLF 3 | 0.9586 | 0.8142 | -0.1444 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | WTCLF 3 | 0.9655 | 0.8142 | -0.1513 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | WTCLF 3 | 0.9586 | 0.8142 | -0.1444 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | WTCLF 3 | 0.9655 | 0.8142 | -0.1513 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | WTCLF 3 | 0.9586 | 0.8142 | -0.1444 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | WTCLF 3 | 0.9655 | 0.8142 | -0.1513 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | WTCLF 3 | 0.9586 | 0.8142 | -0.1444 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | WTCLF 3 | 0.9655 | 0.8142 | -0.1513 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | WTCLF 3 | 0.9586 | 0.8142 | -0.1444 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | WTCLF 3 | 0.9655 | 0.8142 | -0.1513 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | WTCLF 3 | 0.9586 | 0.8142 | -0.1444 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | WTCLF 3 | 0.9655 | 0.8142 | -0.1513 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | WTCLF 3 | 0.9586 | 0.8142 | -0.1444 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | WTCLF 3 | 0.9655 | 0.8142 | -0.1513 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | WTCLF 3 | 0.9586 | 0.8142 | -0.1444 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | WTCLF 3 | 0.9655 | 0.8142 | -0.1513 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | WTCLF 3 | 0.9586 | 0.8142 | -0.1444 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | WTCLF 3 | 0.9655 | 0.8142 | -0.1513 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | WTCLF 3 | 0.9586 | 0.8142 | -0.1444 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | WTCLF 3 | 0.9655 | 0.8142 | -0.1513 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | WTCLF 3 | 0.9586 | 0.8142 | -0.1444 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | WTCLF 3 | 0.9655 | 0.8142 | -0.1513 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | WTCLF 3 | 0.9586 | 0.8142 | -0.1444 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | WTCLF 3 | 0.9655 | 0.8142 | -0.1513 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | WTCLF 3 | 0.9586 | 0.8142 | -0.1444 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | WTCLF 3 | 0.9655 | 0.8142 | -0.1513 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | WTCLF 3 | 0.9586 | 0.8142 | -0.1444 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | WTCLF 3 | 0.9655 | 0.8142 | -0.1513 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | WTCLF 3 | 0.9586 | 0.8142 | -0.1444 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | WTCLF 3 | 0.9655 | 0.8142 | -0.1513 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | WTCLF 3 | 0.9586 | 0.8142 | -0.1444 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | WTCLF 3 | 0.9655 | 0.8142 | -0.1513 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | WTCLF 3 | 0.9586 | 0.8142 | -0.1444 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | WTCLF 3 | 0.9655 | 0.8142 | -0.1513 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | WTCLF 3 | 0.9586 | 0.8142 | -0.1444 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | WTCLF 3 | 0.9655 | 0.8142 | -0.1513 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | WTCLF 3 | 0.9586 | 0.8142 | -0.1444 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | WTCLF 3 | 0.9655 | 0.8142 | -0.1513 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | WTCLF 3 | 0.9586 | 0.8142 | -0.1444 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | WTCLF 3 | 0.9655 | 0.8142 | -0.1513 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | WTCLF 3 | 0.9586 | 0.8142 | -0.1444 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | WTCLF 3 | 0.9655 | 0.8142 | -0.1513 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | WTCLF 3 | 0.9586 | 0.8142 | -0.1444 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | WTCLF 3 | 0.9655 | 0.8142 | -0.1513 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | WTCLF 3 | 0.9586 | 0.8142 | -0.1444 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | WTCLF 3 | 0.9655 | 0.8142 | -0.1513 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | WTCLF 3 | 0.9586 | 0.8142 | -0.1444 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | WTCLF 3 | 0.9655 | 0.8142 | -0.1513 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | WTCLFTP3 | 0.9596 | 0.8154 | -0.1442 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | WTCLFTP3 | 0.9665 | 0.8154 | -0.1511 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | WTCLFTP3 | 0.9596 | 0.8154 | -0.1442 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | WTCLFTP3 | 0.9665 | 0.8154 | -0.1511 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | WTCLFTP3 | 0.9596 | 0.8154 | -0.1442 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | WTCLFTP3 | 0.9665 | 0.8154 | -0.1511 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | WTCLFTP3 | 0.9596 | 0.8154 | -0.1442 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | WTCLFTP3 | 0.9665 | 0.8154 | -0.1511 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | WTCLFTP3 | 0.9596 | 0.8154 | -0.1442 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | WTCLFTP3 | 0.9665 | 0.8154 | -0.1511 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | WTCLFTP3 | 0.9596 | 0.8154 | -0.1442 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | WTCLFTP3 | 0.9665 | 0.8154 | -0.1511 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | WTCLFTP3 | 0.9596 | 0.8154 | -0.1442 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | WTCLFTP3 | 0.9665 | 0.8154 | -0.1511 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | WTCLFTP3 | 0.9596 | 0.8154 | -0.1442 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | WTCLFTP3 | 0.9665 | 0.8154 | -0.1511 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | WTCLFTP3 | 0.9596 | 0.8154 | -0.1442 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | WTCLFTP3 | 0.9665 | 0.8154 | -0.1511 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | WTCLFTP3 | 0.9596 | 0.8154 | -0.1442 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | WTCLFTP3 | 0.9665 | 0.8154 | -0.1511 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | WTCLFTP3 | 0.9596 | 0.8154 | -0.1442 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | WTCLFTP3 | 0.9665 | 0.8154 | -0.1511 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | WTCLFTP3 | 0.9596 | 0.8154 | -0.1442 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | WTCLFTP3 | 0.9665 | 0.8154 | -0.1511 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | WTCLFTP3 | 0.9596 | 0.8154 | -0.1442 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | WTCLFTP3 | 0.9665 | 0.8154 | -0.1511 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | WTCLFTP3 | 0.9596 | 0.8154 | -0.1442 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | WTCLFTP3 | 0.9665 | 0.8154 | -0.1511 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | WTCLFTP3 | 0.9596 | 0.8154 | -0.1442 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | WTCLFTP3 | 0.9665 | 0.8154 | -0.1511 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | WTCLFTP3 | 0.9596 | 0.8154 | -0.1442 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | WTCLFTP3 | 0.9665 | 0.8154 | -0.1511 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | WTCLFTP3 | 0.9596 | 0.8154 | -0.1442 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | WTCLFTP3 | 0.9665 | 0.8154 | -0.1511 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | WTCLFTP3 | 0.9596 | 0.8154 | -0.1442 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | WTCLFTP3 | 0.9665 | 0.8154 | -0.1511 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | WTCLFTP3 | 0.9596 | 0.8154 | -0.1442 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | WTCLFTP3 | 0.9665 | 0.8154 | -0.1511 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | WTCLFTP3 | 0.9596 | 0.8154 | -0.1442 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | WTCLFTP3 | 0.9665 | 0.8154 | -0.1511 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | WTCLFTP3 | 0.9596 | 0.8154 | -0.1442 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | WTCLFTP3 | 0.9665 | 0.8154 | -0.1511 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | WTCLFTP3 | 0.9596 | 0.8154 | -0.1442 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | WTCLFTP3 | 0.9665 | 0.8154 | -0.1511 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | WTCLFTP3 | 0.9596 | 0.8154 | -0.1442 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | WTCLFTP3 | 0.9665 | 0.8154 | -0.1511 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | WTCLFTP3 | 0.9596 | 0.8154 | -0.1442 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | WTCLFTP3 | 0.9665 | 0.8154 | -0.1511 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | WTCLFTP3 | 0.9596 | 0.8154 | -0.1442 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | WTCLFTP3 | 0.9665 | 0.8154 | -0.1511 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | WTCLFTP3 | 0.9596 | 0.8154 | -0.1442 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | WTCLFTP3 | 0.9665 | 0.8154 | -0.1511 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | WTCLFTP3 | 0.9596 | 0.8154 | -0.1442 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | WTCLFTP3 | 0.9665 | 0.8154 | -0.1511 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | WTCLF 3 | 0.9586 | 0.8204 | -0.1382 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | WTCLF 3 | 0.9586 | 0.8204 | -0.1382 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | WTCLF 3 | 0.9586 | 0.8204 | -0.1382 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | WTCLF 3 | 0.9586 | 0.8204 | -0.1382 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | WTCLF 3 | 0.9586 | 0.8204 | -0.1382 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | WTCLF 3 | 0.9586 | 0.8204 | -0.1382 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | WTCLF 3 | 0.9586 | 0.8204 | -0.1382 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | WTCLF 3 | 0.9586 | 0.8204 | -0.1382 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | WTCLF 3 | 0.9586 | 0.8204 | -0.1382 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | WTCLF 3 | 0.9586 | 0.8204 | -0.1382 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | WTCLF 3 | 0.9586 | 0.8204 | -0.1382 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | WTCLF 3 | 0.9586 | 0.8204 | -0.1382 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | WTCLF 3 | 0.9586 | 0.8204 | -0.1382 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | WTCLF 3 | 0.9586 | 0.8204 | -0.1382 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | WTCLF 3 | 0.9586 | 0.8204 | -0.1382 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | WTCLF 3 | 0.9586 | 0.8204 | -0.1382 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | WTCLF 3 | 0.9586 | 0.8204 | -0.1382 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | WTCLF 3 | 0.9586 | 0.8204 | -0.1382 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | WTCLF 3 | 0.9586 | 0.8204 | -0.1382 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | WTCLF 3 | 0.9586 | 0.8204 | -0.1382 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | WTCLF 3 | 0.9586 | 0.8204 | -0.1382 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | WTCLF 3 | 0.9586 | 0.8204 | -0.1382 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | WTCLF 3 | 0.9586 | 0.8204 | -0.1382 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | WTCLF 3 | 0.9586 | 0.8204 | -0.1382 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | WTCLF 3 | 0.9586 | 0.8204 | -0.1382 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | WTCLF 3 | 0.9586 | 0.8204 | -0.1382 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | WTCLF 3 | 0.9586 | 0.8204 | -0.1382 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | WTCLFTP3 | 0.9596 | 0.8216 | -0.138 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | WTCLFTP3 | 0.9596 | 0.8216 | -0.138 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | WTCLFTP3 | 0.9596 | 0.8216 | -0.138 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | WTCLFTP3 | 0.9596 | 0.8216 | -0.138 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | WTCLFTP3 | 0.9596 | 0.8216 | -0.138 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | WTCLFTP3 | 0.9596 | 0.8216 | -0.138 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | WTCLFTP3 | 0.9596 | 0.8216 | -0.138 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | WTCLFTP3 | 0.9596 | 0.8216 | -0.138 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | WTCLFTP3 | 0.9596 | 0.8216 | -0.138 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | WTCLFTP3 | 0.9596 | 0.8216 | -0.138 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | WTCLFTP3 | 0.9596 | 0.8216 | -0.138 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | WTCLFTP3 | 0.9596 | 0.8216 | -0.138 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | WTCLFTP3 | 0.9596 | 0.8216 | -0.138 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | WTCLFTP3 | 0.9596 | 0.8216 | -0.138 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | WTCLFTP3 | 0.9596 | 0.8216 | -0.138 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | WTCLFTP3 | 0.9596 | 0.8216 | -0.138 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | WTCLFTP3 | 0.9596 | 0.8216 | -0.138 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | WTCLFTP3 | 0.9596 | 0.8216 | -0.138 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | WTCLFTP3 | 0.9596 | 0.8216 | -0.138 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | WTCLFTP3 | 0.9596 | 0.8216 | -0.138 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | WTCLFTP3 | 0.9596 | 0.8216 | -0.138 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | WTCLFTP3 | 0.9596 | 0.8216 | -0.138 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | WTCLFTP3 | 0.9596 | 0.8216 | -0.138 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | WTCLFTP3 | 0.9596 | 0.8216 | -0.138 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | WTCLFTP3 | 0.9596 | 0.8216 | -0.138 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | WTCLFTP3 | 0.9596 | 0.8216 | -0.138 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | WTCLFTP3 | 0.9596 | 0.8216 | -0.138 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | WTCLF 3 | 0.9714 | 0.8251 | -0.1463 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | WTCLF 3 | 0.9773 | 0.8251 | -0.1522 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | WTCLF 3 | 0.9714 | 0.8251 | -0.1463 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | WTCLF 3 | 0.9773 | 0.8251 | -0.1522 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | WTCLF 3 | 0.9714 | 0.8251 | -0.1463 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | WTCLF 3 | 0.9773 | 0.8251 | -0.1522 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | WTCLF 3 | 0.9714 | 0.8251 | -0.1463 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | WTCLF 3 | 0.9773 | 0.8251 | -0.1522 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | WTCLF 3 | 0.9714 | 0.8251 | -0.1463 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | WTCLF 3 | 0.9773 | 0.8251 | -0.1522 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | WTCLF 3 | 0.9714 | 0.8251 | -0.1463 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | WTCLF 3 | 0.9773 | 0.8251 | -0.1522 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | WTCLF 3 | 0.9714 | 0.8251 | -0.1463 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | WTCLF 3 | 0.9773 | 0.8251 | -0.1522 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | WTCLF 3 | 0.9714 | 0.8251 | -0.1463 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | WTCLF 3 | 0.9773 | 0.8251 | -0.1522 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | WTCLF 3 | 0.9714 | 0.8251 | -0.1463 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | WTCLF 3 | 0.9773 | 0.8251 | -0.1522 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | WTCLF 3 | 0.9714 | 0.8251 | -0.1463 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | WTCLF 3 | 0.9773 | 0.8251 | -0.1522 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | WTCLF 3 | 0.9714 | 0.8251 | -0.1463 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | WTCLF 3 | 0.9773 | 0.8251 | -0.1522 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | WTCLF 3 | 0.9714 | 0.8251 | -0.1463 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | WTCLF 3 | 0.9773 | 0.8251 | -0.1522 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | WTCLF 3 | 0.9714 | 0.8251 | -0.1463 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | WTCLF 3 | 0.9773 | 0.8251 | -0.1522 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | WTCLF 3 | 0.9714 | 0.8251 | -0.1463 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | WTCLF 3 | 0.9773 | 0.8251 | -0.1522 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | WTCLF 3 | 0.9714 | 0.8251 | -0.1463 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | WTCLF 3 | 0.9773 | 0.8251 | -0.1522 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | WTCLF 3 | 0.9714 | 0.8251 | -0.1463 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | WTCLF 3 | 0.9773 | 0.8251 | -0.1522 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | WTCLF 3 | 0.9714 | 0.8251 | -0.1463 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | WTCLF 3 | 0.9773 | 0.8251 | -0.1522 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | WTCLF 3 | 0.9714 | 0.8251 | -0.1463 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | WTCLF 3 | 0.9773 | 0.8251 | -0.1522 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | WTCLF 3 | 0.9714 | 0.8251 | -0.1463 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | WTCLF 3 | 0.9773 | 0.8251 | -0.1522 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | WTCLF 3 | 0.9714 | 0.8251 | -0.1463 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | WTCLF 3 | 0.9773 | 0.8251 | -0.1522 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | WTCLF 3 | 0.9714 | 0.8251 | -0.1463 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | WTCLF 3 | 0.9773 | 0.8251 | -0.1522 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | WTCLF 3 | 0.9714 | 0.8251 | -0.1463 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | WTCLF 3 | 0.9773 | 0.8251 | -0.1522 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | WTCLF 3 | 0.9714 | 0.8251 | -0.1463 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | WTCLF 3 | 0.9773 | 0.8251 | -0.1522 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | WTCLF 3 | 0.9714 | 0.8251 | -0.1463 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | WTCLF 3 | 0.9773 | 0.8251 | -0.1522 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | WTCLF 3 | 0.9714 | 0.8251 | -0.1463 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | WTCLF 3 | 0.9773 | 0.8251 | -0.1522 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | WTCLF 3 | 0.9714 | 0.8251 | -0.1463 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | WTCLF 3 | 0.9773 | 0.8251 | -0.1522 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | WTCLF 3 | 0.9714 | 0.8251 | -0.1463 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | WTCLF 3 | 0.9773 | 0.8251 | -0.1522 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | KANARAD3 | 0.965 | 0.8253 | -0.1397 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | KANARAD3 | 0.9709 | 0.8253 | -0.1456 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | KANARAD3 | 0.965 | 0.8253 | -0.1397 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | KANARAD3 | 0.9709 | 0.8253 | -0.1456 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | KANARAD3 | 0.965 | 0.8253 | -0.1397 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | KANARAD3 | 0.9709 | 0.8253 | -0.1456 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | KANARAD3 | 0.965 | 0.8253 | -0.1397 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | KANARAD3 | 0.9709 | 0.8253 | -0.1456 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | KANARAD3 | 0.965 | 0.8253 | -0.1397 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | KANARAD3 | 0.9709 | 0.8253 | -0.1456 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | KANARAD3 | 0.965 | 0.8253 | -0.1397 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | KANARAD3 | 0.9709 | 0.8253 | -0.1456 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | KANARAD3 | 0.965 | 0.8253 | -0.1397 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | KANARAD3 | 0.9709 | 0.8253 | -0.1456 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | KANARAD3 | 0.965 | 0.8253 | -0.1397 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | KANARAD3 | 0.9709 | 0.8253 | -0.1456 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | KANARAD3 | 0.965 | 0.8253 | -0.1397 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | KANARAD3 | 0.9709 | 0.8253 | -0.1456 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | KANARAD3 | 0.965 | 0.8253 | -0.1397 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | KANARAD3 | 0.9709 | 0.8253 | -0.1456 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | KANARAD3 | 0.965 | 0.8253 | -0.1397 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | KANARAD3 | 0.9709 | 0.8253 | -0.1456 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | KANARAD3 | 0.965 | 0.8253 | -0.1397 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | KANARAD3 | 0.9709 | 0.8253 | -0.1456 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | KANARAD3 | 0.965 | 0.8253 | -0.1397 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | KANARAD3 | 0.9709 | 0.8253 | -0.1456 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | KANARAD3 | 0.965 | 0.8253 | -0.1397 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | KANARAD3 | 0.9709 | 0.8253 | -0.1456 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | KANARAD3 | 0.965 | 0.8253 | -0.1397 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | KANARAD3 | 0.9709 | 0.8253 | -0.1456 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | KANARAD3 | 0.965 | 0.8253 | -0.1397 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | KANARAD3 | 0.9709 | 0.8253 | -0.1456 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | KANARAD3 | 0.965 | 0.8253 | -0.1397 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | KANARAD3 | 0.9709 | 0.8253 | -0.1456 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | KANARAD3 | 0.965 | 0.8253 | -0.1397 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | KANARAD3 | 0.9709 | 0.8253 | -0.1456 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | KANARAD3 | 0.965 | 0.8253 | -0.1397 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | KANARAD3 | 0.9709 | 0.8253 | -0.1456 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | KANARAD3 | 0.965 | 0.8253 | -0.1397 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | KANARAD3 | 0.9709 | 0.8253 | -0.1456 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | KANARAD3 | 0.965 | 0.8253 | -0.1397 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | KANARAD3 | 0.9709 | 0.8253 | -0.1456 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | KANARAD3 | 0.965 | 0.8253 | -0.1397 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | KANARAD3 | 0.9709 | 0.8253 | -0.1456 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | KANARAD3 | 0.965 | 0.8253 | -0.1397 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | KANARAD3 | 0.9709 | 0.8253 | -0.1456 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | KANARAD3 | 0.965 | 0.8253 | -0.1397 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | KANARAD3 | 0.9709 | 0.8253 | -0.1456 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | KANARAD3 | 0.965 | 0.8253 | -0.1397 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | KANARAD3 | 0.9709 | 0.8253 | -0.1456 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | KANARAD3 | 0.965 | 0.8253 | -0.1397 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | KANARAD3 | 0.9709 | 0.8253 | -0.1456 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | KANARAD3 | 0.965 | 0.8253 | -0.1397 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | KANARAD3 | 0.9709 | 0.8253 | -0.1456 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | CHASE 3 | 0.9603 | 0.8259 | -0.1344 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | CHASE 3 | 0.968 | 0.8259 | -0.1421 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | CHASE 3 | 0.9603 | 0.8259 | -0.1344 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | CHASE 3 | 0.968 | 0.8259 | -0.1421 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | CHASE 3 | 0.9603 | 0.8259 | -0.1344 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | CHASE 3 | 0.968 | 0.8259 | -0.1421 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | CHASE 3 | 0.9603 | 0.8259 | -0.1344 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | CHASE 3 | 0.968 | 0.8259 | -0.1421 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | CHASE 3 | 0.9603 | 0.8259 | -0.1344 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | CHASE 3 | 0.968 | 0.8259 | -0.1421 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | CHASE 3 | 0.9603 | 0.8259 | -0.1344 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | CHASE 3 | 0.968 | 0.8259 | -0.1421 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | CHASE 3 | 0.9603 | 0.8259 | -0.1344 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | CHASE 3 | 0.968 | 0.8259 | -0.1421 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | CHASE 3 | 0.9603 | 0.8259 | -0.1344 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | CHASE 3 | 0.968 | 0.8259 | -0.1421 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | CHASE 3 | 0.9603 | 0.8259 | -0.1344 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | CHASE 3 | 0.968 | 0.8259 | -0.1421 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | CHASE 3 | 0.9603 | 0.8259 | -0.1344 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | CHASE 3 | 0.968 | 0.8259 | -0.1421 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | CHASE 3 | 0.9603 | 0.8259 | -0.1344 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | CHASE 3 | 0.968 | 0.8259 | -0.1421 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | CHASE 3 | 0.9603 | 0.8259 | -0.1344 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | CHASE 3 | 0.968 | 0.8259 | -0.1421 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | CHASE 3 | 0.9603 | 0.8259 | -0.1344 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | CHASE 3 | 0.968 | 0.8259 | -0.1421 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | CHASE 3 | 0.9603 | 0.8259 | -0.1344 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | CHASE 3 | 0.968 | 0.8259 | -0.1421 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | CHASE 3 | 0.9603 | 0.8259 | -0.1344 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | CHASE 3 | 0.968 | 0.8259 | -0.1421 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | CHASE 3 | 0.9603 | 0.8259 | -0.1344 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | CHASE 3 | 0.968 | 0.8259 | -0.1421 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | CHASE 3 | 0.9603 | 0.8259 | -0.1344 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | CHASE 3 | 0.968 | 0.8259 | -0.1421 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | CHASE 3 | 0.9603 | 0.8259 | -0.1344 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | CHASE 3 | 0.968 | 0.8259 | -0.1421 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | CHASE 3 | 0.9603 | 0.8259 | -0.1344 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | CHASE 3 | 0.968 | 0.8259 | -0.1421 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | CHASE 3 | 0.9603 | 0.8259 | -0.1344 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | CHASE 3 | 0.968 | 0.8259 | -0.1421 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | CHASE 3 | 0.9603 | 0.8259 | -0.1344 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | CHASE 3 | 0.968 | 0.8259 | -0.1421 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | CHASE 3 | 0.9603 | 0.8259 | -0.1344 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | CHASE 3 | 0.968 | 0.8259 | -0.1421 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | CHASE 3 | 0.9603 | 0.8259 | -0.1344 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | CHASE 3 | 0.968 | 0.8259 | -0.1421 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | CHASE 3 | 0.9603 | 0.8259 | -0.1344 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | CHASE 3 | 0.968 | 0.8259 | -0.1421 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | CHASE 3 | 0.9603 | 0.8259 | -0.1344 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | CHASE 3 | 0.968 | 0.8259 | -0.1421 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | CHASE 3 | 0.9603 | 0.8259 | -0.1344 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | CHASE 3 | 0.968 | 0.8259 | -0.1421 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | CHASE 3 | 0.9603 | 0.8259 | -0.1344 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | CHASE 3 | 0.968 | 0.8259 | -0.1421 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | SHARNSP3 | 0.9603 | 0.826 | -0.1343 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | SHARNSP3 | 0.9681 | 0.826 | -0.1421 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | SHARNSP3 | 0.9603 | 0.826 | -0.1343 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | SHARNSP3 | 0.9681 | 0.826 | -0.1421 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | SHARNSP3 | 0.9603 | 0.826 | -0.1343 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | SHARNSP3 | 0.9681 | 0.826 | -0.1421 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | SHARNSP3 | 0.9603 | 0.826 | -0.1343 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | SHARNSP3 | 0.9681 | 0.826 | -0.1421 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | SHARNSP3 | 0.9603 | 0.826 | -0.1343 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | SHARNSP3 | 0.9681 | 0.826 | -0.1421 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | SHARNSP3 | 0.9603 | 0.826 | -0.1343 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | SHARNSP3 | 0.9681 | 0.826 | -0.1421 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | SHARNSP3 | 0.9603 | 0.826 | -0.1343 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | SHARNSP3 | 0.9681 | 0.826 | -0.1421 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | SHARNSP3 | 0.9603 | 0.826 | -0.1343 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | SHARNSP3 | 0.9681 | 0.826 | -0.1421 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | SHARNSP3 | 0.9603 | 0.826 | -0.1343 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | SHARNSP3 | 0.9681 | 0.826 | -0.1421 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | SHARNSP3 | 0.9603 | 0.826 | -0.1343 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | SHARNSP3 | 0.9681 | 0.826 | -0.1421 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | SHARNSP3 | 0.9603 | 0.826 | -0.1343 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | SHARNSP3 | 0.9681 | 0.826 | -0.1421 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | SHARNSP3 | 0.9603 | 0.826 | -0.1343 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | SHARNSP3 | 0.9681 | 0.826 | -0.1421 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | SHARNSP3 | 0.9603 | 0.826 | -0.1343 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | SHARNSP3 | 0.9681 | 0.826 | -0.1421 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | SHARNSP3 | 0.9603 | 0.826 | -0.1343 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | SHARNSP3 | 0.9681 | 0.826 | -0.1421 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | SHARNSP3 | 0.9603 | 0.826 | -0.1343 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | SHARNSP3 | 0.9681 | 0.826 | -0.1421 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | SHARNSP3 | 0.9603 | 0.826 | -0.1343 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | SHARNSP3 | 0.9681 | 0.826 | -0.1421 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | SHARNSP3 | 0.9603 | 0.826 | -0.1343 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | SHARNSP3 | 0.9681 | 0.826 | -0.1421 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | SHARNSP3 | 0.9603 | 0.826 | -0.1343 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | SHARNSP3 | 0.9681 | 0.826 | -0.1421 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | SHARNSP3 | 0.9603 | 0.826 | -0.1343 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | SHARNSP3 | 0.9681 | 0.826 | -0.1421 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | SHARNSP3 | 0.9603 | 0.826 | -0.1343 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | SHARNSP3 | 0.9681 | 0.826 | -0.1421 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | SHARNSP3 | 0.9603 | 0.826 | -0.1343 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | SHARNSP3 | 0.9681 | 0.826 | -0.1421 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | SHARNSP3 | 0.9603 | 0.826 | -0.1343 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | SHARNSP3 | 0.9681 | 0.826 | -0.1421 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | SHARNSP3 | 0.9603 | 0.826 | -0.1343 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | SHARNSP3 | 0.9681 | 0.826 | -0.1421 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | SHARNSP3 | 0.9603 | 0.826 | -0.1343 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | SHARNSP3 | 0.9681 | 0.826 | -0.1421 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | SHARNSP3 | 0.9603 | 0.826 | -0.1343 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | SHARNSP3 | 0.9681 | 0.826 | -0.1421 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | SHARNSP3 | 0.9603 | 0.826 | -0.1343 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | SHARNSP3 | 0.9681 | 0.826 | -0.1421 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | SHARNSP3 | 0.9603 | 0.826 | -0.1343 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | SHARNSP3 | 0.9681 | 0.826 | -0.1421 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | WTCLFTP3 | 0.9723 | 0.8263 | -0.146 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | WTCLFTP3 | 0.9783 | 0.8263 | -0.152 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | WTCLFTP3 | 0.9723 | 0.8263 | -0.146 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | WTCLFTP3 | 0.9783 | 0.8263 | -0.152 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | WTCLFTP3 | 0.9723 | 0.8263 | -0.146 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | WTCLFTP3 | 0.9783 | 0.8263 | -0.152 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | WTCLFTP3 | 0.9723 | 0.8263 | -0.146 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | WTCLFTP3 | 0.9783 | 0.8263 | -0.152 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | WTCLFTP3 | 0.9723 | 0.8263 | -0.146 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | WTCLFTP3 | 0.9783 | 0.8263 | -0.152 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | WTCLFTP3 | 0.9723 | 0.8263 | -0.146 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | WTCLFTP3 | 0.9783 | 0.8263 | -0.152 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | WTCLFTP3 | 0.9723 | 0.8263 | -0.146 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | WTCLFTP3 | 0.9783 | 0.8263 | -0.152 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | WTCLFTP3 | 0.9723 | 0.8263 | -0.146 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | WTCLFTP3 | 0.9783 | 0.8263 | -0.152 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | WTCLFTP3 | 0.9723 | 0.8263 | -0.146 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | WTCLFTP3 | 0.9783 | 0.8263 | -0.152 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | WTCLFTP3 | 0.9723 | 0.8263 | -0.146 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | WTCLFTP3 | 0.9783 | 0.8263 | -0.152 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | WTCLFTP3 | 0.9723 | 0.8263 | -0.146 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | WTCLFTP3 | 0.9783 | 0.8263 | -0.152 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | WTCLFTP3 | 0.9723 | 0.8263 | -0.146 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | WTCLFTP3 | 0.9783 | 0.8263 | -0.152 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | WTCLFTP3 | 0.9723 | 0.8263 | -0.146 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | WTCLFTP3 | 0.9783 | 0.8263 | -0.152 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | WTCLFTP3 | 0.9723 | 0.8263 | -0.146 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | WTCLFTP3 | 0.9783 | 0.8263 | -0.152 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | WTCLFTP3 | 0.9723 | 0.8263 | -0.146 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | WTCLFTP3 | 0.9783 | 0.8263 | -0.152 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | WTCLFTP3 | 0.9723 | 0.8263 | -0.146 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | WTCLFTP3 | 0.9783 | 0.8263 | -0.152 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | WTCLFTP3 | 0.9723 | 0.8263 | -0.146 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | WTCLFTP3 | 0.9783 | 0.8263 | -0.152 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | WTCLFTP3 | 0.9723 | 0.8263 | -0.146 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | WTCLFTP3 | 0.9783 | 0.8263 | -0.152 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | WTCLFTP3 | 0.9723 | 0.8263 | -0.146 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | WTCLFTP3 | 0.9783 | 0.8263 | -0.152 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | WTCLFTP3 | 0.9723 | 0.8263 | -0.146 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | WTCLFTP3 | 0.9783 | 0.8263 | -0.152 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | WTCLFTP3 | 0.9723 | 0.8263 | -0.146 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | WTCLFTP3 | 0.9783 | 0.8263 | -0.152 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | WTCLFTP3 | 0.9723 | 0.8263 | -0.146 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | WTCLFTP3 | 0.9783 | 0.8263 | -0.152 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | WTCLFTP3 | 0.9723 | 0.8263 | -0.146 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | WTCLFTP3 | 0.9783 | 0.8263 | -0.152 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | WTCLFTP3 | 0.9723 | 0.8263 | -0.146 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | WTCLFTP3 | 0.9783 | 0.8263 | -0.152 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | WTCLFTP3 | 0.9723 | 0.8263 | -0.146 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | WTCLFTP3 | 0.9783 | 0.8263 | -0.152 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | WTCLFTP3 | 0.9723 | 0.8263 | -0.146 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | WTCLFTP3 | 0.9783 | 0.8263 | -0.152 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | WTCLFTP3 | 0.9723 | 0.8263 | -0.146 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | WTCLFTP3 | 0.9783 | 0.8263 | -0.152 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | CHASE 3 | 0.9603 | 0.831 | -0.1293 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | CHASE 3 | 0.9603 | 0.831 | -0.1293 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | CHASE 3 | 0.9603 | 0.831 | -0.1293 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | CHASE 3 | 0.9603 | 0.831 | -0.1293 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | CHASE 3 | 0.9603 | 0.831 | -0.1293 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | CHASE 3 | 0.9603 | 0.831 | -0.1293 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | CHASE 3 | 0.9603 | 0.831 | -0.1293 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | CHASE 3 | 0.9603 | 0.831 | -0.1293 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | CHASE 3 | 0.9603 | 0.831 | -0.1293 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | CHASE 3 | 0.9603 | 0.831 | -0.1293 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | CHASE 3 | 0.9603 | 0.831 | -0.1293 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | CHASE 3 | 0.9603 | 0.831 | -0.1293 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | CHASE 3 | 0.9603 | 0.831 | -0.1293 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | CHASE 3 | 0.9603 | 0.831 | -0.1293 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | CHASE 3 | 0.9603 | 0.831 | -0.1293 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | CHASE 3 | 0.9603 | 0.831 | -0.1293 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | CHASE 3 | 0.9603 | 0.831 | -0.1293 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | CHASE 3 | 0.9603 | 0.831 | -0.1293 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | CHASE 3 | 0.9603 | 0.831 | -0.1293 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | CHASE 3 | 0.9603 | 0.831 | -0.1293 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | CHASE 3 | 0.9603 | 0.831 | -0.1293 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | CHASE 3 | 0.9603 | 0.831 | -0.1293 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | CHASE 3 | 0.9603 | 0.831 | -0.1293 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | CHASE 3 | 0.9603 | 0.831 | -0.1293 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | CHASE 3 | 0.9603 | 0.831 | -0.1293 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | CHASE 3 | 0.9603 | 0.831 | -0.1293 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | CHASE 3 | 0.9603 | 0.831 | -0.1293 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | SHARNSP3 | 0.9603 | 0.8311 | -0.1292 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | SHARNSP3 | 0.9603 | 0.8311 | -0.1292 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | SHARNSP3 | 0.9603 | 0.8311 | -0.1292 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | SHARNSP3 | 0.9603 | 0.8311 | -0.1292 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | SHARNSP3 | 0.9603 | 0.8311 | -0.1292 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | SHARNSP3 | 0.9603 | 0.8311 | -0.1292 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | SHARNSP3 | 0.9603 | 0.8311 | -0.1292 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | SHARNSP3 | 0.9603 | 0.8311 | -0.1292 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | SHARNSP3 | 0.9603 | 0.8311 | -0.1292 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | SHARNSP3 | 0.9603 | 0.8311 | -0.1292 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | SHARNSP3 | 0.9603 | 0.8311 | -0.1292 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | SHARNSP3 | 0.9603 | 0.8311 | -0.1292 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | SHARNSP3 | 0.9603 | 0.8311 | -0.1292 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | SHARNSP3 | 0.9603 | 0.8311 | -0.1292 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | SHARNSP3 | 0.9603 | 0.8311 | -0.1292 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | SHARNSP3 | 0.9603 | 0.8311 | -0.1292 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | SHARNSP3 | 0.9603 | 0.8311 | -0.1292 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | SHARNSP3 | 0.9603 | 0.8311 | -0.1292 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | SHARNSP3 | 0.9603 | 0.8311 | -0.1292 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | SHARNSP3 | 0.9603 | 0.8311 | -0.1292 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | SHARNSP3 | 0.9603 | 0.8311 | -0.1292 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | SHARNSP3 | 0.9603 | 0.8311 | -0.1292 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | SHARNSP3 | 0.9603 | 0.8311 | -0.1292 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | SHARNSP3 | 0.9603 | 0.8311 | -0.1292 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | SHARNSP3 | 0.9603 | 0.8311 | -0.1292 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | SHARNSP3 | 0.9603 | 0.8311 | -0.1292 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | SHARNSP3 | 0.9603 | 0.8311 | -0.1292 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | WTCLF 3 | 0.9714 | 0.8314 | -0.14 |  | 0.9 | 1.05 | 0.05095 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | WTCLF 3 | 0.9714 | 0.8314 | -0.14 |  | 0.9 | 1.05 | 0.04905 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | WTCLF 3 | 0.9714 | 0.8314 | -0.14 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | WTCLF 3 | 0.9714 | 0.8314 | -0.14 |  | 0.9 | 1.05 | 0.04262 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | WTCLF 3 | 0.9714 | 0.8314 | -0.14 |  | 0.9 | 1.05 | 0.0627 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | WTCLF 3 | 0.9714 | 0.8314 | -0.14 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | WTCLF 3 | 0.9714 | 0.8314 | -0.14 |  | 0.9 | 1.05 | 0.05043 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | WTCLF 3 | 0.9714 | 0.8314 | -0.14 |  | 0.9 | 1.05 | 0.05292 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | WTCLF 3 | 0.9714 | 0.8314 | -0.14 |  | 0.9 | 1.05 | 0.0444 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | WTCLF 3 | 0.9714 | 0.8314 | -0.14 |  | 0.9 | 1.05 | 0.04788 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | WTCLF 3 | 0.9714 | 0.8314 | -0.14 |  | 0.9 | 1.05 | 0.05824 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | WTCLF 3 | 0.9714 | 0.8314 | -0.14 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | WTCLF 3 | 0.9714 | 0.8314 | -0.14 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | WTCLF 3 | 0.9714 | 0.8314 | -0.14 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | WTCLF 3 | 0.9714 | 0.8314 | -0.14 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | WTCLF 3 | 0.9714 | 0.8314 | -0.14 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | WTCLF 3 | 0.9714 | 0.8314 | -0.14 |  | 0.9 | 1.05 | 0.04773 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | WTCLF 3 | 0.9714 | 0.8314 | -0.14 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | WTCLF 3 | 0.9714 | 0.8314 | -0.14 |  | 0.9 | 1.05 | 0.0348 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | WTCLF 3 | 0.9714 | 0.8314 | -0.14 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | WTCLF 3 | 0.9714 | 0.8314 | -0.14 |  | 0.9 | 1.05 | 0.04996 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | WTCLF 3 | 0.9714 | 0.8314 | -0.14 |  | 0.9 | 1.05 | 0.04835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | WTCLF 3 | 0.9714 | 0.8314 | -0.14 |  | 0.9 | 1.05 | 0.05448 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | WTCLF 3 | 0.9714 | 0.8314 | -0.14 |  | 0.9 | 1.05 | 0.05382 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | WTCLF 3 | 0.9714 | 0.8314 | -0.14 |  | 0.9 | 1.05 | 0.03774 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | WTCLF 3 | 0.9714 | 0.8314 | -0.14 |  | 0.9 | 1.05 | 0.04948 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | WTCLF 3 | 0.9714 | 0.8314 | -0.14 |  | 0.9 | 1.05 | 0.04054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | KANARAD3 | 0.965 | 0.8319 | -0.1331 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | KANARAD3 | 0.965 | 0.8319 | -0.1331 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | KANARAD3 | 0.965 | 0.8319 | -0.1331 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | KANARAD3 | 0.965 | 0.8319 | -0.1331 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | KANARAD3 | 0.965 | 0.8319 | -0.1331 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | KANARAD3 | 0.965 | 0.8319 | -0.1331 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | KANARAD3 | 0.965 | 0.8319 | -0.1331 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | KANARAD3 | 0.965 | 0.8319 | -0.1331 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | KANARAD3 | 0.965 | 0.8319 | -0.1331 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | KANARAD3 | 0.965 | 0.8319 | -0.1331 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | KANARAD3 | 0.965 | 0.8319 | -0.1331 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | KANARAD3 | 0.965 | 0.8319 | -0.1331 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | KANARAD3 | 0.965 | 0.8319 | -0.1331 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | KANARAD3 | 0.965 | 0.8319 | -0.1331 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | KANARAD3 | 0.965 | 0.8319 | -0.1331 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | KANARAD3 | 0.965 | 0.8319 | -0.1331 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | KANARAD3 | 0.965 | 0.8319 | -0.1331 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | KANARAD3 | 0.965 | 0.8319 | -0.1331 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | KANARAD3 | 0.965 | 0.8319 | -0.1331 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | KANARAD3 | 0.965 | 0.8319 | -0.1331 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | KANARAD3 | 0.965 | 0.8319 | -0.1331 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | KANARAD3 | 0.965 | 0.8319 | -0.1331 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | KANARAD3 | 0.965 | 0.8319 | -0.1331 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | KANARAD3 | 0.965 | 0.8319 | -0.1331 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | KANARAD3 | 0.965 | 0.8319 | -0.1331 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | KANARAD3 | 0.965 | 0.8319 | -0.1331 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | KANARAD3 | 0.965 | 0.8319 | -0.1331 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | WTCLFTP3 | 0.9723 | 0.8326 | -0.1397 |  | 0.9 | 1.05 | 0.05095 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | WTCLFTP3 | 0.9723 | 0.8326 | -0.1397 |  | 0.9 | 1.05 | 0.04905 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | WTCLFTP3 | 0.9723 | 0.8326 | -0.1397 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | WTCLFTP3 | 0.9723 | 0.8326 | -0.1397 |  | 0.9 | 1.05 | 0.04262 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | WTCLFTP3 | 0.9723 | 0.8326 | -0.1397 |  | 0.9 | 1.05 | 0.0627 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | WTCLFTP3 | 0.9723 | 0.8326 | -0.1397 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | WTCLFTP3 | 0.9723 | 0.8326 | -0.1397 |  | 0.9 | 1.05 | 0.05043 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | WTCLFTP3 | 0.9723 | 0.8326 | -0.1397 |  | 0.9 | 1.05 | 0.05292 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | WTCLFTP3 | 0.9723 | 0.8326 | -0.1397 |  | 0.9 | 1.05 | 0.0444 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | WTCLFTP3 | 0.9723 | 0.8326 | -0.1397 |  | 0.9 | 1.05 | 0.04788 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | WTCLFTP3 | 0.9723 | 0.8326 | -0.1397 |  | 0.9 | 1.05 | 0.05824 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | WTCLFTP3 | 0.9723 | 0.8326 | -0.1397 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | WTCLFTP3 | 0.9723 | 0.8326 | -0.1397 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | WTCLFTP3 | 0.9723 | 0.8326 | -0.1397 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | WTCLFTP3 | 0.9723 | 0.8326 | -0.1397 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | WTCLFTP3 | 0.9723 | 0.8326 | -0.1397 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | WTCLFTP3 | 0.9723 | 0.8326 | -0.1397 |  | 0.9 | 1.05 | 0.04773 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | WTCLFTP3 | 0.9723 | 0.8326 | -0.1397 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | WTCLFTP3 | 0.9723 | 0.8326 | -0.1397 |  | 0.9 | 1.05 | 0.0348 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | WTCLFTP3 | 0.9723 | 0.8326 | -0.1397 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | WTCLFTP3 | 0.9723 | 0.8326 | -0.1397 |  | 0.9 | 1.05 | 0.04996 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | WTCLFTP3 | 0.9723 | 0.8326 | -0.1397 |  | 0.9 | 1.05 | 0.04835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | WTCLFTP3 | 0.9723 | 0.8326 | -0.1397 |  | 0.9 | 1.05 | 0.05448 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | WTCLFTP3 | 0.9723 | 0.8326 | -0.1397 |  | 0.9 | 1.05 | 0.05382 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | WTCLFTP3 | 0.9723 | 0.8326 | -0.1397 |  | 0.9 | 1.05 | 0.03774 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | WTCLFTP3 | 0.9723 | 0.8326 | -0.1397 |  | 0.9 | 1.05 | 0.04948 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | WTCLFTP3 | 0.9723 | 0.8326 | -0.1397 |  | 0.9 | 1.05 | 0.04054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | NSI | 0.9676 | 0.834 | -0.1336 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | NSI | 0.973 | 0.834 | -0.139 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | NSI | 0.9676 | 0.834 | -0.1336 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | NSI | 0.973 | 0.834 | -0.139 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | NSI | 0.9676 | 0.834 | -0.1336 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | NSI | 0.973 | 0.834 | -0.139 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | NSI | 0.9676 | 0.834 | -0.1336 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | NSI | 0.973 | 0.834 | -0.139 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | NSI | 0.9676 | 0.834 | -0.1336 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | NSI | 0.973 | 0.834 | -0.139 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | NSI | 0.9676 | 0.834 | -0.1336 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | NSI | 0.973 | 0.834 | -0.139 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | NSI | 0.9676 | 0.834 | -0.1336 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | NSI | 0.973 | 0.834 | -0.139 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | NSI | 0.9676 | 0.834 | -0.1336 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | NSI | 0.973 | 0.834 | -0.139 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | NSI | 0.9676 | 0.834 | -0.1336 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | NSI | 0.973 | 0.834 | -0.139 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | NSI | 0.9676 | 0.834 | -0.1336 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | NSI | 0.973 | 0.834 | -0.139 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | NSI | 0.9676 | 0.834 | -0.1336 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | NSI | 0.973 | 0.834 | -0.139 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | NSI | 0.9676 | 0.834 | -0.1336 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | NSI | 0.973 | 0.834 | -0.139 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | NSI | 0.9676 | 0.834 | -0.1336 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | NSI | 0.973 | 0.834 | -0.139 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | NSI | 0.9676 | 0.834 | -0.1336 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | NSI | 0.973 | 0.834 | -0.139 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | NSI | 0.9676 | 0.834 | -0.1336 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | NSI | 0.973 | 0.834 | -0.139 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | NSI | 0.9676 | 0.834 | -0.1336 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | NSI | 0.973 | 0.834 | -0.139 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | NSI | 0.9676 | 0.834 | -0.1336 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | NSI | 0.973 | 0.834 | -0.139 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | NSI | 0.9676 | 0.834 | -0.1336 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | NSI | 0.973 | 0.834 | -0.139 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | NSI | 0.9676 | 0.834 | -0.1336 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | NSI | 0.973 | 0.834 | -0.139 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | NSI | 0.9676 | 0.834 | -0.1336 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | NSI | 0.973 | 0.834 | -0.139 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | NSI | 0.9676 | 0.834 | -0.1336 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | NSI | 0.973 | 0.834 | -0.139 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | NSI | 0.9676 | 0.834 | -0.1336 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | NSI | 0.973 | 0.834 | -0.139 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | NSI | 0.9676 | 0.834 | -0.1336 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | NSI | 0.973 | 0.834 | -0.139 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | NSI | 0.9676 | 0.834 | -0.1336 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | NSI | 0.973 | 0.834 | -0.139 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | NSI | 0.9676 | 0.834 | -0.1336 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | NSI | 0.973 | 0.834 | -0.139 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | NSI | 0.9676 | 0.834 | -0.1336 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | NSI | 0.973 | 0.834 | -0.139 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | NSI | 0.9676 | 0.834 | -0.1336 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | NSI | 0.973 | 0.834 | -0.139 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | CHASE 3 | 0.9698 | 0.8342 | -0.1356 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | CHASE 3 | 0.9765 | 0.8342 | -0.1423 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | CHASE 3 | 0.9698 | 0.8342 | -0.1356 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | CHASE 3 | 0.9765 | 0.8342 | -0.1423 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | CHASE 3 | 0.9698 | 0.8342 | -0.1356 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | CHASE 3 | 0.9765 | 0.8342 | -0.1423 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | CHASE 3 | 0.9698 | 0.8342 | -0.1356 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | CHASE 3 | 0.9765 | 0.8342 | -0.1423 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | CHASE 3 | 0.9698 | 0.8342 | -0.1356 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | CHASE 3 | 0.9765 | 0.8342 | -0.1423 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | CHASE 3 | 0.9698 | 0.8342 | -0.1356 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | CHASE 3 | 0.9765 | 0.8342 | -0.1423 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | CHASE 3 | 0.9698 | 0.8342 | -0.1356 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | CHASE 3 | 0.9765 | 0.8342 | -0.1423 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | CHASE 3 | 0.9698 | 0.8342 | -0.1356 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | CHASE 3 | 0.9765 | 0.8342 | -0.1423 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | CHASE 3 | 0.9698 | 0.8342 | -0.1356 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | CHASE 3 | 0.9765 | 0.8342 | -0.1423 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | CHASE 3 | 0.9698 | 0.8342 | -0.1356 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | CHASE 3 | 0.9765 | 0.8342 | -0.1423 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | CHASE 3 | 0.9698 | 0.8342 | -0.1356 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | CHASE 3 | 0.9765 | 0.8342 | -0.1423 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | CHASE 3 | 0.9698 | 0.8342 | -0.1356 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | CHASE 3 | 0.9765 | 0.8342 | -0.1423 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | CHASE 3 | 0.9698 | 0.8342 | -0.1356 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | CHASE 3 | 0.9765 | 0.8342 | -0.1423 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | CHASE 3 | 0.9698 | 0.8342 | -0.1356 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | CHASE 3 | 0.9765 | 0.8342 | -0.1423 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | CHASE 3 | 0.9698 | 0.8342 | -0.1356 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | CHASE 3 | 0.9765 | 0.8342 | -0.1423 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | CHASE 3 | 0.9698 | 0.8342 | -0.1356 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | CHASE 3 | 0.9765 | 0.8342 | -0.1423 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | CHASE 3 | 0.9698 | 0.8342 | -0.1356 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | CHASE 3 | 0.9765 | 0.8342 | -0.1423 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | CHASE 3 | 0.9698 | 0.8342 | -0.1356 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | CHASE 3 | 0.9765 | 0.8342 | -0.1423 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | CHASE 3 | 0.9698 | 0.8342 | -0.1356 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | CHASE 3 | 0.9765 | 0.8342 | -0.1423 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | CHASE 3 | 0.9698 | 0.8342 | -0.1356 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | CHASE 3 | 0.9765 | 0.8342 | -0.1423 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | CHASE 3 | 0.9698 | 0.8342 | -0.1356 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | CHASE 3 | 0.9765 | 0.8342 | -0.1423 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | CHASE 3 | 0.9698 | 0.8342 | -0.1356 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | CHASE 3 | 0.9765 | 0.8342 | -0.1423 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | CHASE 3 | 0.9698 | 0.8342 | -0.1356 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | CHASE 3 | 0.9765 | 0.8342 | -0.1423 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | CHASE 3 | 0.9698 | 0.8342 | -0.1356 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | CHASE 3 | 0.9765 | 0.8342 | -0.1423 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | CHASE 3 | 0.9698 | 0.8342 | -0.1356 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | CHASE 3 | 0.9765 | 0.8342 | -0.1423 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | CHASE 3 | 0.9698 | 0.8342 | -0.1356 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | CHASE 3 | 0.9765 | 0.8342 | -0.1423 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | CHASE 3 | 0.9698 | 0.8342 | -0.1356 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | CHASE 3 | 0.9765 | 0.8342 | -0.1423 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | SHARNSP3 | 0.9699 | 0.8343 | -0.1356 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | SHARNSP3 | 0.9766 | 0.8343 | -0.1423 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | SHARNSP3 | 0.9699 | 0.8343 | -0.1356 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | SHARNSP3 | 0.9766 | 0.8343 | -0.1423 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | SHARNSP3 | 0.9699 | 0.8343 | -0.1356 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | SHARNSP3 | 0.9766 | 0.8343 | -0.1423 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | SHARNSP3 | 0.9699 | 0.8343 | -0.1356 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | SHARNSP3 | 0.9766 | 0.8343 | -0.1423 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | SHARNSP3 | 0.9699 | 0.8343 | -0.1356 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | SHARNSP3 | 0.9766 | 0.8343 | -0.1423 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | SHARNSP3 | 0.9699 | 0.8343 | -0.1356 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | SHARNSP3 | 0.9766 | 0.8343 | -0.1423 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | SHARNSP3 | 0.9699 | 0.8343 | -0.1356 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | SHARNSP3 | 0.9766 | 0.8343 | -0.1423 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | SHARNSP3 | 0.9699 | 0.8343 | -0.1356 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | SHARNSP3 | 0.9766 | 0.8343 | -0.1423 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | SHARNSP3 | 0.9699 | 0.8343 | -0.1356 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | SHARNSP3 | 0.9766 | 0.8343 | -0.1423 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | SHARNSP3 | 0.9699 | 0.8343 | -0.1356 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | SHARNSP3 | 0.9766 | 0.8343 | -0.1423 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | SHARNSP3 | 0.9699 | 0.8343 | -0.1356 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | SHARNSP3 | 0.9766 | 0.8343 | -0.1423 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | SHARNSP3 | 0.9699 | 0.8343 | -0.1356 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | SHARNSP3 | 0.9766 | 0.8343 | -0.1423 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | SHARNSP3 | 0.9699 | 0.8343 | -0.1356 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | SHARNSP3 | 0.9766 | 0.8343 | -0.1423 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | SHARNSP3 | 0.9699 | 0.8343 | -0.1356 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | SHARNSP3 | 0.9766 | 0.8343 | -0.1423 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | SHARNSP3 | 0.9699 | 0.8343 | -0.1356 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | SHARNSP3 | 0.9766 | 0.8343 | -0.1423 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | SHARNSP3 | 0.9699 | 0.8343 | -0.1356 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | SHARNSP3 | 0.9766 | 0.8343 | -0.1423 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | SHARNSP3 | 0.9699 | 0.8343 | -0.1356 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | SHARNSP3 | 0.9766 | 0.8343 | -0.1423 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | SHARNSP3 | 0.9699 | 0.8343 | -0.1356 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | SHARNSP3 | 0.9766 | 0.8343 | -0.1423 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | SHARNSP3 | 0.9699 | 0.8343 | -0.1356 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | SHARNSP3 | 0.9766 | 0.8343 | -0.1423 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | SHARNSP3 | 0.9699 | 0.8343 | -0.1356 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | SHARNSP3 | 0.9766 | 0.8343 | -0.1423 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | SHARNSP3 | 0.9699 | 0.8343 | -0.1356 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | SHARNSP3 | 0.9766 | 0.8343 | -0.1423 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | SHARNSP3 | 0.9699 | 0.8343 | -0.1356 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | SHARNSP3 | 0.9766 | 0.8343 | -0.1423 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | SHARNSP3 | 0.9699 | 0.8343 | -0.1356 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | SHARNSP3 | 0.9766 | 0.8343 | -0.1423 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | SHARNSP3 | 0.9699 | 0.8343 | -0.1356 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | SHARNSP3 | 0.9766 | 0.8343 | -0.1423 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | SHARNSP3 | 0.9699 | 0.8343 | -0.1356 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | SHARNSP3 | 0.9766 | 0.8343 | -0.1423 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | SHARNSP3 | 0.9699 | 0.8343 | -0.1356 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | SHARNSP3 | 0.9766 | 0.8343 | -0.1423 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | SHARNSP3 | 0.9699 | 0.8343 | -0.1356 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | SHARNSP3 | 0.9766 | 0.8343 | -0.1423 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | NSI TAP3 | 0.9683 | 0.8349 | -0.1334 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | NSI TAP3 | 0.9738 | 0.8349 | -0.1389 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | NSI TAP3 | 0.9683 | 0.8349 | -0.1334 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | NSI TAP3 | 0.9738 | 0.8349 | -0.1389 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | NSI TAP3 | 0.9683 | 0.8349 | -0.1334 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | NSI TAP3 | 0.9738 | 0.8349 | -0.1389 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | NSI TAP3 | 0.9683 | 0.8349 | -0.1334 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | NSI TAP3 | 0.9738 | 0.8349 | -0.1389 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | NSI TAP3 | 0.9683 | 0.8349 | -0.1334 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | NSI TAP3 | 0.9738 | 0.8349 | -0.1389 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | NSI TAP3 | 0.9683 | 0.8349 | -0.1334 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | NSI TAP3 | 0.9738 | 0.8349 | -0.1389 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | NSI TAP3 | 0.9683 | 0.8349 | -0.1334 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | NSI TAP3 | 0.9738 | 0.8349 | -0.1389 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | NSI TAP3 | 0.9683 | 0.8349 | -0.1334 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | NSI TAP3 | 0.9738 | 0.8349 | -0.1389 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | NSI TAP3 | 0.9683 | 0.8349 | -0.1334 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | NSI TAP3 | 0.9738 | 0.8349 | -0.1389 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | NSI TAP3 | 0.9683 | 0.8349 | -0.1334 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | NSI TAP3 | 0.9738 | 0.8349 | -0.1389 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | NSI TAP3 | 0.9683 | 0.8349 | -0.1334 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | NSI TAP3 | 0.9738 | 0.8349 | -0.1389 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | NSI TAP3 | 0.9683 | 0.8349 | -0.1334 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | NSI TAP3 | 0.9738 | 0.8349 | -0.1389 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | NSI TAP3 | 0.9683 | 0.8349 | -0.1334 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | NSI TAP3 | 0.9738 | 0.8349 | -0.1389 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | NSI TAP3 | 0.9683 | 0.8349 | -0.1334 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | NSI TAP3 | 0.9738 | 0.8349 | -0.1389 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | NSI TAP3 | 0.9683 | 0.8349 | -0.1334 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | NSI TAP3 | 0.9738 | 0.8349 | -0.1389 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | NSI TAP3 | 0.9683 | 0.8349 | -0.1334 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | NSI TAP3 | 0.9738 | 0.8349 | -0.1389 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | NSI TAP3 | 0.9683 | 0.8349 | -0.1334 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | NSI TAP3 | 0.9738 | 0.8349 | -0.1389 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | NSI TAP3 | 0.9683 | 0.8349 | -0.1334 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | NSI TAP3 | 0.9738 | 0.8349 | -0.1389 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | NSI TAP3 | 0.9683 | 0.8349 | -0.1334 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | NSI TAP3 | 0.9738 | 0.8349 | -0.1389 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | NSI TAP3 | 0.9683 | 0.8349 | -0.1334 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | NSI TAP3 | 0.9738 | 0.8349 | -0.1389 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | NSI TAP3 | 0.9683 | 0.8349 | -0.1334 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | NSI TAP3 | 0.9738 | 0.8349 | -0.1389 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | NSI TAP3 | 0.9683 | 0.8349 | -0.1334 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | NSI TAP3 | 0.9738 | 0.8349 | -0.1389 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | NSI TAP3 | 0.9683 | 0.8349 | -0.1334 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | NSI TAP3 | 0.9738 | 0.8349 | -0.1389 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | NSI TAP3 | 0.9683 | 0.8349 | -0.1334 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | NSI TAP3 | 0.9738 | 0.8349 | -0.1389 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | NSI TAP3 | 0.9683 | 0.8349 | -0.1334 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | NSI TAP3 | 0.9738 | 0.8349 | -0.1389 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | NSI TAP3 | 0.9683 | 0.8349 | -0.1334 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | NSI TAP3 | 0.9738 | 0.8349 | -0.1389 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | NSI TAP3 | 0.9683 | 0.8349 | -0.1334 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | NSI TAP3 | 0.9738 | 0.8349 | -0.1389 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | KANARAD3 | 0.9808 | 0.8381 | -0.1427 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | KANARAD3 | 0.9859 | 0.8381 | -0.1478 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | KANARAD3 | 0.9808 | 0.8381 | -0.1427 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | KANARAD3 | 0.9859 | 0.8381 | -0.1478 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | KANARAD3 | 0.9808 | 0.8381 | -0.1427 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | KANARAD3 | 0.9859 | 0.8381 | -0.1478 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | KANARAD3 | 0.9808 | 0.8381 | -0.1427 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | KANARAD3 | 0.9859 | 0.8381 | -0.1478 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | KANARAD3 | 0.9808 | 0.8381 | -0.1427 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | KANARAD3 | 0.9859 | 0.8381 | -0.1478 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | KANARAD3 | 0.9808 | 0.8381 | -0.1427 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | KANARAD3 | 0.9859 | 0.8381 | -0.1478 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | KANARAD3 | 0.9808 | 0.8381 | -0.1427 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | KANARAD3 | 0.9859 | 0.8381 | -0.1478 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | KANARAD3 | 0.9808 | 0.8381 | -0.1427 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | KANARAD3 | 0.9859 | 0.8381 | -0.1478 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | KANARAD3 | 0.9808 | 0.8381 | -0.1427 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | KANARAD3 | 0.9859 | 0.8381 | -0.1478 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | KANARAD3 | 0.9808 | 0.8381 | -0.1427 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | KANARAD3 | 0.9859 | 0.8381 | -0.1478 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | KANARAD3 | 0.9808 | 0.8381 | -0.1427 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | KANARAD3 | 0.9859 | 0.8381 | -0.1478 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | KANARAD3 | 0.9808 | 0.8381 | -0.1427 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | KANARAD3 | 0.9859 | 0.8381 | -0.1478 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | KANARAD3 | 0.9808 | 0.8381 | -0.1427 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | KANARAD3 | 0.9859 | 0.8381 | -0.1478 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | KANARAD3 | 0.9808 | 0.8381 | -0.1427 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | KANARAD3 | 0.9859 | 0.8381 | -0.1478 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | KANARAD3 | 0.9808 | 0.8381 | -0.1427 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | KANARAD3 | 0.9859 | 0.8381 | -0.1478 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | KANARAD3 | 0.9808 | 0.8381 | -0.1427 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | KANARAD3 | 0.9859 | 0.8381 | -0.1478 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | KANARAD3 | 0.9808 | 0.8381 | -0.1427 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | KANARAD3 | 0.9859 | 0.8381 | -0.1478 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | KANARAD3 | 0.9808 | 0.8381 | -0.1427 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | KANARAD3 | 0.9859 | 0.8381 | -0.1478 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | KANARAD3 | 0.9808 | 0.8381 | -0.1427 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | KANARAD3 | 0.9859 | 0.8381 | -0.1478 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | KANARAD3 | 0.9808 | 0.8381 | -0.1427 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | KANARAD3 | 0.9859 | 0.8381 | -0.1478 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | KANARAD3 | 0.9808 | 0.8381 | -0.1427 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | KANARAD3 | 0.9859 | 0.8381 | -0.1478 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | KANARAD3 | 0.9808 | 0.8381 | -0.1427 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | KANARAD3 | 0.9859 | 0.8381 | -0.1478 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | KANARAD3 | 0.9808 | 0.8381 | -0.1427 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | KANARAD3 | 0.9859 | 0.8381 | -0.1478 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | KANARAD3 | 0.9808 | 0.8381 | -0.1427 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | KANARAD3 | 0.9859 | 0.8381 | -0.1478 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | KANARAD3 | 0.9808 | 0.8381 | -0.1427 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | KANARAD3 | 0.9859 | 0.8381 | -0.1478 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | KANARAD3 | 0.9808 | 0.8381 | -0.1427 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | KANARAD3 | 0.9859 | 0.8381 | -0.1478 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | KANARAD3 | 0.9808 | 0.8381 | -0.1427 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | KANARAD3 | 0.9859 | 0.8381 | -0.1478 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | CHASE 3 | 0.9698 | 0.8395 | -0.1303 |  | 0.9 | 1.05 | 0.05095 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | CHASE 3 | 0.9698 | 0.8395 | -0.1303 |  | 0.9 | 1.05 | 0.04905 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | CHASE 3 | 0.9698 | 0.8395 | -0.1303 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | CHASE 3 | 0.9698 | 0.8395 | -0.1303 |  | 0.9 | 1.05 | 0.04262 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | CHASE 3 | 0.9698 | 0.8395 | -0.1303 |  | 0.9 | 1.05 | 0.0627 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | CHASE 3 | 0.9698 | 0.8395 | -0.1303 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | CHASE 3 | 0.9698 | 0.8395 | -0.1303 |  | 0.9 | 1.05 | 0.05043 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | CHASE 3 | 0.9698 | 0.8395 | -0.1303 |  | 0.9 | 1.05 | 0.05292 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | CHASE 3 | 0.9698 | 0.8395 | -0.1303 |  | 0.9 | 1.05 | 0.0444 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | CHASE 3 | 0.9698 | 0.8395 | -0.1303 |  | 0.9 | 1.05 | 0.04788 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | CHASE 3 | 0.9698 | 0.8395 | -0.1303 |  | 0.9 | 1.05 | 0.05824 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | CHASE 3 | 0.9698 | 0.8395 | -0.1303 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | CHASE 3 | 0.9698 | 0.8395 | -0.1303 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | CHASE 3 | 0.9698 | 0.8395 | -0.1303 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | CHASE 3 | 0.9698 | 0.8395 | -0.1303 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | CHASE 3 | 0.9698 | 0.8395 | -0.1303 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | CHASE 3 | 0.9698 | 0.8395 | -0.1303 |  | 0.9 | 1.05 | 0.04773 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | CHASE 3 | 0.9698 | 0.8395 | -0.1303 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | CHASE 3 | 0.9698 | 0.8395 | -0.1303 |  | 0.9 | 1.05 | 0.0348 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | CHASE 3 | 0.9698 | 0.8395 | -0.1303 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | CHASE 3 | 0.9698 | 0.8395 | -0.1303 |  | 0.9 | 1.05 | 0.04996 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | CHASE 3 | 0.9698 | 0.8395 | -0.1303 |  | 0.9 | 1.05 | 0.04835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | CHASE 3 | 0.9698 | 0.8395 | -0.1303 |  | 0.9 | 1.05 | 0.05448 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | CHASE 3 | 0.9698 | 0.8395 | -0.1303 |  | 0.9 | 1.05 | 0.05382 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | CHASE 3 | 0.9698 | 0.8395 | -0.1303 |  | 0.9 | 1.05 | 0.03774 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | CHASE 3 | 0.9698 | 0.8395 | -0.1303 |  | 0.9 | 1.05 | 0.04948 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | CHASE 3 | 0.9698 | 0.8395 | -0.1303 |  | 0.9 | 1.05 | 0.04054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | SHARNSP3 | 0.9699 | 0.8396 | -0.1303 |  | 0.9 | 1.05 | 0.05095 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | SHARNSP3 | 0.9699 | 0.8396 | -0.1303 |  | 0.9 | 1.05 | 0.04905 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | SHARNSP3 | 0.9699 | 0.8396 | -0.1303 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | SHARNSP3 | 0.9699 | 0.8396 | -0.1303 |  | 0.9 | 1.05 | 0.04262 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | SHARNSP3 | 0.9699 | 0.8396 | -0.1303 |  | 0.9 | 1.05 | 0.0627 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | SHARNSP3 | 0.9699 | 0.8396 | -0.1303 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | SHARNSP3 | 0.9699 | 0.8396 | -0.1303 |  | 0.9 | 1.05 | 0.05043 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | SHARNSP3 | 0.9699 | 0.8396 | -0.1303 |  | 0.9 | 1.05 | 0.05292 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | SHARNSP3 | 0.9699 | 0.8396 | -0.1303 |  | 0.9 | 1.05 | 0.0444 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | SHARNSP3 | 0.9699 | 0.8396 | -0.1303 |  | 0.9 | 1.05 | 0.04788 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | SHARNSP3 | 0.9699 | 0.8396 | -0.1303 |  | 0.9 | 1.05 | 0.05824 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | SHARNSP3 | 0.9699 | 0.8396 | -0.1303 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | SHARNSP3 | 0.9699 | 0.8396 | -0.1303 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | SHARNSP3 | 0.9699 | 0.8396 | -0.1303 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | SHARNSP3 | 0.9699 | 0.8396 | -0.1303 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | SHARNSP3 | 0.9699 | 0.8396 | -0.1303 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | SHARNSP3 | 0.9699 | 0.8396 | -0.1303 |  | 0.9 | 1.05 | 0.04773 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | SHARNSP3 | 0.9699 | 0.8396 | -0.1303 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | SHARNSP3 | 0.9699 | 0.8396 | -0.1303 |  | 0.9 | 1.05 | 0.0348 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | SHARNSP3 | 0.9699 | 0.8396 | -0.1303 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | SHARNSP3 | 0.9699 | 0.8396 | -0.1303 |  | 0.9 | 1.05 | 0.04996 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | SHARNSP3 | 0.9699 | 0.8396 | -0.1303 |  | 0.9 | 1.05 | 0.04835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | SHARNSP3 | 0.9699 | 0.8396 | -0.1303 |  | 0.9 | 1.05 | 0.05448 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | SHARNSP3 | 0.9699 | 0.8396 | -0.1303 |  | 0.9 | 1.05 | 0.05382 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | SHARNSP3 | 0.9699 | 0.8396 | -0.1303 |  | 0.9 | 1.05 | 0.03774 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | SHARNSP3 | 0.9699 | 0.8396 | -0.1303 |  | 0.9 | 1.05 | 0.04948 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | SHARNSP3 | 0.9699 | 0.8396 | -0.1303 |  | 0.9 | 1.05 | 0.04054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | NSI | 0.9676 | 0.8405 | -0.1271 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | NSI | 0.9676 | 0.8405 | -0.1271 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | NSI | 0.9676 | 0.8405 | -0.1271 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | NSI | 0.9676 | 0.8405 | -0.1271 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | NSI | 0.9676 | 0.8405 | -0.1271 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | NSI | 0.9676 | 0.8405 | -0.1271 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | NSI | 0.9676 | 0.8405 | -0.1271 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | NSI | 0.9676 | 0.8405 | -0.1271 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | NSI | 0.9676 | 0.8405 | -0.1271 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | NSI | 0.9676 | 0.8405 | -0.1271 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | NSI | 0.9676 | 0.8405 | -0.1271 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | NSI | 0.9676 | 0.8405 | -0.1271 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | NSI | 0.9676 | 0.8405 | -0.1271 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | NSI | 0.9676 | 0.8405 | -0.1271 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | NSI | 0.9676 | 0.8405 | -0.1271 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | NSI | 0.9676 | 0.8405 | -0.1271 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | NSI | 0.9676 | 0.8405 | -0.1271 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | NSI | 0.9676 | 0.8405 | -0.1271 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | NSI | 0.9676 | 0.8405 | -0.1271 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | NSI | 0.9676 | 0.8405 | -0.1271 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | NSI | 0.9676 | 0.8405 | -0.1271 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | NSI | 0.9676 | 0.8405 | -0.1271 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | NSI | 0.9676 | 0.8405 | -0.1271 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | NSI | 0.9676 | 0.8405 | -0.1271 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | NSI | 0.9676 | 0.8405 | -0.1271 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | NSI | 0.9676 | 0.8405 | -0.1271 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | NSI | 0.9676 | 0.8405 | -0.1271 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | NSI TAP3 | 0.9683 | 0.8414 | -0.1269 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | NSI TAP3 | 0.9683 | 0.8414 | -0.1269 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | NSI TAP3 | 0.9683 | 0.8414 | -0.1269 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | NSI TAP3 | 0.9683 | 0.8414 | -0.1269 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | NSI TAP3 | 0.9683 | 0.8414 | -0.1269 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | NSI TAP3 | 0.9683 | 0.8414 | -0.1269 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | NSI TAP3 | 0.9683 | 0.8414 | -0.1269 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | NSI TAP3 | 0.9683 | 0.8414 | -0.1269 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | NSI TAP3 | 0.9683 | 0.8414 | -0.1269 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | NSI TAP3 | 0.9683 | 0.8414 | -0.1269 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | NSI TAP3 | 0.9683 | 0.8414 | -0.1269 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | NSI TAP3 | 0.9683 | 0.8414 | -0.1269 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | NSI TAP3 | 0.9683 | 0.8414 | -0.1269 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | NSI TAP3 | 0.9683 | 0.8414 | -0.1269 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | NSI TAP3 | 0.9683 | 0.8414 | -0.1269 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | NSI TAP3 | 0.9683 | 0.8414 | -0.1269 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | NSI TAP3 | 0.9683 | 0.8414 | -0.1269 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | NSI TAP3 | 0.9683 | 0.8414 | -0.1269 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | NSI TAP3 | 0.9683 | 0.8414 | -0.1269 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | NSI TAP3 | 0.9683 | 0.8414 | -0.1269 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | NSI TAP3 | 0.9683 | 0.8414 | -0.1269 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | NSI TAP3 | 0.9683 | 0.8414 | -0.1269 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | NSI TAP3 | 0.9683 | 0.8414 | -0.1269 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | NSI TAP3 | 0.9683 | 0.8414 | -0.1269 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | NSI TAP3 | 0.9683 | 0.8414 | -0.1269 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | NSI TAP3 | 0.9683 | 0.8414 | -0.1269 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | NSI TAP3 | 0.9683 | 0.8414 | -0.1269 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | KANARAD3 | 0.9808 | 0.8448 | -0.136 |  | 0.9 | 1.05 | 0.05095 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | KANARAD3 | 0.9808 | 0.8448 | -0.136 |  | 0.9 | 1.05 | 0.04905 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | KANARAD3 | 0.9808 | 0.8448 | -0.136 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | KANARAD3 | 0.9808 | 0.8448 | -0.136 |  | 0.9 | 1.05 | 0.04262 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | KANARAD3 | 0.9808 | 0.8448 | -0.136 |  | 0.9 | 1.05 | 0.0627 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | KANARAD3 | 0.9808 | 0.8448 | -0.136 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | KANARAD3 | 0.9808 | 0.8448 | -0.136 |  | 0.9 | 1.05 | 0.05043 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | KANARAD3 | 0.9808 | 0.8448 | -0.136 |  | 0.9 | 1.05 | 0.05292 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | KANARAD3 | 0.9808 | 0.8448 | -0.136 |  | 0.9 | 1.05 | 0.0444 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | KANARAD3 | 0.9808 | 0.8448 | -0.136 |  | 0.9 | 1.05 | 0.04788 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | KANARAD3 | 0.9808 | 0.8448 | -0.136 |  | 0.9 | 1.05 | 0.05824 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | KANARAD3 | 0.9808 | 0.8448 | -0.136 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | KANARAD3 | 0.9808 | 0.8448 | -0.136 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | KANARAD3 | 0.9808 | 0.8448 | -0.136 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | KANARAD3 | 0.9808 | 0.8448 | -0.136 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | KANARAD3 | 0.9808 | 0.8448 | -0.136 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | KANARAD3 | 0.9808 | 0.8448 | -0.136 |  | 0.9 | 1.05 | 0.04773 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | KANARAD3 | 0.9808 | 0.8448 | -0.136 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | KANARAD3 | 0.9808 | 0.8448 | -0.136 |  | 0.9 | 1.05 | 0.0348 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | KANARAD3 | 0.9808 | 0.8448 | -0.136 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | KANARAD3 | 0.9808 | 0.8448 | -0.136 |  | 0.9 | 1.05 | 0.04996 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | KANARAD3 | 0.9808 | 0.8448 | -0.136 |  | 0.9 | 1.05 | 0.04835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | KANARAD3 | 0.9808 | 0.8448 | -0.136 |  | 0.9 | 1.05 | 0.05448 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | KANARAD3 | 0.9808 | 0.8448 | -0.136 |  | 0.9 | 1.05 | 0.05382 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | KANARAD3 | 0.9808 | 0.8448 | -0.136 |  | 0.9 | 1.05 | 0.03774 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | KANARAD3 | 0.9808 | 0.8448 | -0.136 |  | 0.9 | 1.05 | 0.04948 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | KANARAD3 | 0.9808 | 0.8448 | -0.136 |  | 0.9 | 1.05 | 0.04054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | NSI | 0.9847 | 0.8474 | -0.1373 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | NSI | 0.9893 | 0.8474 | -0.1419 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | NSI | 0.9847 | 0.8474 | -0.1373 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | NSI | 0.9893 | 0.8474 | -0.1419 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | NSI | 0.9847 | 0.8474 | -0.1373 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | NSI | 0.9893 | 0.8474 | -0.1419 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | NSI | 0.9847 | 0.8474 | -0.1373 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | NSI | 0.9893 | 0.8474 | -0.1419 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | NSI | 0.9847 | 0.8474 | -0.1373 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | NSI | 0.9893 | 0.8474 | -0.1419 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | NSI | 0.9847 | 0.8474 | -0.1373 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | NSI | 0.9893 | 0.8474 | -0.1419 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | NSI | 0.9847 | 0.8474 | -0.1373 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | NSI | 0.9893 | 0.8474 | -0.1419 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | NSI | 0.9847 | 0.8474 | -0.1373 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | NSI | 0.9893 | 0.8474 | -0.1419 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | NSI | 0.9847 | 0.8474 | -0.1373 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | NSI | 0.9893 | 0.8474 | -0.1419 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | NSI | 0.9847 | 0.8474 | -0.1373 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | NSI | 0.9893 | 0.8474 | -0.1419 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | NSI | 0.9847 | 0.8474 | -0.1373 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | NSI | 0.9893 | 0.8474 | -0.1419 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | NSI | 0.9847 | 0.8474 | -0.1373 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | NSI | 0.9893 | 0.8474 | -0.1419 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | NSI | 0.9847 | 0.8474 | -0.1373 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | NSI | 0.9893 | 0.8474 | -0.1419 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | NSI | 0.9847 | 0.8474 | -0.1373 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | NSI | 0.9893 | 0.8474 | -0.1419 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | NSI | 0.9847 | 0.8474 | -0.1373 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | NSI | 0.9893 | 0.8474 | -0.1419 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | NSI | 0.9847 | 0.8474 | -0.1373 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | NSI | 0.9893 | 0.8474 | -0.1419 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | NSI | 0.9847 | 0.8474 | -0.1373 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | NSI | 0.9893 | 0.8474 | -0.1419 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | NSI | 0.9847 | 0.8474 | -0.1373 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | NSI | 0.9893 | 0.8474 | -0.1419 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | NSI | 0.9847 | 0.8474 | -0.1373 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | NSI | 0.9893 | 0.8474 | -0.1419 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | NSI | 0.9847 | 0.8474 | -0.1373 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | NSI | 0.9893 | 0.8474 | -0.1419 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | NSI | 0.9847 | 0.8474 | -0.1373 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | NSI | 0.9893 | 0.8474 | -0.1419 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | NSI | 0.9847 | 0.8474 | -0.1373 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | NSI | 0.9893 | 0.8474 | -0.1419 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | NSI | 0.9847 | 0.8474 | -0.1373 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | NSI | 0.9893 | 0.8474 | -0.1419 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | NSI | 0.9847 | 0.8474 | -0.1373 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | NSI | 0.9893 | 0.8474 | -0.1419 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | NSI | 0.9847 | 0.8474 | -0.1373 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | NSI | 0.9893 | 0.8474 | -0.1419 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | NSI | 0.9847 | 0.8474 | -0.1373 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | NSI | 0.9893 | 0.8474 | -0.1419 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | NSI | 0.9847 | 0.8474 | -0.1373 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | NSI | 0.9893 | 0.8474 | -0.1419 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | RULETON3 | 0.9725 | 0.8478 | -0.1247 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | RULETON3 | 0.9776 | 0.8478 | -0.1298 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | RULETON3 | 0.9725 | 0.8478 | -0.1247 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | RULETON3 | 0.9776 | 0.8478 | -0.1298 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | RULETON3 | 0.9725 | 0.8478 | -0.1247 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | RULETON3 | 0.9776 | 0.8478 | -0.1298 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | RULETON3 | 0.9725 | 0.8478 | -0.1247 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | RULETON3 | 0.9776 | 0.8478 | -0.1298 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | RULETON3 | 0.9725 | 0.8478 | -0.1247 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | RULETON3 | 0.9776 | 0.8478 | -0.1298 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | RULETON3 | 0.9725 | 0.8478 | -0.1247 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | RULETON3 | 0.9776 | 0.8478 | -0.1298 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | RULETON3 | 0.9725 | 0.8478 | -0.1247 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | RULETON3 | 0.9776 | 0.8478 | -0.1298 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | RULETON3 | 0.9725 | 0.8478 | -0.1247 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | RULETON3 | 0.9776 | 0.8478 | -0.1298 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | RULETON3 | 0.9725 | 0.8478 | -0.1247 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | RULETON3 | 0.9776 | 0.8478 | -0.1298 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | RULETON3 | 0.9725 | 0.8478 | -0.1247 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | RULETON3 | 0.9776 | 0.8478 | -0.1298 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | RULETON3 | 0.9725 | 0.8478 | -0.1247 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | RULETON3 | 0.9776 | 0.8478 | -0.1298 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | RULETON3 | 0.9725 | 0.8478 | -0.1247 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | RULETON3 | 0.9776 | 0.8478 | -0.1298 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | RULETON3 | 0.9725 | 0.8478 | -0.1247 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | RULETON3 | 0.9776 | 0.8478 | -0.1298 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | RULETON3 | 0.9725 | 0.8478 | -0.1247 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | RULETON3 | 0.9776 | 0.8478 | -0.1298 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | RULETON3 | 0.9725 | 0.8478 | -0.1247 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | RULETON3 | 0.9776 | 0.8478 | -0.1298 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | RULETON3 | 0.9725 | 0.8478 | -0.1247 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | RULETON3 | 0.9776 | 0.8478 | -0.1298 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | RULETON3 | 0.9725 | 0.8478 | -0.1247 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | RULETON3 | 0.9776 | 0.8478 | -0.1298 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | RULETON3 | 0.9725 | 0.8478 | -0.1247 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | RULETON3 | 0.9776 | 0.8478 | -0.1298 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | RULETON3 | 0.9725 | 0.8478 | -0.1247 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | RULETON3 | 0.9776 | 0.8478 | -0.1298 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | RULETON3 | 0.9725 | 0.8478 | -0.1247 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | RULETON3 | 0.9776 | 0.8478 | -0.1298 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | RULETON3 | 0.9725 | 0.8478 | -0.1247 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | RULETON3 | 0.9776 | 0.8478 | -0.1298 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | RULETON3 | 0.9725 | 0.8478 | -0.1247 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | RULETON3 | 0.9776 | 0.8478 | -0.1298 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | RULETON3 | 0.9725 | 0.8478 | -0.1247 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | RULETON3 | 0.9776 | 0.8478 | -0.1298 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | RULETON3 | 0.9725 | 0.8478 | -0.1247 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | RULETON3 | 0.9776 | 0.8478 | -0.1298 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | RULETON3 | 0.9725 | 0.8478 | -0.1247 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | RULETON3 | 0.9776 | 0.8478 | -0.1298 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | RULETON3 | 0.9725 | 0.8478 | -0.1247 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | RULETON3 | 0.9776 | 0.8478 | -0.1298 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | RULETON3 | 0.9725 | 0.8478 | -0.1247 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | RULETON3 | 0.9776 | 0.8478 | -0.1298 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | NSI TAP3 | 0.9855 | 0.8484 | -0.1371 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | NSI TAP3 | 0.9901 | 0.8484 | -0.1417 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | NSI TAP3 | 0.9855 | 0.8484 | -0.1371 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | NSI TAP3 | 0.9901 | 0.8484 | -0.1417 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | NSI TAP3 | 0.9855 | 0.8484 | -0.1371 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | NSI TAP3 | 0.9901 | 0.8484 | -0.1417 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | NSI TAP3 | 0.9855 | 0.8484 | -0.1371 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | NSI TAP3 | 0.9901 | 0.8484 | -0.1417 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | NSI TAP3 | 0.9855 | 0.8484 | -0.1371 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | NSI TAP3 | 0.9901 | 0.8484 | -0.1417 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | NSI TAP3 | 0.9855 | 0.8484 | -0.1371 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | NSI TAP3 | 0.9901 | 0.8484 | -0.1417 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | NSI TAP3 | 0.9855 | 0.8484 | -0.1371 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | NSI TAP3 | 0.9901 | 0.8484 | -0.1417 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | NSI TAP3 | 0.9855 | 0.8484 | -0.1371 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | NSI TAP3 | 0.9901 | 0.8484 | -0.1417 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | NSI TAP3 | 0.9855 | 0.8484 | -0.1371 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | NSI TAP3 | 0.9901 | 0.8484 | -0.1417 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | NSI TAP3 | 0.9855 | 0.8484 | -0.1371 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | NSI TAP3 | 0.9901 | 0.8484 | -0.1417 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | NSI TAP3 | 0.9855 | 0.8484 | -0.1371 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | NSI TAP3 | 0.9901 | 0.8484 | -0.1417 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | NSI TAP3 | 0.9855 | 0.8484 | -0.1371 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | NSI TAP3 | 0.9901 | 0.8484 | -0.1417 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | NSI TAP3 | 0.9855 | 0.8484 | -0.1371 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | NSI TAP3 | 0.9901 | 0.8484 | -0.1417 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | NSI TAP3 | 0.9855 | 0.8484 | -0.1371 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | NSI TAP3 | 0.9901 | 0.8484 | -0.1417 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | NSI TAP3 | 0.9855 | 0.8484 | -0.1371 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | NSI TAP3 | 0.9901 | 0.8484 | -0.1417 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | NSI TAP3 | 0.9855 | 0.8484 | -0.1371 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | NSI TAP3 | 0.9901 | 0.8484 | -0.1417 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | NSI TAP3 | 0.9855 | 0.8484 | -0.1371 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | NSI TAP3 | 0.9901 | 0.8484 | -0.1417 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | NSI TAP3 | 0.9855 | 0.8484 | -0.1371 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | NSI TAP3 | 0.9901 | 0.8484 | -0.1417 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | NSI TAP3 | 0.9855 | 0.8484 | -0.1371 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | NSI TAP3 | 0.9901 | 0.8484 | -0.1417 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | NSI TAP3 | 0.9855 | 0.8484 | -0.1371 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | NSI TAP3 | 0.9901 | 0.8484 | -0.1417 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | NSI TAP3 | 0.9855 | 0.8484 | -0.1371 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | NSI TAP3 | 0.9901 | 0.8484 | -0.1417 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | NSI TAP3 | 0.9855 | 0.8484 | -0.1371 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | NSI TAP3 | 0.9901 | 0.8484 | -0.1417 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | NSI TAP3 | 0.9855 | 0.8484 | -0.1371 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | NSI TAP3 | 0.9901 | 0.8484 | -0.1417 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | NSI TAP3 | 0.9855 | 0.8484 | -0.1371 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | NSI TAP3 | 0.9901 | 0.8484 | -0.1417 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | NSI TAP3 | 0.9855 | 0.8484 | -0.1371 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | NSI TAP3 | 0.9901 | 0.8484 | -0.1417 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | NSI TAP3 | 0.9855 | 0.8484 | -0.1371 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | NSI TAP3 | 0.9901 | 0.8484 | -0.1417 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | NSI TAP3 | 0.9855 | 0.8484 | -0.1371 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | NSI TAP3 | 0.9901 | 0.8484 | -0.1417 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | LAWNRID3 | 0.9677 | 0.853 | -0.1147 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | LAWNRID3 | 0.9723 | 0.853 | -0.1193 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | LAWNRID3 | 0.9677 | 0.853 | -0.1147 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | LAWNRID3 | 0.9723 | 0.853 | -0.1193 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | LAWNRID3 | 0.9677 | 0.853 | -0.1147 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | LAWNRID3 | 0.9723 | 0.853 | -0.1193 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | LAWNRID3 | 0.9677 | 0.853 | -0.1147 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | LAWNRID3 | 0.9723 | 0.853 | -0.1193 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | LAWNRID3 | 0.9677 | 0.853 | -0.1147 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | LAWNRID3 | 0.9723 | 0.853 | -0.1193 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | LAWNRID3 | 0.9677 | 0.853 | -0.1147 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | LAWNRID3 | 0.9723 | 0.853 | -0.1193 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | LAWNRID3 | 0.9677 | 0.853 | -0.1147 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | LAWNRID3 | 0.9723 | 0.853 | -0.1193 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | LAWNRID3 | 0.9677 | 0.853 | -0.1147 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | LAWNRID3 | 0.9723 | 0.853 | -0.1193 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | LAWNRID3 | 0.9677 | 0.853 | -0.1147 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | LAWNRID3 | 0.9723 | 0.853 | -0.1193 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | LAWNRID3 | 0.9677 | 0.853 | -0.1147 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | LAWNRID3 | 0.9723 | 0.853 | -0.1193 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | LAWNRID3 | 0.9677 | 0.853 | -0.1147 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | LAWNRID3 | 0.9723 | 0.853 | -0.1193 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | LAWNRID3 | 0.9677 | 0.853 | -0.1147 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | LAWNRID3 | 0.9723 | 0.853 | -0.1193 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | LAWNRID3 | 0.9677 | 0.853 | -0.1147 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | LAWNRID3 | 0.9723 | 0.853 | -0.1193 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | LAWNRID3 | 0.9677 | 0.853 | -0.1147 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | LAWNRID3 | 0.9723 | 0.853 | -0.1193 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | LAWNRID3 | 0.9677 | 0.853 | -0.1147 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | LAWNRID3 | 0.9723 | 0.853 | -0.1193 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | LAWNRID3 | 0.9677 | 0.853 | -0.1147 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | LAWNRID3 | 0.9723 | 0.853 | -0.1193 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | LAWNRID3 | 0.9677 | 0.853 | -0.1147 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | LAWNRID3 | 0.9723 | 0.853 | -0.1193 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | LAWNRID3 | 0.9677 | 0.853 | -0.1147 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | LAWNRID3 | 0.9723 | 0.853 | -0.1193 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | LAWNRID3 | 0.9677 | 0.853 | -0.1147 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | LAWNRID3 | 0.9723 | 0.853 | -0.1193 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | LAWNRID3 | 0.9677 | 0.853 | -0.1147 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | LAWNRID3 | 0.9723 | 0.853 | -0.1193 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | LAWNRID3 | 0.9677 | 0.853 | -0.1147 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | LAWNRID3 | 0.9723 | 0.853 | -0.1193 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | LAWNRID3 | 0.9677 | 0.853 | -0.1147 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | LAWNRID3 | 0.9723 | 0.853 | -0.1193 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | LAWNRID3 | 0.9677 | 0.853 | -0.1147 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | LAWNRID3 | 0.9723 | 0.853 | -0.1193 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | LAWNRID3 | 0.9677 | 0.853 | -0.1147 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | LAWNRID3 | 0.9723 | 0.853 | -0.1193 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | LAWNRID3 | 0.9677 | 0.853 | -0.1147 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | LAWNRID3 | 0.9723 | 0.853 | -0.1193 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | LAWNRID3 | 0.9677 | 0.853 | -0.1147 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | LAWNRID3 | 0.9723 | 0.853 | -0.1193 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | LAWNRID3 | 0.9677 | 0.853 | -0.1147 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | LAWNRID3 | 0.9723 | 0.853 | -0.1193 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | NSI | 0.9847 | 0.854 | -0.1307 |  | 0.9 | 1.05 | 0.05095 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | NSI | 0.9847 | 0.854 | -0.1307 |  | 0.9 | 1.05 | 0.04905 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | NSI | 0.9847 | 0.854 | -0.1307 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | NSI | 0.9847 | 0.854 | -0.1307 |  | 0.9 | 1.05 | 0.04262 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | NSI | 0.9847 | 0.854 | -0.1307 |  | 0.9 | 1.05 | 0.0627 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | NSI | 0.9847 | 0.854 | -0.1307 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | NSI | 0.9847 | 0.854 | -0.1307 |  | 0.9 | 1.05 | 0.05043 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | NSI | 0.9847 | 0.854 | -0.1307 |  | 0.9 | 1.05 | 0.05292 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | NSI | 0.9847 | 0.854 | -0.1307 |  | 0.9 | 1.05 | 0.0444 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | NSI | 0.9847 | 0.854 | -0.1307 |  | 0.9 | 1.05 | 0.04788 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | NSI | 0.9847 | 0.854 | -0.1307 |  | 0.9 | 1.05 | 0.05824 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | NSI | 0.9847 | 0.854 | -0.1307 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | NSI | 0.9847 | 0.854 | -0.1307 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | NSI | 0.9847 | 0.854 | -0.1307 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | NSI | 0.9847 | 0.854 | -0.1307 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | NSI | 0.9847 | 0.854 | -0.1307 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | NSI | 0.9847 | 0.854 | -0.1307 |  | 0.9 | 1.05 | 0.04773 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | NSI | 0.9847 | 0.854 | -0.1307 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | NSI | 0.9847 | 0.854 | -0.1307 |  | 0.9 | 1.05 | 0.0348 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | NSI | 0.9847 | 0.854 | -0.1307 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | NSI | 0.9847 | 0.854 | -0.1307 |  | 0.9 | 1.05 | 0.04996 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | NSI | 0.9847 | 0.854 | -0.1307 |  | 0.9 | 1.05 | 0.04835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | NSI | 0.9847 | 0.854 | -0.1307 |  | 0.9 | 1.05 | 0.05448 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | NSI | 0.9847 | 0.854 | -0.1307 |  | 0.9 | 1.05 | 0.05382 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | NSI | 0.9847 | 0.854 | -0.1307 |  | 0.9 | 1.05 | 0.03774 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | NSI | 0.9847 | 0.854 | -0.1307 |  | 0.9 | 1.05 | 0.04948 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | NSI | 0.9847 | 0.854 | -0.1307 |  | 0.9 | 1.05 | 0.04054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | RULETON3 | 0.9725 | 0.8541 | -0.1184 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | RULETON3 | 0.9725 | 0.8541 | -0.1184 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | RULETON3 | 0.9725 | 0.8541 | -0.1184 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | RULETON3 | 0.9725 | 0.8541 | -0.1184 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | RULETON3 | 0.9725 | 0.8541 | -0.1184 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | RULETON3 | 0.9725 | 0.8541 | -0.1184 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | RULETON3 | 0.9725 | 0.8541 | -0.1184 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | RULETON3 | 0.9725 | 0.8541 | -0.1184 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | RULETON3 | 0.9725 | 0.8541 | -0.1184 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | RULETON3 | 0.9725 | 0.8541 | -0.1184 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | RULETON3 | 0.9725 | 0.8541 | -0.1184 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | RULETON3 | 0.9725 | 0.8541 | -0.1184 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | RULETON3 | 0.9725 | 0.8541 | -0.1184 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | RULETON3 | 0.9725 | 0.8541 | -0.1184 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | RULETON3 | 0.9725 | 0.8541 | -0.1184 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | RULETON3 | 0.9725 | 0.8541 | -0.1184 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | RULETON3 | 0.9725 | 0.8541 | -0.1184 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | RULETON3 | 0.9725 | 0.8541 | -0.1184 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | RULETON3 | 0.9725 | 0.8541 | -0.1184 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | RULETON3 | 0.9725 | 0.8541 | -0.1184 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | RULETON3 | 0.9725 | 0.8541 | -0.1184 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | RULETON3 | 0.9725 | 0.8541 | -0.1184 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | RULETON3 | 0.9725 | 0.8541 | -0.1184 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | RULETON3 | 0.9725 | 0.8541 | -0.1184 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | RULETON3 | 0.9725 | 0.8541 | -0.1184 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | RULETON3 | 0.9725 | 0.8541 | -0.1184 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | RULETON3 | 0.9725 | 0.8541 | -0.1184 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | NSI TAP3 | 0.9855 | 0.855 | -0.1305 |  | 0.9 | 1.05 | 0.05095 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | NSI TAP3 | 0.9855 | 0.855 | -0.1305 |  | 0.9 | 1.05 | 0.04905 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | NSI TAP3 | 0.9855 | 0.855 | -0.1305 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | NSI TAP3 | 0.9855 | 0.855 | -0.1305 |  | 0.9 | 1.05 | 0.04262 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | NSI TAP3 | 0.9855 | 0.855 | -0.1305 |  | 0.9 | 1.05 | 0.0627 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | NSI TAP3 | 0.9855 | 0.855 | -0.1305 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | NSI TAP3 | 0.9855 | 0.855 | -0.1305 |  | 0.9 | 1.05 | 0.05043 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | NSI TAP3 | 0.9855 | 0.855 | -0.1305 |  | 0.9 | 1.05 | 0.05292 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | NSI TAP3 | 0.9855 | 0.855 | -0.1305 |  | 0.9 | 1.05 | 0.0444 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | NSI TAP3 | 0.9855 | 0.855 | -0.1305 |  | 0.9 | 1.05 | 0.04788 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | NSI TAP3 | 0.9855 | 0.855 | -0.1305 |  | 0.9 | 1.05 | 0.05824 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | NSI TAP3 | 0.9855 | 0.855 | -0.1305 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | NSI TAP3 | 0.9855 | 0.855 | -0.1305 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | NSI TAP3 | 0.9855 | 0.855 | -0.1305 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | NSI TAP3 | 0.9855 | 0.855 | -0.1305 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | NSI TAP3 | 0.9855 | 0.855 | -0.1305 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | NSI TAP3 | 0.9855 | 0.855 | -0.1305 |  | 0.9 | 1.05 | 0.04773 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | NSI TAP3 | 0.9855 | 0.855 | -0.1305 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | NSI TAP3 | 0.9855 | 0.855 | -0.1305 |  | 0.9 | 1.05 | 0.0348 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | NSI TAP3 | 0.9855 | 0.855 | -0.1305 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | NSI TAP3 | 0.9855 | 0.855 | -0.1305 |  | 0.9 | 1.05 | 0.04996 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | NSI TAP3 | 0.9855 | 0.855 | -0.1305 |  | 0.9 | 1.05 | 0.04835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | NSI TAP3 | 0.9855 | 0.855 | -0.1305 |  | 0.9 | 1.05 | 0.05448 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | NSI TAP3 | 0.9855 | 0.855 | -0.1305 |  | 0.9 | 1.05 | 0.05382 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | NSI TAP3 | 0.9855 | 0.855 | -0.1305 |  | 0.9 | 1.05 | 0.03774 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | NSI TAP3 | 0.9855 | 0.855 | -0.1305 |  | 0.9 | 1.05 | 0.04948 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | NSI TAP3 | 0.9855 | 0.855 | -0.1305 |  | 0.9 | 1.05 | 0.04054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | LAWNRID3 | 0.9677 | 0.859 | -0.1087 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | ELLIS 2 | 0.963 | 0.859 | -0.104 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | ELLIS 2 | 0.969 | 0.859 | -0.11 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | LAWNRID3 | 0.9677 | 0.859 | -0.1087 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | ELLIS 2 | 0.963 | 0.859 | -0.104 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | ELLIS 2 | 0.969 | 0.859 | -0.11 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | LAWNRID3 | 0.9677 | 0.859 | -0.1087 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | ELLIS 2 | 0.963 | 0.859 | -0.104 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | ELLIS 2 | 0.969 | 0.859 | -0.11 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | LAWNRID3 | 0.9677 | 0.859 | -0.1087 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | ELLIS 2 | 0.963 | 0.859 | -0.104 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | ELLIS 2 | 0.969 | 0.859 | -0.11 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | LAWNRID3 | 0.9677 | 0.859 | -0.1087 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | ELLIS 2 | 0.963 | 0.859 | -0.104 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | ELLIS 2 | 0.969 | 0.859 | -0.11 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | LAWNRID3 | 0.9677 | 0.859 | -0.1087 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | ELLIS 2 | 0.963 | 0.859 | -0.104 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | ELLIS 2 | 0.969 | 0.859 | -0.11 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | LAWNRID3 | 0.9677 | 0.859 | -0.1087 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | ELLIS 2 | 0.963 | 0.859 | -0.104 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | ELLIS 2 | 0.969 | 0.859 | -0.11 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | LAWNRID3 | 0.9677 | 0.859 | -0.1087 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | ELLIS 2 | 0.963 | 0.859 | -0.104 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | ELLIS 2 | 0.969 | 0.859 | -0.11 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | LAWNRID3 | 0.9677 | 0.859 | -0.1087 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | ELLIS 2 | 0.963 | 0.859 | -0.104 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | ELLIS 2 | 0.969 | 0.859 | -0.11 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | LAWNRID3 | 0.9677 | 0.859 | -0.1087 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | ELLIS 2 | 0.963 | 0.859 | -0.104 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | ELLIS 2 | 0.969 | 0.859 | -0.11 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | LAWNRID3 | 0.9677 | 0.859 | -0.1087 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | ELLIS 2 | 0.963 | 0.859 | -0.104 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | ELLIS 2 | 0.969 | 0.859 | -0.11 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | LAWNRID3 | 0.9677 | 0.859 | -0.1087 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | ELLIS 2 | 0.963 | 0.859 | -0.104 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | ELLIS 2 | 0.969 | 0.859 | -0.11 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | LAWNRID3 | 0.9677 | 0.859 | -0.1087 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | ELLIS 2 | 0.963 | 0.859 | -0.104 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | ELLIS 2 | 0.969 | 0.859 | -0.11 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | LAWNRID3 | 0.9677 | 0.859 | -0.1087 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | ELLIS 2 | 0.963 | 0.859 | -0.104 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | ELLIS 2 | 0.969 | 0.859 | -0.11 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | LAWNRID3 | 0.9677 | 0.859 | -0.1087 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | ELLIS 2 | 0.963 | 0.859 | -0.104 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | ELLIS 2 | 0.969 | 0.859 | -0.11 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | LAWNRID3 | 0.9677 | 0.859 | -0.1087 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | ELLIS 2 | 0.963 | 0.859 | -0.104 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | ELLIS 2 | 0.969 | 0.859 | -0.11 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | LAWNRID3 | 0.9677 | 0.859 | -0.1087 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | ELLIS 2 | 0.963 | 0.859 | -0.104 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | ELLIS 2 | 0.969 | 0.859 | -0.11 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | LAWNRID3 | 0.9677 | 0.859 | -0.1087 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | ELLIS 2 | 0.963 | 0.859 | -0.104 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | ELLIS 2 | 0.969 | 0.859 | -0.11 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | LAWNRID3 | 0.9677 | 0.859 | -0.1087 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | ELLIS 2 | 0.963 | 0.859 | -0.104 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | ELLIS 2 | 0.969 | 0.859 | -0.11 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | LAWNRID3 | 0.9677 | 0.859 | -0.1087 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | ELLIS 2 | 0.963 | 0.859 | -0.104 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | ELLIS 2 | 0.969 | 0.859 | -0.11 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | LAWNRID3 | 0.9677 | 0.859 | -0.1087 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | ELLIS 2 | 0.963 | 0.859 | -0.104 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | ELLIS 2 | 0.969 | 0.859 | -0.11 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | LAWNRID3 | 0.9677 | 0.859 | -0.1087 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | ELLIS 2 | 0.963 | 0.859 | -0.104 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | ELLIS 2 | 0.969 | 0.859 | -0.11 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | LAWNRID3 | 0.9677 | 0.859 | -0.1087 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | ELLIS 2 | 0.963 | 0.859 | -0.104 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | ELLIS 2 | 0.969 | 0.859 | -0.11 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | LAWNRID3 | 0.9677 | 0.859 | -0.1087 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | ELLIS 2 | 0.963 | 0.859 | -0.104 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | ELLIS 2 | 0.969 | 0.859 | -0.11 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | LAWNRID3 | 0.9677 | 0.859 | -0.1087 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | ELLIS 2 | 0.963 | 0.859 | -0.104 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | ELLIS 2 | 0.969 | 0.859 | -0.11 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | LAWNRID3 | 0.9677 | 0.859 | -0.1087 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | ELLIS 2 | 0.963 | 0.859 | -0.104 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | ELLIS 2 | 0.969 | 0.859 | -0.11 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | LAWNRID3 | 0.9677 | 0.859 | -0.1087 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | ELLIS 2 | 0.963 | 0.859 | -0.104 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | ELLIS 2 | 0.969 | 0.859 | -0.11 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | CHASE 3 | 0.9603 | 0.861 | -0.0993 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | CHASE 3 | 0.9603 | 0.861 | -0.0993 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | CHASE 3 | 0.9603 | 0.861 | -0.0993 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | CHASE 3 | 0.9603 | 0.861 | -0.0993 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | CHASE 3 | 0.9603 | 0.861 | -0.0993 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | CHASE 3 | 0.9603 | 0.861 | -0.0993 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | CHASE 3 | 0.9603 | 0.861 | -0.0993 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | CHASE 3 | 0.9603 | 0.861 | -0.0993 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | CHASE 3 | 0.9603 | 0.861 | -0.0993 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | CHASE 3 | 0.9603 | 0.861 | -0.0993 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | CHASE 3 | 0.9603 | 0.861 | -0.0993 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | CHASE 3 | 0.9603 | 0.861 | -0.0993 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | CHASE 3 | 0.9603 | 0.861 | -0.0993 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | CHASE 3 | 0.9603 | 0.861 | -0.0993 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | CHASE 3 | 0.9603 | 0.861 | -0.0993 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | CHASE 3 | 0.9603 | 0.861 | -0.0993 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | CHASE 3 | 0.9603 | 0.861 | -0.0993 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | CHASE 3 | 0.9603 | 0.861 | -0.0993 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | CHASE 3 | 0.9603 | 0.861 | -0.0993 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | CHASE 3 | 0.9603 | 0.861 | -0.0993 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | CHASE 3 | 0.9603 | 0.861 | -0.0993 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | CHASE 3 | 0.9603 | 0.861 | -0.0993 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | CHASE 3 | 0.9603 | 0.861 | -0.0993 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | CHASE 3 | 0.9603 | 0.861 | -0.0993 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | CHASE 3 | 0.9603 | 0.861 | -0.0993 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | CHASE 3 | 0.9603 | 0.861 | -0.0993 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | CHASE 3 | 0.9603 | 0.861 | -0.0993 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | SHARNSP3 | 0.9604 | 0.8611 | -0.0993 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | SHARNSP3 | 0.9604 | 0.8611 | -0.0993 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | SHARNSP3 | 0.9604 | 0.8611 | -0.0993 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | SHARNSP3 | 0.9604 | 0.8611 | -0.0993 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | SHARNSP3 | 0.9604 | 0.8611 | -0.0993 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | SHARNSP3 | 0.9604 | 0.8611 | -0.0993 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | SHARNSP3 | 0.9604 | 0.8611 | -0.0993 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | SHARNSP3 | 0.9604 | 0.8611 | -0.0993 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | SHARNSP3 | 0.9604 | 0.8611 | -0.0993 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | SHARNSP3 | 0.9604 | 0.8611 | -0.0993 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | SHARNSP3 | 0.9604 | 0.8611 | -0.0993 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | SHARNSP3 | 0.9604 | 0.8611 | -0.0993 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | SHARNSP3 | 0.9604 | 0.8611 | -0.0993 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | SHARNSP3 | 0.9604 | 0.8611 | -0.0993 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | SHARNSP3 | 0.9604 | 0.8611 | -0.0993 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | SHARNSP3 | 0.9604 | 0.8611 | -0.0993 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | SHARNSP3 | 0.9604 | 0.8611 | -0.0993 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | SHARNSP3 | 0.9604 | 0.8611 | -0.0993 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | SHARNSP3 | 0.9604 | 0.8611 | -0.0993 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | SHARNSP3 | 0.9604 | 0.8611 | -0.0993 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | SHARNSP3 | 0.9604 | 0.8611 | -0.0993 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | SHARNSP3 | 0.9604 | 0.8611 | -0.0993 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | SHARNSP3 | 0.9604 | 0.8611 | -0.0993 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | SHARNSP3 | 0.9604 | 0.8611 | -0.0993 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | SHARNSP3 | 0.9604 | 0.8611 | -0.0993 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | SHARNSP3 | 0.9604 | 0.8611 | -0.0993 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | SHARNSP3 | 0.9604 | 0.8611 | -0.0993 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | RULETON3 | 0.9909 | 0.8618 | -0.1291 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | RULETON3 | 0.9952 | 0.8618 | -0.1334 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | RULETON3 | 0.9909 | 0.8618 | -0.1291 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | RULETON3 | 0.9952 | 0.8618 | -0.1334 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | RULETON3 | 0.9909 | 0.8618 | -0.1291 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | RULETON3 | 0.9952 | 0.8618 | -0.1334 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | RULETON3 | 0.9909 | 0.8618 | -0.1291 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | RULETON3 | 0.9952 | 0.8618 | -0.1334 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | RULETON3 | 0.9909 | 0.8618 | -0.1291 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | RULETON3 | 0.9952 | 0.8618 | -0.1334 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | RULETON3 | 0.9909 | 0.8618 | -0.1291 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | RULETON3 | 0.9952 | 0.8618 | -0.1334 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | RULETON3 | 0.9909 | 0.8618 | -0.1291 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | RULETON3 | 0.9952 | 0.8618 | -0.1334 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | RULETON3 | 0.9909 | 0.8618 | -0.1291 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | RULETON3 | 0.9952 | 0.8618 | -0.1334 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | RULETON3 | 0.9909 | 0.8618 | -0.1291 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | RULETON3 | 0.9952 | 0.8618 | -0.1334 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | RULETON3 | 0.9909 | 0.8618 | -0.1291 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | RULETON3 | 0.9952 | 0.8618 | -0.1334 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | RULETON3 | 0.9909 | 0.8618 | -0.1291 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | RULETON3 | 0.9952 | 0.8618 | -0.1334 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | RULETON3 | 0.9909 | 0.8618 | -0.1291 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | RULETON3 | 0.9952 | 0.8618 | -0.1334 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | RULETON3 | 0.9909 | 0.8618 | -0.1291 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | RULETON3 | 0.9952 | 0.8618 | -0.1334 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | RULETON3 | 0.9909 | 0.8618 | -0.1291 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | RULETON3 | 0.9952 | 0.8618 | -0.1334 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | RULETON3 | 0.9909 | 0.8618 | -0.1291 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | RULETON3 | 0.9952 | 0.8618 | -0.1334 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | RULETON3 | 0.9909 | 0.8618 | -0.1291 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | RULETON3 | 0.9952 | 0.8618 | -0.1334 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | RULETON3 | 0.9909 | 0.8618 | -0.1291 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | RULETON3 | 0.9952 | 0.8618 | -0.1334 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | RULETON3 | 0.9909 | 0.8618 | -0.1291 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | RULETON3 | 0.9952 | 0.8618 | -0.1334 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | RULETON3 | 0.9909 | 0.8618 | -0.1291 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | RULETON3 | 0.9952 | 0.8618 | -0.1334 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | RULETON3 | 0.9909 | 0.8618 | -0.1291 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | RULETON3 | 0.9952 | 0.8618 | -0.1334 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | RULETON3 | 0.9909 | 0.8618 | -0.1291 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | RULETON3 | 0.9952 | 0.8618 | -0.1334 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | RULETON3 | 0.9909 | 0.8618 | -0.1291 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | RULETON3 | 0.9952 | 0.8618 | -0.1334 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | RULETON3 | 0.9909 | 0.8618 | -0.1291 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | RULETON3 | 0.9952 | 0.8618 | -0.1334 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | RULETON3 | 0.9909 | 0.8618 | -0.1291 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | RULETON3 | 0.9952 | 0.8618 | -0.1334 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | RULETON3 | 0.9909 | 0.8618 | -0.1291 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | RULETON3 | 0.9952 | 0.8618 | -0.1334 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | RULETON3 | 0.9909 | 0.8618 | -0.1291 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | RULETON3 | 0.9952 | 0.8618 | -0.1334 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | RULETON3 | 0.9909 | 0.8618 | -0.1291 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | RULETON3 | 0.9952 | 0.8618 | -0.1334 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | ELLIS 2 | 0.963 | 0.8629 | -0.1001 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | ELLIS 2 | 0.963 | 0.8629 | -0.1001 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | ELLIS 2 | 0.963 | 0.8629 | -0.1001 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | ELLIS 2 | 0.963 | 0.8629 | -0.1001 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | ELLIS 2 | 0.963 | 0.8629 | -0.1001 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | ELLIS 2 | 0.963 | 0.8629 | -0.1001 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | ELLIS 2 | 0.963 | 0.8629 | -0.1001 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | ELLIS 2 | 0.963 | 0.8629 | -0.1001 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | ELLIS 2 | 0.963 | 0.8629 | -0.1001 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | ELLIS 2 | 0.963 | 0.8629 | -0.1001 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | ELLIS 2 | 0.963 | 0.8629 | -0.1001 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | ELLIS 2 | 0.963 | 0.8629 | -0.1001 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | ELLIS 2 | 0.963 | 0.8629 | -0.1001 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | ELLIS 2 | 0.963 | 0.8629 | -0.1001 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | ELLIS 2 | 0.963 | 0.8629 | -0.1001 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | ELLIS 2 | 0.963 | 0.8629 | -0.1001 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | ELLIS 2 | 0.963 | 0.8629 | -0.1001 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | ELLIS 2 | 0.963 | 0.8629 | -0.1001 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | ELLIS 2 | 0.963 | 0.8629 | -0.1001 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | ELLIS 2 | 0.963 | 0.8629 | -0.1001 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | ELLIS 2 | 0.963 | 0.8629 | -0.1001 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | ELLIS 2 | 0.963 | 0.8629 | -0.1001 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | ELLIS 2 | 0.963 | 0.8629 | -0.1001 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | ELLIS 2 | 0.963 | 0.8629 | -0.1001 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | ELLIS 2 | 0.963 | 0.8629 | -0.1001 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | ELLIS 2 | 0.963 | 0.8629 | -0.1001 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | ELLIS 2 | 0.963 | 0.8629 | -0.1001 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | CSTFRAN3 | 0.9659 | 0.8638 | -0.1021 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | CSTFRAN3 | 0.9703 | 0.8638 | -0.1065 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | CSTFRAN3 | 0.9659 | 0.8638 | -0.1021 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | CSTFRAN3 | 0.9703 | 0.8638 | -0.1065 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | CSTFRAN3 | 0.9659 | 0.8638 | -0.1021 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | CSTFRAN3 | 0.9703 | 0.8638 | -0.1065 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | CSTFRAN3 | 0.9659 | 0.8638 | -0.1021 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | CSTFRAN3 | 0.9703 | 0.8638 | -0.1065 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | CSTFRAN3 | 0.9659 | 0.8638 | -0.1021 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | CSTFRAN3 | 0.9703 | 0.8638 | -0.1065 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | CSTFRAN3 | 0.9659 | 0.8638 | -0.1021 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | CSTFRAN3 | 0.9703 | 0.8638 | -0.1065 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | CSTFRAN3 | 0.9659 | 0.8638 | -0.1021 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | CSTFRAN3 | 0.9703 | 0.8638 | -0.1065 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | CSTFRAN3 | 0.9659 | 0.8638 | -0.1021 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | CSTFRAN3 | 0.9703 | 0.8638 | -0.1065 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | CSTFRAN3 | 0.9659 | 0.8638 | -0.1021 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | CSTFRAN3 | 0.9703 | 0.8638 | -0.1065 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | CSTFRAN3 | 0.9659 | 0.8638 | -0.1021 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | CSTFRAN3 | 0.9703 | 0.8638 | -0.1065 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | CSTFRAN3 | 0.9659 | 0.8638 | -0.1021 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | CSTFRAN3 | 0.9703 | 0.8638 | -0.1065 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | CSTFRAN3 | 0.9659 | 0.8638 | -0.1021 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | CSTFRAN3 | 0.9703 | 0.8638 | -0.1065 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | CSTFRAN3 | 0.9659 | 0.8638 | -0.1021 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | CSTFRAN3 | 0.9703 | 0.8638 | -0.1065 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | CSTFRAN3 | 0.9659 | 0.8638 | -0.1021 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | CSTFRAN3 | 0.9703 | 0.8638 | -0.1065 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | CSTFRAN3 | 0.9659 | 0.8638 | -0.1021 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | CSTFRAN3 | 0.9703 | 0.8638 | -0.1065 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | CSTFRAN3 | 0.9659 | 0.8638 | -0.1021 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | CSTFRAN3 | 0.9703 | 0.8638 | -0.1065 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | CSTFRAN3 | 0.9659 | 0.8638 | -0.1021 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | CSTFRAN3 | 0.9703 | 0.8638 | -0.1065 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | CSTFRAN3 | 0.9659 | 0.8638 | -0.1021 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | CSTFRAN3 | 0.9703 | 0.8638 | -0.1065 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | CSTFRAN3 | 0.9659 | 0.8638 | -0.1021 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | CSTFRAN3 | 0.9703 | 0.8638 | -0.1065 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | CSTFRAN3 | 0.9659 | 0.8638 | -0.1021 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | CSTFRAN3 | 0.9703 | 0.8638 | -0.1065 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | CSTFRAN3 | 0.9659 | 0.8638 | -0.1021 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | CSTFRAN3 | 0.9703 | 0.8638 | -0.1065 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | CSTFRAN3 | 0.9659 | 0.8638 | -0.1021 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | CSTFRAN3 | 0.9703 | 0.8638 | -0.1065 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | CSTFRAN3 | 0.9659 | 0.8638 | -0.1021 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | CSTFRAN3 | 0.9703 | 0.8638 | -0.1065 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | CSTFRAN3 | 0.9659 | 0.8638 | -0.1021 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | CSTFRAN3 | 0.9703 | 0.8638 | -0.1065 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | CSTFRAN3 | 0.9659 | 0.8638 | -0.1021 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | CSTFRAN3 | 0.9703 | 0.8638 | -0.1065 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | CSTFRAN3 | 0.9659 | 0.8638 | -0.1021 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | CSTFRAN3 | 0.9703 | 0.8638 | -0.1065 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | CSTFRAN3 | 0.9659 | 0.8638 | -0.1021 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | CSTFRAN3 | 0.9703 | 0.8638 | -0.1065 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | STFRANT3 | 0.9661 | 0.864 | -0.1021 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | STFRANT3 | 0.9704 | 0.864 | -0.1064 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | STFRANT3 | 0.9661 | 0.864 | -0.1021 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | STFRANT3 | 0.9704 | 0.864 | -0.1064 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | STFRANT3 | 0.9661 | 0.864 | -0.1021 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | STFRANT3 | 0.9704 | 0.864 | -0.1064 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | STFRANT3 | 0.9661 | 0.864 | -0.1021 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | STFRANT3 | 0.9704 | 0.864 | -0.1064 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | STFRANT3 | 0.9661 | 0.864 | -0.1021 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | STFRANT3 | 0.9704 | 0.864 | -0.1064 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | STFRANT3 | 0.9661 | 0.864 | -0.1021 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | STFRANT3 | 0.9704 | 0.864 | -0.1064 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | STFRANT3 | 0.9661 | 0.864 | -0.1021 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | STFRANT3 | 0.9704 | 0.864 | -0.1064 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | STFRANT3 | 0.9661 | 0.864 | -0.1021 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | STFRANT3 | 0.9704 | 0.864 | -0.1064 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | STFRANT3 | 0.9661 | 0.864 | -0.1021 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | STFRANT3 | 0.9704 | 0.864 | -0.1064 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | STFRANT3 | 0.9661 | 0.864 | -0.1021 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | STFRANT3 | 0.9704 | 0.864 | -0.1064 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | STFRANT3 | 0.9661 | 0.864 | -0.1021 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | STFRANT3 | 0.9704 | 0.864 | -0.1064 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | STFRANT3 | 0.9661 | 0.864 | -0.1021 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | STFRANT3 | 0.9704 | 0.864 | -0.1064 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | STFRANT3 | 0.9661 | 0.864 | -0.1021 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | STFRANT3 | 0.9704 | 0.864 | -0.1064 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | STFRANT3 | 0.9661 | 0.864 | -0.1021 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | STFRANT3 | 0.9704 | 0.864 | -0.1064 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | STFRANT3 | 0.9661 | 0.864 | -0.1021 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | STFRANT3 | 0.9704 | 0.864 | -0.1064 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | STFRANT3 | 0.9661 | 0.864 | -0.1021 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | STFRANT3 | 0.9704 | 0.864 | -0.1064 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | STFRANT3 | 0.9661 | 0.864 | -0.1021 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | STFRANT3 | 0.9704 | 0.864 | -0.1064 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | STFRANT3 | 0.9661 | 0.864 | -0.1021 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | STFRANT3 | 0.9704 | 0.864 | -0.1064 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | STFRANT3 | 0.9661 | 0.864 | -0.1021 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | STFRANT3 | 0.9704 | 0.864 | -0.1064 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | STFRANT3 | 0.9661 | 0.864 | -0.1021 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | STFRANT3 | 0.9704 | 0.864 | -0.1064 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | STFRANT3 | 0.9661 | 0.864 | -0.1021 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | STFRANT3 | 0.9704 | 0.864 | -0.1064 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | STFRANT3 | 0.9661 | 0.864 | -0.1021 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | STFRANT3 | 0.9704 | 0.864 | -0.1064 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | STFRANT3 | 0.9661 | 0.864 | -0.1021 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | STFRANT3 | 0.9704 | 0.864 | -0.1064 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | STFRANT3 | 0.9661 | 0.864 | -0.1021 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | STFRANT3 | 0.9704 | 0.864 | -0.1064 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | STFRANT3 | 0.9661 | 0.864 | -0.1021 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | STFRANT3 | 0.9704 | 0.864 | -0.1064 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | STFRANT3 | 0.9661 | 0.864 | -0.1021 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | STFRANT3 | 0.9704 | 0.864 | -0.1064 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | STFRANT3 | 0.9661 | 0.864 | -0.1021 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | STFRANT3 | 0.9704 | 0.864 | -0.1064 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | WTCLF 3 | 0.9595 | 0.8652 | -0.0943 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | WTCLF 3 | 0.9595 | 0.8652 | -0.0943 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | WTCLF 3 | 0.9595 | 0.8652 | -0.0943 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | WTCLF 3 | 0.9595 | 0.8652 | -0.0943 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | WTCLF 3 | 0.9595 | 0.8652 | -0.0943 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | WTCLF 3 | 0.9595 | 0.8652 | -0.0943 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | WTCLF 3 | 0.9595 | 0.8652 | -0.0943 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | WTCLF 3 | 0.9595 | 0.8652 | -0.0943 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | WTCLF 3 | 0.9595 | 0.8652 | -0.0943 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | WTCLF 3 | 0.9595 | 0.8652 | -0.0943 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | WTCLF 3 | 0.9595 | 0.8652 | -0.0943 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | WTCLF 3 | 0.9595 | 0.8652 | -0.0943 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | WTCLF 3 | 0.9595 | 0.8652 | -0.0943 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | WTCLF 3 | 0.9595 | 0.8652 | -0.0943 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | WTCLF 3 | 0.9595 | 0.8652 | -0.0943 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | WTCLF 3 | 0.9595 | 0.8652 | -0.0943 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | WTCLF 3 | 0.9595 | 0.8652 | -0.0943 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | WTCLF 3 | 0.9595 | 0.8652 | -0.0943 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | WTCLF 3 | 0.9595 | 0.8652 | -0.0943 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | WTCLF 3 | 0.9595 | 0.8652 | -0.0943 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | WTCLF 3 | 0.9595 | 0.8652 | -0.0943 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | WTCLF 3 | 0.9595 | 0.8652 | -0.0943 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | WTCLF 3 | 0.9595 | 0.8652 | -0.0943 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | WTCLF 3 | 0.9595 | 0.8652 | -0.0943 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | WTCLF 3 | 0.9595 | 0.8652 | -0.0943 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | WTCLF 3 | 0.9595 | 0.8652 | -0.0943 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | WTCLF 3 | 0.9595 | 0.8652 | -0.0943 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | RANSOM 2 | 0.9689 | 0.8659 | -0.103 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | RANSOM 2 | 0.9749 | 0.8659 | -0.109 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | RANSOM 2 | 0.9689 | 0.8659 | -0.103 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | RANSOM 2 | 0.9749 | 0.8659 | -0.109 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | RANSOM 2 | 0.9689 | 0.8659 | -0.103 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | RANSOM 2 | 0.9749 | 0.8659 | -0.109 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | RANSOM 2 | 0.9689 | 0.8659 | -0.103 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | RANSOM 2 | 0.9749 | 0.8659 | -0.109 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | RANSOM 2 | 0.9689 | 0.8659 | -0.103 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | RANSOM 2 | 0.9749 | 0.8659 | -0.109 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | RANSOM 2 | 0.9689 | 0.8659 | -0.103 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | RANSOM 2 | 0.9749 | 0.8659 | -0.109 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | RANSOM 2 | 0.9689 | 0.8659 | -0.103 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | RANSOM 2 | 0.9749 | 0.8659 | -0.109 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | RANSOM 2 | 0.9689 | 0.8659 | -0.103 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | RANSOM 2 | 0.9749 | 0.8659 | -0.109 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | RANSOM 2 | 0.9689 | 0.8659 | -0.103 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | RANSOM 2 | 0.9749 | 0.8659 | -0.109 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | RANSOM 2 | 0.9689 | 0.8659 | -0.103 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | RANSOM 2 | 0.9749 | 0.8659 | -0.109 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | RANSOM 2 | 0.9689 | 0.8659 | -0.103 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | RANSOM 2 | 0.9749 | 0.8659 | -0.109 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | RANSOM 2 | 0.9689 | 0.8659 | -0.103 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | RANSOM 2 | 0.9749 | 0.8659 | -0.109 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | RANSOM 2 | 0.9689 | 0.8659 | -0.103 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | RANSOM 2 | 0.9749 | 0.8659 | -0.109 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | RANSOM 2 | 0.9689 | 0.8659 | -0.103 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | RANSOM 2 | 0.9749 | 0.8659 | -0.109 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | RANSOM 2 | 0.9689 | 0.8659 | -0.103 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | RANSOM 2 | 0.9749 | 0.8659 | -0.109 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | RANSOM 2 | 0.9689 | 0.8659 | -0.103 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | RANSOM 2 | 0.9749 | 0.8659 | -0.109 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | RANSOM 2 | 0.9689 | 0.8659 | -0.103 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | RANSOM 2 | 0.9749 | 0.8659 | -0.109 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | RANSOM 2 | 0.9689 | 0.8659 | -0.103 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | RANSOM 2 | 0.9749 | 0.8659 | -0.109 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | RANSOM 2 | 0.9689 | 0.8659 | -0.103 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | RANSOM 2 | 0.9749 | 0.8659 | -0.109 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | RANSOM 2 | 0.9689 | 0.8659 | -0.103 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | RANSOM 2 | 0.9749 | 0.8659 | -0.109 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | RANSOM 2 | 0.9689 | 0.8659 | -0.103 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | RANSOM 2 | 0.9749 | 0.8659 | -0.109 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | RANSOM 2 | 0.9689 | 0.8659 | -0.103 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | RANSOM 2 | 0.9749 | 0.8659 | -0.109 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | RANSOM 2 | 0.9689 | 0.8659 | -0.103 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | RANSOM 2 | 0.9749 | 0.8659 | -0.109 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | RANSOM 2 | 0.9689 | 0.8659 | -0.103 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | RANSOM 2 | 0.9749 | 0.8659 | -0.109 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | RANSOM 2 | 0.9689 | 0.8659 | -0.103 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | RANSOM 2 | 0.9749 | 0.8659 | -0.109 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | RANSOM 2 | 0.9689 | 0.8659 | -0.103 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | RANSOM 2 | 0.9749 | 0.8659 | -0.109 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | RANSOM 2 | 0.9689 | 0.8659 | -0.103 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | RANSOM 2 | 0.9749 | 0.8659 | -0.109 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | PILE 3 | 0.9644 | 0.866 | -0.0984 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | ELLIS 2 | 0.9727 | 0.866 | -0.1067 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | ELLIS 2 | 0.9781 | 0.866 | -0.1121 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | PILE 3 | 0.9644 | 0.866 | -0.0984 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | ELLIS 2 | 0.9727 | 0.866 | -0.1067 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | ELLIS 2 | 0.9781 | 0.866 | -0.1121 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | PILE 3 | 0.9644 | 0.866 | -0.0984 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | ELLIS 2 | 0.9727 | 0.866 | -0.1067 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | ELLIS 2 | 0.9781 | 0.866 | -0.1121 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | PILE 3 | 0.9644 | 0.866 | -0.0984 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | ELLIS 2 | 0.9727 | 0.866 | -0.1067 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | ELLIS 2 | 0.9781 | 0.866 | -0.1121 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | PILE 3 | 0.9644 | 0.866 | -0.0984 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | ELLIS 2 | 0.9727 | 0.866 | -0.1067 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | ELLIS 2 | 0.9781 | 0.866 | -0.1121 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | PILE 3 | 0.9644 | 0.866 | -0.0984 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | ELLIS 2 | 0.9727 | 0.866 | -0.1067 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | ELLIS 2 | 0.9781 | 0.866 | -0.1121 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | PILE 3 | 0.9644 | 0.866 | -0.0984 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | ELLIS 2 | 0.9727 | 0.866 | -0.1067 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | ELLIS 2 | 0.9781 | 0.866 | -0.1121 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | PILE 3 | 0.9644 | 0.866 | -0.0984 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | ELLIS 2 | 0.9727 | 0.866 | -0.1067 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | ELLIS 2 | 0.9781 | 0.866 | -0.1121 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | PILE 3 | 0.9644 | 0.866 | -0.0984 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | ELLIS 2 | 0.9727 | 0.866 | -0.1067 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | ELLIS 2 | 0.9781 | 0.866 | -0.1121 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | PILE 3 | 0.9644 | 0.866 | -0.0984 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | ELLIS 2 | 0.9727 | 0.866 | -0.1067 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | ELLIS 2 | 0.9781 | 0.866 | -0.1121 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | PILE 3 | 0.9644 | 0.866 | -0.0984 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | ELLIS 2 | 0.9727 | 0.866 | -0.1067 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | ELLIS 2 | 0.9781 | 0.866 | -0.1121 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | PILE 3 | 0.9644 | 0.866 | -0.0984 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | ELLIS 2 | 0.9727 | 0.866 | -0.1067 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | ELLIS 2 | 0.9781 | 0.866 | -0.1121 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | PILE 3 | 0.9644 | 0.866 | -0.0984 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | ELLIS 2 | 0.9727 | 0.866 | -0.1067 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | ELLIS 2 | 0.9781 | 0.866 | -0.1121 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | PILE 3 | 0.9644 | 0.866 | -0.0984 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | ELLIS 2 | 0.9727 | 0.866 | -0.1067 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | ELLIS 2 | 0.9781 | 0.866 | -0.1121 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | PILE 3 | 0.9644 | 0.866 | -0.0984 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | ELLIS 2 | 0.9727 | 0.866 | -0.1067 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | ELLIS 2 | 0.9781 | 0.866 | -0.1121 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | PILE 3 | 0.9644 | 0.866 | -0.0984 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | ELLIS 2 | 0.9727 | 0.866 | -0.1067 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | ELLIS 2 | 0.9781 | 0.866 | -0.1121 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | PILE 3 | 0.9644 | 0.866 | -0.0984 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | ELLIS 2 | 0.9727 | 0.866 | -0.1067 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | ELLIS 2 | 0.9781 | 0.866 | -0.1121 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | PILE 3 | 0.9644 | 0.866 | -0.0984 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | ELLIS 2 | 0.9727 | 0.866 | -0.1067 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | ELLIS 2 | 0.9781 | 0.866 | -0.1121 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | PILE 3 | 0.9644 | 0.866 | -0.0984 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | ELLIS 2 | 0.9727 | 0.866 | -0.1067 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | ELLIS 2 | 0.9781 | 0.866 | -0.1121 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | PILE 3 | 0.9644 | 0.866 | -0.0984 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | ELLIS 2 | 0.9727 | 0.866 | -0.1067 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | ELLIS 2 | 0.9781 | 0.866 | -0.1121 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | PILE 3 | 0.9644 | 0.866 | -0.0984 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | ELLIS 2 | 0.9727 | 0.866 | -0.1067 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | ELLIS 2 | 0.9781 | 0.866 | -0.1121 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | PILE 3 | 0.9644 | 0.866 | -0.0984 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | ELLIS 2 | 0.9727 | 0.866 | -0.1067 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | ELLIS 2 | 0.9781 | 0.866 | -0.1121 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | PILE 3 | 0.9644 | 0.866 | -0.0984 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | ELLIS 2 | 0.9727 | 0.866 | -0.1067 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | ELLIS 2 | 0.9781 | 0.866 | -0.1121 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | PILE 3 | 0.9644 | 0.866 | -0.0984 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | ELLIS 2 | 0.9727 | 0.866 | -0.1067 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | ELLIS 2 | 0.9781 | 0.866 | -0.1121 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | PILE 3 | 0.9644 | 0.866 | -0.0984 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | ELLIS 2 | 0.9727 | 0.866 | -0.1067 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | ELLIS 2 | 0.9781 | 0.866 | -0.1121 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | PILE 3 | 0.9644 | 0.866 | -0.0984 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | ELLIS 2 | 0.9727 | 0.866 | -0.1067 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | ELLIS 2 | 0.9781 | 0.866 | -0.1121 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | PILE 3 | 0.9644 | 0.866 | -0.0984 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | ELLIS 2 | 0.9727 | 0.866 | -0.1067 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | ELLIS 2 | 0.9781 | 0.866 | -0.1121 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | WTCLFTP3 | 0.9605 | 0.8663 | -0.0942 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | WTCLFTP3 | 0.9605 | 0.8663 | -0.0942 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | WTCLFTP3 | 0.9605 | 0.8663 | -0.0942 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | WTCLFTP3 | 0.9605 | 0.8663 | -0.0942 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | WTCLFTP3 | 0.9605 | 0.8663 | -0.0942 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | WTCLFTP3 | 0.9605 | 0.8663 | -0.0942 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | WTCLFTP3 | 0.9605 | 0.8663 | -0.0942 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | WTCLFTP3 | 0.9605 | 0.8663 | -0.0942 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | WTCLFTP3 | 0.9605 | 0.8663 | -0.0942 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | WTCLFTP3 | 0.9605 | 0.8663 | -0.0942 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | WTCLFTP3 | 0.9605 | 0.8663 | -0.0942 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | WTCLFTP3 | 0.9605 | 0.8663 | -0.0942 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | WTCLFTP3 | 0.9605 | 0.8663 | -0.0942 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | WTCLFTP3 | 0.9605 | 0.8663 | -0.0942 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | WTCLFTP3 | 0.9605 | 0.8663 | -0.0942 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | WTCLFTP3 | 0.9605 | 0.8663 | -0.0942 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | WTCLFTP3 | 0.9605 | 0.8663 | -0.0942 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | WTCLFTP3 | 0.9605 | 0.8663 | -0.0942 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | WTCLFTP3 | 0.9605 | 0.8663 | -0.0942 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | WTCLFTP3 | 0.9605 | 0.8663 | -0.0942 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | WTCLFTP3 | 0.9605 | 0.8663 | -0.0942 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | WTCLFTP3 | 0.9605 | 0.8663 | -0.0942 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | WTCLFTP3 | 0.9605 | 0.8663 | -0.0942 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | WTCLFTP3 | 0.9605 | 0.8663 | -0.0942 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | WTCLFTP3 | 0.9605 | 0.8663 | -0.0942 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | WTCLFTP3 | 0.9605 | 0.8663 | -0.0942 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | WTCLFTP3 | 0.9605 | 0.8663 | -0.0942 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | STFRAN 3 | 0.966 | 0.8665 | -0.0995 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | STFRAN 3 | 0.9702 | 0.8665 | -0.1037 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | STFRAN 3 | 0.966 | 0.8665 | -0.0995 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | STFRAN 3 | 0.9702 | 0.8665 | -0.1037 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | STFRAN 3 | 0.966 | 0.8665 | -0.0995 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | STFRAN 3 | 0.9702 | 0.8665 | -0.1037 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | STFRAN 3 | 0.966 | 0.8665 | -0.0995 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | STFRAN 3 | 0.9702 | 0.8665 | -0.1037 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | STFRAN 3 | 0.966 | 0.8665 | -0.0995 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | STFRAN 3 | 0.9702 | 0.8665 | -0.1037 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | STFRAN 3 | 0.966 | 0.8665 | -0.0995 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | STFRAN 3 | 0.9702 | 0.8665 | -0.1037 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | STFRAN 3 | 0.966 | 0.8665 | -0.0995 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | STFRAN 3 | 0.9702 | 0.8665 | -0.1037 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | STFRAN 3 | 0.966 | 0.8665 | -0.0995 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | STFRAN 3 | 0.9702 | 0.8665 | -0.1037 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | STFRAN 3 | 0.966 | 0.8665 | -0.0995 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | STFRAN 3 | 0.9702 | 0.8665 | -0.1037 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | STFRAN 3 | 0.966 | 0.8665 | -0.0995 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | STFRAN 3 | 0.9702 | 0.8665 | -0.1037 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | STFRAN 3 | 0.966 | 0.8665 | -0.0995 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | STFRAN 3 | 0.9702 | 0.8665 | -0.1037 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | STFRAN 3 | 0.966 | 0.8665 | -0.0995 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | STFRAN 3 | 0.9702 | 0.8665 | -0.1037 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | STFRAN 3 | 0.966 | 0.8665 | -0.0995 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | STFRAN 3 | 0.9702 | 0.8665 | -0.1037 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | STFRAN 3 | 0.966 | 0.8665 | -0.0995 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | STFRAN 3 | 0.9702 | 0.8665 | -0.1037 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | STFRAN 3 | 0.966 | 0.8665 | -0.0995 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | STFRAN 3 | 0.9702 | 0.8665 | -0.1037 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | STFRAN 3 | 0.966 | 0.8665 | -0.0995 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | STFRAN 3 | 0.9702 | 0.8665 | -0.1037 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | STFRAN 3 | 0.966 | 0.8665 | -0.0995 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | STFRAN 3 | 0.9702 | 0.8665 | -0.1037 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | STFRAN 3 | 0.966 | 0.8665 | -0.0995 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | STFRAN 3 | 0.9702 | 0.8665 | -0.1037 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | STFRAN 3 | 0.966 | 0.8665 | -0.0995 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | STFRAN 3 | 0.9702 | 0.8665 | -0.1037 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | STFRAN 3 | 0.966 | 0.8665 | -0.0995 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | STFRAN 3 | 0.9702 | 0.8665 | -0.1037 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | STFRAN 3 | 0.966 | 0.8665 | -0.0995 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | STFRAN 3 | 0.9702 | 0.8665 | -0.1037 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | STFRAN 3 | 0.966 | 0.8665 | -0.0995 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | STFRAN 3 | 0.9702 | 0.8665 | -0.1037 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | STFRAN 3 | 0.966 | 0.8665 | -0.0995 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | STFRAN 3 | 0.9702 | 0.8665 | -0.1037 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | STFRAN 3 | 0.966 | 0.8665 | -0.0995 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | STFRAN 3 | 0.9702 | 0.8665 | -0.1037 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | STFRAN 3 | 0.966 | 0.8665 | -0.0995 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | STFRAN 3 | 0.9702 | 0.8665 | -0.1037 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | STFRAN 3 | 0.966 | 0.8665 | -0.0995 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | STFRAN 3 | 0.9702 | 0.8665 | -0.1037 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | STFRAN 3 | 0.966 | 0.8665 | -0.0995 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | STFRAN 3 | 0.9702 | 0.8665 | -0.1037 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | PALMER3 | 0.9672 | 0.8667 | -0.1005 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | PALMER3 | 0.9672 | 0.8667 | -0.1005 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | PALMER3 | 0.9672 | 0.8667 | -0.1005 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | PALMER3 | 0.9672 | 0.8667 | -0.1005 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | PALMER3 | 0.9672 | 0.8667 | -0.1005 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | PALMER3 | 0.9672 | 0.8667 | -0.1005 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | PALMER3 | 0.9672 | 0.8667 | -0.1005 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | PALMER3 | 0.9672 | 0.8667 | -0.1005 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | PALMER3 | 0.9672 | 0.8667 | -0.1005 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | PALMER3 | 0.9672 | 0.8667 | -0.1005 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | PALMER3 | 0.9672 | 0.8667 | -0.1005 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | PALMER3 | 0.9672 | 0.8667 | -0.1005 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | PALMER3 | 0.9672 | 0.8667 | -0.1005 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | PALMER3 | 0.9672 | 0.8667 | -0.1005 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | PALMER3 | 0.9672 | 0.8667 | -0.1005 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | PALMER3 | 0.9672 | 0.8667 | -0.1005 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | PALMER3 | 0.9672 | 0.8667 | -0.1005 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | PALMER3 | 0.9672 | 0.8667 | -0.1005 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | PALMER3 | 0.9672 | 0.8667 | -0.1005 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | PALMER3 | 0.9672 | 0.8667 | -0.1005 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | PALMER3 | 0.9672 | 0.8667 | -0.1005 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | PALMER3 | 0.9672 | 0.8667 | -0.1005 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | PALMER3 | 0.9672 | 0.8667 | -0.1005 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | PALMER3 | 0.9672 | 0.8667 | -0.1005 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | PALMER3 | 0.9672 | 0.8667 | -0.1005 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | PALMER3 | 0.9672 | 0.8667 | -0.1005 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | PALMER3 | 0.9672 | 0.8667 | -0.1005 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | LAWNRID3 | 0.9858 | 0.8669 | -0.1189 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | LAWNRID3 | 0.9897 | 0.8669 | -0.1228 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | LAWNRID3 | 0.9858 | 0.8669 | -0.1189 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | LAWNRID3 | 0.9897 | 0.8669 | -0.1228 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | LAWNRID3 | 0.9858 | 0.8669 | -0.1189 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | LAWNRID3 | 0.9897 | 0.8669 | -0.1228 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | LAWNRID3 | 0.9858 | 0.8669 | -0.1189 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | LAWNRID3 | 0.9897 | 0.8669 | -0.1228 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | LAWNRID3 | 0.9858 | 0.8669 | -0.1189 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | LAWNRID3 | 0.9897 | 0.8669 | -0.1228 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | LAWNRID3 | 0.9858 | 0.8669 | -0.1189 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | LAWNRID3 | 0.9897 | 0.8669 | -0.1228 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | LAWNRID3 | 0.9858 | 0.8669 | -0.1189 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | LAWNRID3 | 0.9897 | 0.8669 | -0.1228 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | LAWNRID3 | 0.9858 | 0.8669 | -0.1189 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | LAWNRID3 | 0.9897 | 0.8669 | -0.1228 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | LAWNRID3 | 0.9858 | 0.8669 | -0.1189 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | LAWNRID3 | 0.9897 | 0.8669 | -0.1228 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | LAWNRID3 | 0.9858 | 0.8669 | -0.1189 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | LAWNRID3 | 0.9897 | 0.8669 | -0.1228 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | LAWNRID3 | 0.9858 | 0.8669 | -0.1189 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | LAWNRID3 | 0.9897 | 0.8669 | -0.1228 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | LAWNRID3 | 0.9858 | 0.8669 | -0.1189 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | LAWNRID3 | 0.9897 | 0.8669 | -0.1228 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | LAWNRID3 | 0.9858 | 0.8669 | -0.1189 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | LAWNRID3 | 0.9897 | 0.8669 | -0.1228 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | LAWNRID3 | 0.9858 | 0.8669 | -0.1189 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | LAWNRID3 | 0.9897 | 0.8669 | -0.1228 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | LAWNRID3 | 0.9858 | 0.8669 | -0.1189 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | LAWNRID3 | 0.9897 | 0.8669 | -0.1228 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | LAWNRID3 | 0.9858 | 0.8669 | -0.1189 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | LAWNRID3 | 0.9897 | 0.8669 | -0.1228 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | LAWNRID3 | 0.9858 | 0.8669 | -0.1189 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | LAWNRID3 | 0.9897 | 0.8669 | -0.1228 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | LAWNRID3 | 0.9858 | 0.8669 | -0.1189 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | LAWNRID3 | 0.9897 | 0.8669 | -0.1228 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | LAWNRID3 | 0.9858 | 0.8669 | -0.1189 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | LAWNRID3 | 0.9897 | 0.8669 | -0.1228 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | LAWNRID3 | 0.9858 | 0.8669 | -0.1189 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | LAWNRID3 | 0.9897 | 0.8669 | -0.1228 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | LAWNRID3 | 0.9858 | 0.8669 | -0.1189 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | LAWNRID3 | 0.9897 | 0.8669 | -0.1228 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | LAWNRID3 | 0.9858 | 0.8669 | -0.1189 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | LAWNRID3 | 0.9897 | 0.8669 | -0.1228 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | LAWNRID3 | 0.9858 | 0.8669 | -0.1189 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | LAWNRID3 | 0.9897 | 0.8669 | -0.1228 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | LAWNRID3 | 0.9858 | 0.8669 | -0.1189 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | LAWNRID3 | 0.9897 | 0.8669 | -0.1228 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | LAWNRID3 | 0.9858 | 0.8669 | -0.1189 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | LAWNRID3 | 0.9897 | 0.8669 | -0.1228 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | LAWNRID3 | 0.9858 | 0.8669 | -0.1189 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | LAWNRID3 | 0.9897 | 0.8669 | -0.1228 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | LAWNRID3 | 0.9858 | 0.8669 | -0.1189 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | LAWNRID3 | 0.9897 | 0.8669 | -0.1228 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | BEELER 3 | 0.9645 | 0.868 | -0.0965 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | BEELER 3 | 0.9729 | 0.868 | -0.1049 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | BEELER 3 | 0.9645 | 0.868 | -0.0965 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | BEELER 3 | 0.9729 | 0.868 | -0.1049 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | BEELER 3 | 0.9645 | 0.868 | -0.0965 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | BEELER 3 | 0.9729 | 0.868 | -0.1049 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | BEELER 3 | 0.9645 | 0.868 | -0.0965 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | BEELER 3 | 0.9729 | 0.868 | -0.1049 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | BEELER 3 | 0.9645 | 0.868 | -0.0965 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | BEELER 3 | 0.9729 | 0.868 | -0.1049 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | BEELER 3 | 0.9645 | 0.868 | -0.0965 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | BEELER 3 | 0.9729 | 0.868 | -0.1049 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | BEELER 3 | 0.9645 | 0.868 | -0.0965 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | BEELER 3 | 0.9729 | 0.868 | -0.1049 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | BEELER 3 | 0.9645 | 0.868 | -0.0965 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | BEELER 3 | 0.9729 | 0.868 | -0.1049 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | BEELER 3 | 0.9645 | 0.868 | -0.0965 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | BEELER 3 | 0.9729 | 0.868 | -0.1049 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | BEELER 3 | 0.9645 | 0.868 | -0.0965 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | BEELER 3 | 0.9729 | 0.868 | -0.1049 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | BEELER 3 | 0.9645 | 0.868 | -0.0965 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | BEELER 3 | 0.9729 | 0.868 | -0.1049 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | BEELER 3 | 0.9645 | 0.868 | -0.0965 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | BEELER 3 | 0.9729 | 0.868 | -0.1049 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | BEELER 3 | 0.9645 | 0.868 | -0.0965 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | BEELER 3 | 0.9729 | 0.868 | -0.1049 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | BEELER 3 | 0.9645 | 0.868 | -0.0965 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | BEELER 3 | 0.9729 | 0.868 | -0.1049 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | BEELER 3 | 0.9645 | 0.868 | -0.0965 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | BEELER 3 | 0.9729 | 0.868 | -0.1049 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | BEELER 3 | 0.9645 | 0.868 | -0.0965 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | BEELER 3 | 0.9729 | 0.868 | -0.1049 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | BEELER 3 | 0.9645 | 0.868 | -0.0965 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | BEELER 3 | 0.9729 | 0.868 | -0.1049 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | BEELER 3 | 0.9645 | 0.868 | -0.0965 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | BEELER 3 | 0.9729 | 0.868 | -0.1049 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | BEELER 3 | 0.9645 | 0.868 | -0.0965 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | BEELER 3 | 0.9729 | 0.868 | -0.1049 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | BEELER 3 | 0.9645 | 0.868 | -0.0965 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | BEELER 3 | 0.9729 | 0.868 | -0.1049 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | BEELER 3 | 0.9645 | 0.868 | -0.0965 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | BEELER 3 | 0.9729 | 0.868 | -0.1049 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | BEELER 3 | 0.9645 | 0.868 | -0.0965 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | BEELER 3 | 0.9729 | 0.868 | -0.1049 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | BEELER 3 | 0.9645 | 0.868 | -0.0965 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | BEELER 3 | 0.9729 | 0.868 | -0.1049 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | BEELER 3 | 0.9645 | 0.868 | -0.0965 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | BEELER 3 | 0.9729 | 0.868 | -0.1049 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | BEELER 3 | 0.9645 | 0.868 | -0.0965 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | BEELER 3 | 0.9729 | 0.868 | -0.1049 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | BEELER 3 | 0.9645 | 0.868 | -0.0965 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | BEELER 3 | 0.9729 | 0.868 | -0.1049 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | BEELER 3 | 0.9645 | 0.868 | -0.0965 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | BEELER 3 | 0.9729 | 0.868 | -0.1049 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | RULETON3 | 0.9909 | 0.8682 | -0.1227 |  | 0.9 | 1.05 | 0.05095 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | RULETON3 | 0.9909 | 0.8682 | -0.1227 |  | 0.9 | 1.05 | 0.04905 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | RULETON3 | 0.9909 | 0.8682 | -0.1227 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | RULETON3 | 0.9909 | 0.8682 | -0.1227 |  | 0.9 | 1.05 | 0.04262 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | RULETON3 | 0.9909 | 0.8682 | -0.1227 |  | 0.9 | 1.05 | 0.0627 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | RULETON3 | 0.9909 | 0.8682 | -0.1227 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | RULETON3 | 0.9909 | 0.8682 | -0.1227 |  | 0.9 | 1.05 | 0.05043 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | RULETON3 | 0.9909 | 0.8682 | -0.1227 |  | 0.9 | 1.05 | 0.05292 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | RULETON3 | 0.9909 | 0.8682 | -0.1227 |  | 0.9 | 1.05 | 0.0444 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | RULETON3 | 0.9909 | 0.8682 | -0.1227 |  | 0.9 | 1.05 | 0.04788 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | RULETON3 | 0.9909 | 0.8682 | -0.1227 |  | 0.9 | 1.05 | 0.05824 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | RULETON3 | 0.9909 | 0.8682 | -0.1227 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | RULETON3 | 0.9909 | 0.8682 | -0.1227 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | RULETON3 | 0.9909 | 0.8682 | -0.1227 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | RULETON3 | 0.9909 | 0.8682 | -0.1227 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | RULETON3 | 0.9909 | 0.8682 | -0.1227 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | RULETON3 | 0.9909 | 0.8682 | -0.1227 |  | 0.9 | 1.05 | 0.04773 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | RULETON3 | 0.9909 | 0.8682 | -0.1227 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | RULETON3 | 0.9909 | 0.8682 | -0.1227 |  | 0.9 | 1.05 | 0.0348 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | RULETON3 | 0.9909 | 0.8682 | -0.1227 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | RULETON3 | 0.9909 | 0.8682 | -0.1227 |  | 0.9 | 1.05 | 0.04996 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | RULETON3 | 0.9909 | 0.8682 | -0.1227 |  | 0.9 | 1.05 | 0.04835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | RULETON3 | 0.9909 | 0.8682 | -0.1227 |  | 0.9 | 1.05 | 0.05448 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | RULETON3 | 0.9909 | 0.8682 | -0.1227 |  | 0.9 | 1.05 | 0.05382 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | RULETON3 | 0.9909 | 0.8682 | -0.1227 |  | 0.9 | 1.05 | 0.03774 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | RULETON3 | 0.9909 | 0.8682 | -0.1227 |  | 0.9 | 1.05 | 0.04948 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | RULETON3 | 0.9909 | 0.8682 | -0.1227 |  | 0.9 | 1.05 | 0.04054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | RANSOM 3 | 0.9709 | 0.8684 | -0.1025 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | RANSOM 3 | 0.9768 | 0.8684 | -0.1084 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | RANSOM 3 | 0.9709 | 0.8684 | -0.1025 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | RANSOM 3 | 0.9768 | 0.8684 | -0.1084 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | RANSOM 3 | 0.9709 | 0.8684 | -0.1025 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | RANSOM 3 | 0.9768 | 0.8684 | -0.1084 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | RANSOM 3 | 0.9709 | 0.8684 | -0.1025 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | RANSOM 3 | 0.9768 | 0.8684 | -0.1084 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | RANSOM 3 | 0.9709 | 0.8684 | -0.1025 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | RANSOM 3 | 0.9768 | 0.8684 | -0.1084 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | RANSOM 3 | 0.9709 | 0.8684 | -0.1025 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | RANSOM 3 | 0.9768 | 0.8684 | -0.1084 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | RANSOM 3 | 0.9709 | 0.8684 | -0.1025 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | RANSOM 3 | 0.9768 | 0.8684 | -0.1084 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | RANSOM 3 | 0.9709 | 0.8684 | -0.1025 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | RANSOM 3 | 0.9768 | 0.8684 | -0.1084 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | RANSOM 3 | 0.9709 | 0.8684 | -0.1025 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | RANSOM 3 | 0.9768 | 0.8684 | -0.1084 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | RANSOM 3 | 0.9709 | 0.8684 | -0.1025 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | RANSOM 3 | 0.9768 | 0.8684 | -0.1084 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | RANSOM 3 | 0.9709 | 0.8684 | -0.1025 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | RANSOM 3 | 0.9768 | 0.8684 | -0.1084 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | RANSOM 3 | 0.9709 | 0.8684 | -0.1025 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | RANSOM 3 | 0.9768 | 0.8684 | -0.1084 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | RANSOM 3 | 0.9709 | 0.8684 | -0.1025 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | RANSOM 3 | 0.9768 | 0.8684 | -0.1084 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | RANSOM 3 | 0.9709 | 0.8684 | -0.1025 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | RANSOM 3 | 0.9768 | 0.8684 | -0.1084 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | RANSOM 3 | 0.9709 | 0.8684 | -0.1025 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | RANSOM 3 | 0.9768 | 0.8684 | -0.1084 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | RANSOM 3 | 0.9709 | 0.8684 | -0.1025 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | RANSOM 3 | 0.9768 | 0.8684 | -0.1084 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | RANSOM 3 | 0.9709 | 0.8684 | -0.1025 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | RANSOM 3 | 0.9768 | 0.8684 | -0.1084 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | RANSOM 3 | 0.9709 | 0.8684 | -0.1025 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | RANSOM 3 | 0.9768 | 0.8684 | -0.1084 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | RANSOM 3 | 0.9709 | 0.8684 | -0.1025 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | RANSOM 3 | 0.9768 | 0.8684 | -0.1084 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | RANSOM 3 | 0.9709 | 0.8684 | -0.1025 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | RANSOM 3 | 0.9768 | 0.8684 | -0.1084 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | RANSOM 3 | 0.9709 | 0.8684 | -0.1025 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | RANSOM 3 | 0.9768 | 0.8684 | -0.1084 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | RANSOM 3 | 0.9709 | 0.8684 | -0.1025 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | RANSOM 3 | 0.9768 | 0.8684 | -0.1084 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | RANSOM 3 | 0.9709 | 0.8684 | -0.1025 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | RANSOM 3 | 0.9768 | 0.8684 | -0.1084 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | RANSOM 3 | 0.9709 | 0.8684 | -0.1025 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | RANSOM 3 | 0.9768 | 0.8684 | -0.1084 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | RANSOM 3 | 0.9709 | 0.8684 | -0.1025 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | RANSOM 3 | 0.9768 | 0.8684 | -0.1084 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | RANSOM 3 | 0.9709 | 0.8684 | -0.1025 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | RANSOM 3 | 0.9768 | 0.8684 | -0.1084 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | RANSOM 3 | 0.9709 | 0.8684 | -0.1025 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | RANSOM 3 | 0.9768 | 0.8684 | -0.1084 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | GOODCTY3 | 0.9736 | 0.8686 | -0.105 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | GOODCTY3 | 0.978 | 0.8686 | -0.1094 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | GOODCTY3 | 0.9736 | 0.8686 | -0.105 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | GOODCTY3 | 0.978 | 0.8686 | -0.1094 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | GOODCTY3 | 0.9736 | 0.8686 | -0.105 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | GOODCTY3 | 0.978 | 0.8686 | -0.1094 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | GOODCTY3 | 0.9736 | 0.8686 | -0.105 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | GOODCTY3 | 0.978 | 0.8686 | -0.1094 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | GOODCTY3 | 0.9736 | 0.8686 | -0.105 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | GOODCTY3 | 0.978 | 0.8686 | -0.1094 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | GOODCTY3 | 0.9736 | 0.8686 | -0.105 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | GOODCTY3 | 0.978 | 0.8686 | -0.1094 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | GOODCTY3 | 0.9736 | 0.8686 | -0.105 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | GOODCTY3 | 0.978 | 0.8686 | -0.1094 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | GOODCTY3 | 0.9736 | 0.8686 | -0.105 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | GOODCTY3 | 0.978 | 0.8686 | -0.1094 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | GOODCTY3 | 0.9736 | 0.8686 | -0.105 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | GOODCTY3 | 0.978 | 0.8686 | -0.1094 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | GOODCTY3 | 0.9736 | 0.8686 | -0.105 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | GOODCTY3 | 0.978 | 0.8686 | -0.1094 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | GOODCTY3 | 0.9736 | 0.8686 | -0.105 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | GOODCTY3 | 0.978 | 0.8686 | -0.1094 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | GOODCTY3 | 0.9736 | 0.8686 | -0.105 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | GOODCTY3 | 0.978 | 0.8686 | -0.1094 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | GOODCTY3 | 0.9736 | 0.8686 | -0.105 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | GOODCTY3 | 0.978 | 0.8686 | -0.1094 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | GOODCTY3 | 0.9736 | 0.8686 | -0.105 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | GOODCTY3 | 0.978 | 0.8686 | -0.1094 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | GOODCTY3 | 0.9736 | 0.8686 | -0.105 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | GOODCTY3 | 0.978 | 0.8686 | -0.1094 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | GOODCTY3 | 0.9736 | 0.8686 | -0.105 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | GOODCTY3 | 0.978 | 0.8686 | -0.1094 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | GOODCTY3 | 0.9736 | 0.8686 | -0.105 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | GOODCTY3 | 0.978 | 0.8686 | -0.1094 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | GOODCTY3 | 0.9736 | 0.8686 | -0.105 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | GOODCTY3 | 0.978 | 0.8686 | -0.1094 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | GOODCTY3 | 0.9736 | 0.8686 | -0.105 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | GOODCTY3 | 0.978 | 0.8686 | -0.1094 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | GOODCTY3 | 0.9736 | 0.8686 | -0.105 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | GOODCTY3 | 0.978 | 0.8686 | -0.1094 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | GOODCTY3 | 0.9736 | 0.8686 | -0.105 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | GOODCTY3 | 0.978 | 0.8686 | -0.1094 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | GOODCTY3 | 0.9736 | 0.8686 | -0.105 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | GOODCTY3 | 0.978 | 0.8686 | -0.1094 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | GOODCTY3 | 0.9736 | 0.8686 | -0.105 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | GOODCTY3 | 0.978 | 0.8686 | -0.1094 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | GOODCTY3 | 0.9736 | 0.8686 | -0.105 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | GOODCTY3 | 0.978 | 0.8686 | -0.1094 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | GOODCTY3 | 0.9736 | 0.8686 | -0.105 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | GOODCTY3 | 0.978 | 0.8686 | -0.1094 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | GOODCTY3 | 0.9736 | 0.8686 | -0.105 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | GOODCTY3 | 0.978 | 0.8686 | -0.1094 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | GOODCTY3 | 0.9736 | 0.8686 | -0.105 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | GOODCTY3 | 0.978 | 0.8686 | -0.1094 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | NESSCTY3 | 0.9682 | 0.8689 | -0.0993 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | NESSCTY3 | 0.9748 | 0.8689 | -0.1059 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | NESSCTY3 | 0.9682 | 0.8689 | -0.0993 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | NESSCTY3 | 0.9748 | 0.8689 | -0.1059 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | NESSCTY3 | 0.9682 | 0.8689 | -0.0993 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | NESSCTY3 | 0.9748 | 0.8689 | -0.1059 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | NESSCTY3 | 0.9682 | 0.8689 | -0.0993 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | NESSCTY3 | 0.9748 | 0.8689 | -0.1059 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | NESSCTY3 | 0.9682 | 0.8689 | -0.0993 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | NESSCTY3 | 0.9748 | 0.8689 | -0.1059 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | NESSCTY3 | 0.9682 | 0.8689 | -0.0993 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | NESSCTY3 | 0.9748 | 0.8689 | -0.1059 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | NESSCTY3 | 0.9682 | 0.8689 | -0.0993 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | NESSCTY3 | 0.9748 | 0.8689 | -0.1059 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | NESSCTY3 | 0.9682 | 0.8689 | -0.0993 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | NESSCTY3 | 0.9748 | 0.8689 | -0.1059 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | NESSCTY3 | 0.9682 | 0.8689 | -0.0993 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | NESSCTY3 | 0.9748 | 0.8689 | -0.1059 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | NESSCTY3 | 0.9682 | 0.8689 | -0.0993 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | NESSCTY3 | 0.9748 | 0.8689 | -0.1059 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | NESSCTY3 | 0.9682 | 0.8689 | -0.0993 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | NESSCTY3 | 0.9748 | 0.8689 | -0.1059 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | NESSCTY3 | 0.9682 | 0.8689 | -0.0993 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | NESSCTY3 | 0.9748 | 0.8689 | -0.1059 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | NESSCTY3 | 0.9682 | 0.8689 | -0.0993 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | NESSCTY3 | 0.9748 | 0.8689 | -0.1059 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | NESSCTY3 | 0.9682 | 0.8689 | -0.0993 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | NESSCTY3 | 0.9748 | 0.8689 | -0.1059 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | NESSCTY3 | 0.9682 | 0.8689 | -0.0993 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | NESSCTY3 | 0.9748 | 0.8689 | -0.1059 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | NESSCTY3 | 0.9682 | 0.8689 | -0.0993 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | NESSCTY3 | 0.9748 | 0.8689 | -0.1059 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | NESSCTY3 | 0.9682 | 0.8689 | -0.0993 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | NESSCTY3 | 0.9748 | 0.8689 | -0.1059 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | NESSCTY3 | 0.9682 | 0.8689 | -0.0993 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | NESSCTY3 | 0.9748 | 0.8689 | -0.1059 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | NESSCTY3 | 0.9682 | 0.8689 | -0.0993 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | NESSCTY3 | 0.9748 | 0.8689 | -0.1059 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | NESSCTY3 | 0.9682 | 0.8689 | -0.0993 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | NESSCTY3 | 0.9748 | 0.8689 | -0.1059 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | NESSCTY3 | 0.9682 | 0.8689 | -0.0993 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | NESSCTY3 | 0.9748 | 0.8689 | -0.1059 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | NESSCTY3 | 0.9682 | 0.8689 | -0.0993 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | NESSCTY3 | 0.9748 | 0.8689 | -0.1059 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | NESSCTY3 | 0.9682 | 0.8689 | -0.0993 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | NESSCTY3 | 0.9748 | 0.8689 | -0.1059 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | NESSCTY3 | 0.9682 | 0.8689 | -0.0993 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | NESSCTY3 | 0.9748 | 0.8689 | -0.1059 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | NESSCTY3 | 0.9682 | 0.8689 | -0.0993 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | NESSCTY3 | 0.9748 | 0.8689 | -0.1059 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | NESSCTY3 | 0.9682 | 0.8689 | -0.0993 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | NESSCTY3 | 0.9748 | 0.8689 | -0.1059 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | NESSCTY3 | 0.9682 | 0.8689 | -0.0993 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | NESSCTY3 | 0.9748 | 0.8689 | -0.1059 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | NESCTY 3 | 0.9682 | 0.869 | -0.0992 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | NESCTY 3 | 0.9748 | 0.869 | -0.1058 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | NESCTY 3 | 0.9682 | 0.869 | -0.0992 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | NESCTY 3 | 0.9748 | 0.869 | -0.1058 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | NESCTY 3 | 0.9682 | 0.869 | -0.0992 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | NESCTY 3 | 0.9748 | 0.869 | -0.1058 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | NESCTY 3 | 0.9682 | 0.869 | -0.0992 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | NESCTY 3 | 0.9748 | 0.869 | -0.1058 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | NESCTY 3 | 0.9682 | 0.869 | -0.0992 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | NESCTY 3 | 0.9748 | 0.869 | -0.1058 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | NESCTY 3 | 0.9682 | 0.869 | -0.0992 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | NESCTY 3 | 0.9748 | 0.869 | -0.1058 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | NESCTY 3 | 0.9682 | 0.869 | -0.0992 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | NESCTY 3 | 0.9748 | 0.869 | -0.1058 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | NESCTY 3 | 0.9682 | 0.869 | -0.0992 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | NESCTY 3 | 0.9748 | 0.869 | -0.1058 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | NESCTY 3 | 0.9682 | 0.869 | -0.0992 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | NESCTY 3 | 0.9748 | 0.869 | -0.1058 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | NESCTY 3 | 0.9682 | 0.869 | -0.0992 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | NESCTY 3 | 0.9748 | 0.869 | -0.1058 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | NESCTY 3 | 0.9682 | 0.869 | -0.0992 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | NESCTY 3 | 0.9748 | 0.869 | -0.1058 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | NESCTY 3 | 0.9682 | 0.869 | -0.0992 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | NESCTY 3 | 0.9748 | 0.869 | -0.1058 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | NESCTY 3 | 0.9682 | 0.869 | -0.0992 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | NESCTY 3 | 0.9748 | 0.869 | -0.1058 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | NESCTY 3 | 0.9682 | 0.869 | -0.0992 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | NESCTY 3 | 0.9748 | 0.869 | -0.1058 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | NESCTY 3 | 0.9682 | 0.869 | -0.0992 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | NESCTY 3 | 0.9748 | 0.869 | -0.1058 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | NESCTY 3 | 0.9682 | 0.869 | -0.0992 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | NESCTY 3 | 0.9748 | 0.869 | -0.1058 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | NESCTY 3 | 0.9682 | 0.869 | -0.0992 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | NESCTY 3 | 0.9748 | 0.869 | -0.1058 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | NESCTY 3 | 0.9682 | 0.869 | -0.0992 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | NESCTY 3 | 0.9748 | 0.869 | -0.1058 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | NESCTY 3 | 0.9682 | 0.869 | -0.0992 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | NESCTY 3 | 0.9748 | 0.869 | -0.1058 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | NESCTY 3 | 0.9682 | 0.869 | -0.0992 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | NESCTY 3 | 0.9748 | 0.869 | -0.1058 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | NESCTY 3 | 0.9682 | 0.869 | -0.0992 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | NESCTY 3 | 0.9748 | 0.869 | -0.1058 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | NESCTY 3 | 0.9682 | 0.869 | -0.0992 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | NESCTY 3 | 0.9748 | 0.869 | -0.1058 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | NESCTY 3 | 0.9682 | 0.869 | -0.0992 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | NESCTY 3 | 0.9748 | 0.869 | -0.1058 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | NESCTY 3 | 0.9682 | 0.869 | -0.0992 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | NESCTY 3 | 0.9748 | 0.869 | -0.1058 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | NESCTY 3 | 0.9682 | 0.869 | -0.0992 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | NESCTY 3 | 0.9748 | 0.869 | -0.1058 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | NESCTY 3 | 0.9682 | 0.869 | -0.0992 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | NESCTY 3 | 0.9748 | 0.869 | -0.1058 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | NESCTY 3 | 0.9682 | 0.869 | -0.0992 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | NESCTY 3 | 0.9748 | 0.869 | -0.1058 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | CSTFRAN3 | 0.9659 | 0.8694 | -0.0965 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | CSTFRAN3 | 0.9659 | 0.8694 | -0.0965 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | CSTFRAN3 | 0.9659 | 0.8694 | -0.0965 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | CSTFRAN3 | 0.9659 | 0.8694 | -0.0965 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | CSTFRAN3 | 0.9659 | 0.8694 | -0.0965 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | CSTFRAN3 | 0.9659 | 0.8694 | -0.0965 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | CSTFRAN3 | 0.9659 | 0.8694 | -0.0965 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | CSTFRAN3 | 0.9659 | 0.8694 | -0.0965 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | CSTFRAN3 | 0.9659 | 0.8694 | -0.0965 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | CSTFRAN3 | 0.9659 | 0.8694 | -0.0965 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | CSTFRAN3 | 0.9659 | 0.8694 | -0.0965 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | CSTFRAN3 | 0.9659 | 0.8694 | -0.0965 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | CSTFRAN3 | 0.9659 | 0.8694 | -0.0965 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | CSTFRAN3 | 0.9659 | 0.8694 | -0.0965 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | CSTFRAN3 | 0.9659 | 0.8694 | -0.0965 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | CSTFRAN3 | 0.9659 | 0.8694 | -0.0965 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | CSTFRAN3 | 0.9659 | 0.8694 | -0.0965 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | CSTFRAN3 | 0.9659 | 0.8694 | -0.0965 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | CSTFRAN3 | 0.9659 | 0.8694 | -0.0965 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | CSTFRAN3 | 0.9659 | 0.8694 | -0.0965 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | CSTFRAN3 | 0.9659 | 0.8694 | -0.0965 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | CSTFRAN3 | 0.9659 | 0.8694 | -0.0965 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | CSTFRAN3 | 0.9659 | 0.8694 | -0.0965 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | CSTFRAN3 | 0.9659 | 0.8694 | -0.0965 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | CSTFRAN3 | 0.9659 | 0.8694 | -0.0965 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | CSTFRAN3 | 0.9659 | 0.8694 | -0.0965 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | CSTFRAN3 | 0.9659 | 0.8694 | -0.0965 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | STFRANT3 | 0.9661 | 0.8695 | -0.0966 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | STFRANT3 | 0.9661 | 0.8695 | -0.0966 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | STFRANT3 | 0.9661 | 0.8695 | -0.0966 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | STFRANT3 | 0.9661 | 0.8695 | -0.0966 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | STFRANT3 | 0.9661 | 0.8695 | -0.0966 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | STFRANT3 | 0.9661 | 0.8695 | -0.0966 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | STFRANT3 | 0.9661 | 0.8695 | -0.0966 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | STFRANT3 | 0.9661 | 0.8695 | -0.0966 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | STFRANT3 | 0.9661 | 0.8695 | -0.0966 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | STFRANT3 | 0.9661 | 0.8695 | -0.0966 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | STFRANT3 | 0.9661 | 0.8695 | -0.0966 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | STFRANT3 | 0.9661 | 0.8695 | -0.0966 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | STFRANT3 | 0.9661 | 0.8695 | -0.0966 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | STFRANT3 | 0.9661 | 0.8695 | -0.0966 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | STFRANT3 | 0.9661 | 0.8695 | -0.0966 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | STFRANT3 | 0.9661 | 0.8695 | -0.0966 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | STFRANT3 | 0.9661 | 0.8695 | -0.0966 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | STFRANT3 | 0.9661 | 0.8695 | -0.0966 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | STFRANT3 | 0.9661 | 0.8695 | -0.0966 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | STFRANT3 | 0.9661 | 0.8695 | -0.0966 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | STFRANT3 | 0.9661 | 0.8695 | -0.0966 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | STFRANT3 | 0.9661 | 0.8695 | -0.0966 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | STFRANT3 | 0.9661 | 0.8695 | -0.0966 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | STFRANT3 | 0.9661 | 0.8695 | -0.0966 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | STFRANT3 | 0.9661 | 0.8695 | -0.0966 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | STFRANT3 | 0.9661 | 0.8695 | -0.0966 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | STFRANT3 | 0.9661 | 0.8695 | -0.0966 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | RANSOM 2 | 0.9689 | 0.8697 | -0.0992 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | RANSOM 2 | 0.9689 | 0.8697 | -0.0992 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | RANSOM 2 | 0.9689 | 0.8697 | -0.0992 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | RANSOM 2 | 0.9689 | 0.8697 | -0.0992 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | RANSOM 2 | 0.9689 | 0.8697 | -0.0992 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | RANSOM 2 | 0.9689 | 0.8697 | -0.0992 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | RANSOM 2 | 0.9689 | 0.8697 | -0.0992 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | RANSOM 2 | 0.9689 | 0.8697 | -0.0992 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | RANSOM 2 | 0.9689 | 0.8697 | -0.0992 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | RANSOM 2 | 0.9689 | 0.8697 | -0.0992 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | RANSOM 2 | 0.9689 | 0.8697 | -0.0992 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | RANSOM 2 | 0.9689 | 0.8697 | -0.0992 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | RANSOM 2 | 0.9689 | 0.8697 | -0.0992 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | RANSOM 2 | 0.9689 | 0.8697 | -0.0992 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | RANSOM 2 | 0.9689 | 0.8697 | -0.0992 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | RANSOM 2 | 0.9689 | 0.8697 | -0.0992 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | RANSOM 2 | 0.9689 | 0.8697 | -0.0992 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | RANSOM 2 | 0.9689 | 0.8697 | -0.0992 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | RANSOM 2 | 0.9689 | 0.8697 | -0.0992 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | RANSOM 2 | 0.9689 | 0.8697 | -0.0992 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | RANSOM 2 | 0.9689 | 0.8697 | -0.0992 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | RANSOM 2 | 0.9689 | 0.8697 | -0.0992 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | RANSOM 2 | 0.9689 | 0.8697 | -0.0992 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | RANSOM 2 | 0.9689 | 0.8697 | -0.0992 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | RANSOM 2 | 0.9689 | 0.8697 | -0.0992 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | RANSOM 2 | 0.9689 | 0.8697 | -0.0992 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | RANSOM 2 | 0.9689 | 0.8697 | -0.0992 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | ARNOLD3 | 0.972 | 0.8699 | -0.1021 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | ARNOLD3 | 0.9777 | 0.8699 | -0.1078 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | TRIBUNE3 | 0.97 | 0.8699 | -0.1001 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | ARNOLD3 | 0.972 | 0.8699 | -0.1021 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | ARNOLD3 | 0.9777 | 0.8699 | -0.1078 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | TRIBUNE3 | 0.97 | 0.8699 | -0.1001 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | ARNOLD3 | 0.972 | 0.8699 | -0.1021 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | ARNOLD3 | 0.9777 | 0.8699 | -0.1078 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | TRIBUNE3 | 0.97 | 0.8699 | -0.1001 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | ARNOLD3 | 0.972 | 0.8699 | -0.1021 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | ARNOLD3 | 0.9777 | 0.8699 | -0.1078 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | TRIBUNE3 | 0.97 | 0.8699 | -0.1001 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | ARNOLD3 | 0.972 | 0.8699 | -0.1021 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | ARNOLD3 | 0.9777 | 0.8699 | -0.1078 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | TRIBUNE3 | 0.97 | 0.8699 | -0.1001 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | ARNOLD3 | 0.972 | 0.8699 | -0.1021 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | ARNOLD3 | 0.9777 | 0.8699 | -0.1078 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | TRIBUNE3 | 0.97 | 0.8699 | -0.1001 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | ARNOLD3 | 0.972 | 0.8699 | -0.1021 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | ARNOLD3 | 0.9777 | 0.8699 | -0.1078 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | TRIBUNE3 | 0.97 | 0.8699 | -0.1001 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | ARNOLD3 | 0.972 | 0.8699 | -0.1021 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | ARNOLD3 | 0.9777 | 0.8699 | -0.1078 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | TRIBUNE3 | 0.97 | 0.8699 | -0.1001 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | ARNOLD3 | 0.972 | 0.8699 | -0.1021 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | ARNOLD3 | 0.9777 | 0.8699 | -0.1078 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | TRIBUNE3 | 0.97 | 0.8699 | -0.1001 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | ARNOLD3 | 0.972 | 0.8699 | -0.1021 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | ARNOLD3 | 0.9777 | 0.8699 | -0.1078 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | TRIBUNE3 | 0.97 | 0.8699 | -0.1001 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | ARNOLD3 | 0.972 | 0.8699 | -0.1021 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | ARNOLD3 | 0.9777 | 0.8699 | -0.1078 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | TRIBUNE3 | 0.97 | 0.8699 | -0.1001 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | ARNOLD3 | 0.972 | 0.8699 | -0.1021 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | ARNOLD3 | 0.9777 | 0.8699 | -0.1078 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | TRIBUNE3 | 0.97 | 0.8699 | -0.1001 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | ARNOLD3 | 0.972 | 0.8699 | -0.1021 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | ARNOLD3 | 0.9777 | 0.8699 | -0.1078 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | TRIBUNE3 | 0.97 | 0.8699 | -0.1001 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | ARNOLD3 | 0.972 | 0.8699 | -0.1021 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | ARNOLD3 | 0.9777 | 0.8699 | -0.1078 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | TRIBUNE3 | 0.97 | 0.8699 | -0.1001 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | ARNOLD3 | 0.972 | 0.8699 | -0.1021 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | ARNOLD3 | 0.9777 | 0.8699 | -0.1078 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | TRIBUNE3 | 0.97 | 0.8699 | -0.1001 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | ARNOLD3 | 0.972 | 0.8699 | -0.1021 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | ARNOLD3 | 0.9777 | 0.8699 | -0.1078 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | TRIBUNE3 | 0.97 | 0.8699 | -0.1001 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | ARNOLD3 | 0.972 | 0.8699 | -0.1021 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | ARNOLD3 | 0.9777 | 0.8699 | -0.1078 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | TRIBUNE3 | 0.97 | 0.8699 | -0.1001 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | ARNOLD3 | 0.972 | 0.8699 | -0.1021 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | ARNOLD3 | 0.9777 | 0.8699 | -0.1078 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | TRIBUNE3 | 0.97 | 0.8699 | -0.1001 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | ARNOLD3 | 0.972 | 0.8699 | -0.1021 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | ARNOLD3 | 0.9777 | 0.8699 | -0.1078 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | TRIBUNE3 | 0.97 | 0.8699 | -0.1001 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | ARNOLD3 | 0.972 | 0.8699 | -0.1021 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | ARNOLD3 | 0.9777 | 0.8699 | -0.1078 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | TRIBUNE3 | 0.97 | 0.8699 | -0.1001 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | ARNOLD3 | 0.972 | 0.8699 | -0.1021 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | ARNOLD3 | 0.9777 | 0.8699 | -0.1078 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | TRIBUNE3 | 0.97 | 0.8699 | -0.1001 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | ARNOLD3 | 0.972 | 0.8699 | -0.1021 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | ARNOLD3 | 0.9777 | 0.8699 | -0.1078 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | TRIBUNE3 | 0.97 | 0.8699 | -0.1001 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | ARNOLD3 | 0.972 | 0.8699 | -0.1021 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | ARNOLD3 | 0.9777 | 0.8699 | -0.1078 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | TRIBUNE3 | 0.97 | 0.8699 | -0.1001 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | ARNOLD3 | 0.972 | 0.8699 | -0.1021 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | ARNOLD3 | 0.9777 | 0.8699 | -0.1078 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | TRIBUNE3 | 0.97 | 0.8699 | -0.1001 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | ARNOLD3 | 0.972 | 0.8699 | -0.1021 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | ARNOLD3 | 0.9777 | 0.8699 | -0.1078 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | TRIBUNE3 | 0.97 | 0.8699 | -0.1001 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | ARNOLD3 | 0.972 | 0.8699 | -0.1021 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | ARNOLD3 | 0.9777 | 0.8699 | -0.1078 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | TRIBUNE3 | 0.97 | 0.8699 | -0.1001 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | ARNOLD3 | 0.972 | 0.8699 | -0.1021 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | ARNOLD3 | 0.9777 | 0.8699 | -0.1078 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | TRIBUNE3 | 0.97 | 0.8699 | -0.1001 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | TRIB SW3 | 0.97 | 0.8702 | -0.0998 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | TRIB SW3 | 0.97 | 0.8702 | -0.0998 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | TRIB SW3 | 0.97 | 0.8702 | -0.0998 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | TRIB SW3 | 0.97 | 0.8702 | -0.0998 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | TRIB SW3 | 0.97 | 0.8702 | -0.0998 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | TRIB SW3 | 0.97 | 0.8702 | -0.0998 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | TRIB SW3 | 0.97 | 0.8702 | -0.0998 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | TRIB SW3 | 0.97 | 0.8702 | -0.0998 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | TRIB SW3 | 0.97 | 0.8702 | -0.0998 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | TRIB SW3 | 0.97 | 0.8702 | -0.0998 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | TRIB SW3 | 0.97 | 0.8702 | -0.0998 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | TRIB SW3 | 0.97 | 0.8702 | -0.0998 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | TRIB SW3 | 0.97 | 0.8702 | -0.0998 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | TRIB SW3 | 0.97 | 0.8702 | -0.0998 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | TRIB SW3 | 0.97 | 0.8702 | -0.0998 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | TRIB SW3 | 0.97 | 0.8702 | -0.0998 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | TRIB SW3 | 0.97 | 0.8702 | -0.0998 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | TRIB SW3 | 0.97 | 0.8702 | -0.0998 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | TRIB SW3 | 0.97 | 0.8702 | -0.0998 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | TRIB SW3 | 0.97 | 0.8702 | -0.0998 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | TRIB SW3 | 0.97 | 0.8702 | -0.0998 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | TRIB SW3 | 0.97 | 0.8702 | -0.0998 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | TRIB SW3 | 0.97 | 0.8702 | -0.0998 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | TRIB SW3 | 0.97 | 0.8702 | -0.0998 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | TRIB SW3 | 0.97 | 0.8702 | -0.0998 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | TRIB SW3 | 0.97 | 0.8702 | -0.0998 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | TRIB SW3 | 0.97 | 0.8702 | -0.0998 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | BEELER 3 | 0.9645 | 0.8707 | -0.0938 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | BEELER 3 | 0.9645 | 0.8707 | -0.0938 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | BEELER 3 | 0.9645 | 0.8707 | -0.0938 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | BEELER 3 | 0.9645 | 0.8707 | -0.0938 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | BEELER 3 | 0.9645 | 0.8707 | -0.0938 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | BEELER 3 | 0.9645 | 0.8707 | -0.0938 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | BEELER 3 | 0.9645 | 0.8707 | -0.0938 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | BEELER 3 | 0.9645 | 0.8707 | -0.0938 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | BEELER 3 | 0.9645 | 0.8707 | -0.0938 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | BEELER 3 | 0.9645 | 0.8707 | -0.0938 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | BEELER 3 | 0.9645 | 0.8707 | -0.0938 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | BEELER 3 | 0.9645 | 0.8707 | -0.0938 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | BEELER 3 | 0.9645 | 0.8707 | -0.0938 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | BEELER 3 | 0.9645 | 0.8707 | -0.0938 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | BEELER 3 | 0.9645 | 0.8707 | -0.0938 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | BEELER 3 | 0.9645 | 0.8707 | -0.0938 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | BEELER 3 | 0.9645 | 0.8707 | -0.0938 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | BEELER 3 | 0.9645 | 0.8707 | -0.0938 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | BEELER 3 | 0.9645 | 0.8707 | -0.0938 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | BEELER 3 | 0.9645 | 0.8707 | -0.0938 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | BEELER 3 | 0.9645 | 0.8707 | -0.0938 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | BEELER 3 | 0.9645 | 0.8707 | -0.0938 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | BEELER 3 | 0.9645 | 0.8707 | -0.0938 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | BEELER 3 | 0.9645 | 0.8707 | -0.0938 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | BEELER 3 | 0.9645 | 0.8707 | -0.0938 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | BEELER 3 | 0.9645 | 0.8707 | -0.0938 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | BEELER 3 | 0.9645 | 0.8707 | -0.0938 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | ELLIS 2 | 0.9727 | 0.8708 | -0.1019 |  | 0.9 | 1.05 | 0.05095 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | ELLIS 2 | 0.9727 | 0.8708 | -0.1019 |  | 0.9 | 1.05 | 0.04905 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | ELLIS 2 | 0.9727 | 0.8708 | -0.1019 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | ELLIS 2 | 0.9727 | 0.8708 | -0.1019 |  | 0.9 | 1.05 | 0.04262 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | ELLIS 2 | 0.9727 | 0.8708 | -0.1019 |  | 0.9 | 1.05 | 0.0627 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | ELLIS 2 | 0.9727 | 0.8708 | -0.1019 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | ELLIS 2 | 0.9727 | 0.8708 | -0.1019 |  | 0.9 | 1.05 | 0.05043 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | ELLIS 2 | 0.9727 | 0.8708 | -0.1019 |  | 0.9 | 1.05 | 0.05292 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | ELLIS 2 | 0.9727 | 0.8708 | -0.1019 |  | 0.9 | 1.05 | 0.0444 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | ELLIS 2 | 0.9727 | 0.8708 | -0.1019 |  | 0.9 | 1.05 | 0.04788 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | ELLIS 2 | 0.9727 | 0.8708 | -0.1019 |  | 0.9 | 1.05 | 0.05824 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | ELLIS 2 | 0.9727 | 0.8708 | -0.1019 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | ELLIS 2 | 0.9727 | 0.8708 | -0.1019 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | ELLIS 2 | 0.9727 | 0.8708 | -0.1019 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | ELLIS 2 | 0.9727 | 0.8708 | -0.1019 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | ELLIS 2 | 0.9727 | 0.8708 | -0.1019 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | ELLIS 2 | 0.9727 | 0.8708 | -0.1019 |  | 0.9 | 1.05 | 0.04773 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | ELLIS 2 | 0.9727 | 0.8708 | -0.1019 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | ELLIS 2 | 0.9727 | 0.8708 | -0.1019 |  | 0.9 | 1.05 | 0.0348 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | ELLIS 2 | 0.9727 | 0.8708 | -0.1019 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | ELLIS 2 | 0.9727 | 0.8708 | -0.1019 |  | 0.9 | 1.05 | 0.04996 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | ELLIS 2 | 0.9727 | 0.8708 | -0.1019 |  | 0.9 | 1.05 | 0.04835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | ELLIS 2 | 0.9727 | 0.8708 | -0.1019 |  | 0.9 | 1.05 | 0.05448 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | ELLIS 2 | 0.9727 | 0.8708 | -0.1019 |  | 0.9 | 1.05 | 0.05382 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | ELLIS 2 | 0.9727 | 0.8708 | -0.1019 |  | 0.9 | 1.05 | 0.03774 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | ELLIS 2 | 0.9727 | 0.8708 | -0.1019 |  | 0.9 | 1.05 | 0.04948 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | ELLIS 2 | 0.9727 | 0.8708 | -0.1019 |  | 0.9 | 1.05 | 0.04054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | PALMER3 | 0.9709 | 0.871 | -0.0999 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | PALMER3 | 0.9797 | 0.871 | -0.1087 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | LIBERTY3 | 0.961 | 0.871 | -0.09 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | LIBERTY3 | 0.9707 | 0.871 | -0.0997 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | PALMER3 | 0.9709 | 0.871 | -0.0999 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | PALMER3 | 0.9797 | 0.871 | -0.1087 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | LIBERTY3 | 0.961 | 0.871 | -0.09 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | LIBERTY3 | 0.9707 | 0.871 | -0.0997 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | PALMER3 | 0.9709 | 0.871 | -0.0999 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | PALMER3 | 0.9797 | 0.871 | -0.1087 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | LIBERTY3 | 0.961 | 0.871 | -0.09 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | LIBERTY3 | 0.9707 | 0.871 | -0.0997 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | PALMER3 | 0.9709 | 0.871 | -0.0999 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | PALMER3 | 0.9797 | 0.871 | -0.1087 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | LIBERTY3 | 0.961 | 0.871 | -0.09 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | LIBERTY3 | 0.9707 | 0.871 | -0.0997 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | PALMER3 | 0.9709 | 0.871 | -0.0999 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | PALMER3 | 0.9797 | 0.871 | -0.1087 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | LIBERTY3 | 0.961 | 0.871 | -0.09 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | LIBERTY3 | 0.9707 | 0.871 | -0.0997 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | PALMER3 | 0.9709 | 0.871 | -0.0999 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | PALMER3 | 0.9797 | 0.871 | -0.1087 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | LIBERTY3 | 0.961 | 0.871 | -0.09 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | LIBERTY3 | 0.9707 | 0.871 | -0.0997 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | PALMER3 | 0.9709 | 0.871 | -0.0999 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | PALMER3 | 0.9797 | 0.871 | -0.1087 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | LIBERTY3 | 0.961 | 0.871 | -0.09 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | LIBERTY3 | 0.9707 | 0.871 | -0.0997 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | PALMER3 | 0.9709 | 0.871 | -0.0999 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | PALMER3 | 0.9797 | 0.871 | -0.1087 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | LIBERTY3 | 0.961 | 0.871 | -0.09 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | LIBERTY3 | 0.9707 | 0.871 | -0.0997 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | PALMER3 | 0.9709 | 0.871 | -0.0999 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | PALMER3 | 0.9797 | 0.871 | -0.1087 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | LIBERTY3 | 0.961 | 0.871 | -0.09 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | LIBERTY3 | 0.9707 | 0.871 | -0.0997 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | PALMER3 | 0.9709 | 0.871 | -0.0999 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | PALMER3 | 0.9797 | 0.871 | -0.1087 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | LIBERTY3 | 0.961 | 0.871 | -0.09 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | LIBERTY3 | 0.9707 | 0.871 | -0.0997 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | PALMER3 | 0.9709 | 0.871 | -0.0999 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | PALMER3 | 0.9797 | 0.871 | -0.1087 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | LIBERTY3 | 0.961 | 0.871 | -0.09 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | LIBERTY3 | 0.9707 | 0.871 | -0.0997 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | PALMER3 | 0.9709 | 0.871 | -0.0999 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | PALMER3 | 0.9797 | 0.871 | -0.1087 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | LIBERTY3 | 0.961 | 0.871 | -0.09 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | LIBERTY3 | 0.9707 | 0.871 | -0.0997 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | PALMER3 | 0.9709 | 0.871 | -0.0999 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | PALMER3 | 0.9797 | 0.871 | -0.1087 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | LIBERTY3 | 0.961 | 0.871 | -0.09 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | LIBERTY3 | 0.9707 | 0.871 | -0.0997 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | PALMER3 | 0.9709 | 0.871 | -0.0999 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | PALMER3 | 0.9797 | 0.871 | -0.1087 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | LIBERTY3 | 0.961 | 0.871 | -0.09 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | LIBERTY3 | 0.9707 | 0.871 | -0.0997 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | PALMER3 | 0.9709 | 0.871 | -0.0999 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | PALMER3 | 0.9797 | 0.871 | -0.1087 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | LIBERTY3 | 0.961 | 0.871 | -0.09 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | LIBERTY3 | 0.9707 | 0.871 | -0.0997 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | PALMER3 | 0.9709 | 0.871 | -0.0999 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | PALMER3 | 0.9797 | 0.871 | -0.1087 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | LIBERTY3 | 0.961 | 0.871 | -0.09 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | LIBERTY3 | 0.9707 | 0.871 | -0.0997 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | PALMER3 | 0.9709 | 0.871 | -0.0999 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | PALMER3 | 0.9797 | 0.871 | -0.1087 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | LIBERTY3 | 0.961 | 0.871 | -0.09 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | LIBERTY3 | 0.9707 | 0.871 | -0.0997 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | PALMER3 | 0.9709 | 0.871 | -0.0999 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | PALMER3 | 0.9797 | 0.871 | -0.1087 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | LIBERTY3 | 0.961 | 0.871 | -0.09 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | LIBERTY3 | 0.9707 | 0.871 | -0.0997 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | PALMER3 | 0.9709 | 0.871 | -0.0999 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | PALMER3 | 0.9797 | 0.871 | -0.1087 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | LIBERTY3 | 0.961 | 0.871 | -0.09 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | LIBERTY3 | 0.9707 | 0.871 | -0.0997 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | PALMER3 | 0.9709 | 0.871 | -0.0999 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | PALMER3 | 0.9797 | 0.871 | -0.1087 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | LIBERTY3 | 0.961 | 0.871 | -0.09 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | LIBERTY3 | 0.9707 | 0.871 | -0.0997 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | PALMER3 | 0.9709 | 0.871 | -0.0999 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | PALMER3 | 0.9797 | 0.871 | -0.1087 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | LIBERTY3 | 0.961 | 0.871 | -0.09 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | LIBERTY3 | 0.9707 | 0.871 | -0.0997 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | PALMER3 | 0.9709 | 0.871 | -0.0999 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | PALMER3 | 0.9797 | 0.871 | -0.1087 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | LIBERTY3 | 0.961 | 0.871 | -0.09 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | LIBERTY3 | 0.9707 | 0.871 | -0.0997 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | PALMER3 | 0.9709 | 0.871 | -0.0999 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | PALMER3 | 0.9797 | 0.871 | -0.1087 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | LIBERTY3 | 0.961 | 0.871 | -0.09 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | LIBERTY3 | 0.9707 | 0.871 | -0.0997 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | PALMER3 | 0.9709 | 0.871 | -0.0999 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | PALMER3 | 0.9797 | 0.871 | -0.1087 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | LIBERTY3 | 0.961 | 0.871 | -0.09 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | LIBERTY3 | 0.9707 | 0.871 | -0.0997 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | PALMER3 | 0.9709 | 0.871 | -0.0999 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | PALMER3 | 0.9797 | 0.871 | -0.1087 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | LIBERTY3 | 0.961 | 0.871 | -0.09 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | LIBERTY3 | 0.9707 | 0.871 | -0.0997 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | PALMER3 | 0.9709 | 0.871 | -0.0999 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | PALMER3 | 0.9797 | 0.871 | -0.1087 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | LIBERTY3 | 0.961 | 0.871 | -0.09 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | LIBERTY3 | 0.9707 | 0.871 | -0.0997 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | PALMER3 | 0.9709 | 0.871 | -0.0999 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | PALMER3 | 0.9797 | 0.871 | -0.1087 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | LIBERTY3 | 0.961 | 0.871 | -0.09 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | LIBERTY3 | 0.9707 | 0.871 | -0.0997 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | STFRAN 3 | 0.966 | 0.8719 | -0.0941 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | BEELER 3 | 0.9699 | 0.8719 | -0.098 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | BEELER 3 | 0.9776 | 0.8719 | -0.1057 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | STFRAN 3 | 0.966 | 0.8719 | -0.0941 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | BEELER 3 | 0.9699 | 0.8719 | -0.098 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | BEELER 3 | 0.9776 | 0.8719 | -0.1057 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | STFRAN 3 | 0.966 | 0.8719 | -0.0941 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | BEELER 3 | 0.9699 | 0.8719 | -0.098 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | BEELER 3 | 0.9776 | 0.8719 | -0.1057 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | STFRAN 3 | 0.966 | 0.8719 | -0.0941 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | BEELER 3 | 0.9699 | 0.8719 | -0.098 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | BEELER 3 | 0.9776 | 0.8719 | -0.1057 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | STFRAN 3 | 0.966 | 0.8719 | -0.0941 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | BEELER 3 | 0.9699 | 0.8719 | -0.098 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | BEELER 3 | 0.9776 | 0.8719 | -0.1057 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | STFRAN 3 | 0.966 | 0.8719 | -0.0941 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | BEELER 3 | 0.9699 | 0.8719 | -0.098 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | BEELER 3 | 0.9776 | 0.8719 | -0.1057 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | STFRAN 3 | 0.966 | 0.8719 | -0.0941 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | BEELER 3 | 0.9699 | 0.8719 | -0.098 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | BEELER 3 | 0.9776 | 0.8719 | -0.1057 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | STFRAN 3 | 0.966 | 0.8719 | -0.0941 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | BEELER 3 | 0.9699 | 0.8719 | -0.098 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | BEELER 3 | 0.9776 | 0.8719 | -0.1057 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | STFRAN 3 | 0.966 | 0.8719 | -0.0941 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | BEELER 3 | 0.9699 | 0.8719 | -0.098 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | BEELER 3 | 0.9776 | 0.8719 | -0.1057 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | STFRAN 3 | 0.966 | 0.8719 | -0.0941 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | BEELER 3 | 0.9699 | 0.8719 | -0.098 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | BEELER 3 | 0.9776 | 0.8719 | -0.1057 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | STFRAN 3 | 0.966 | 0.8719 | -0.0941 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | BEELER 3 | 0.9699 | 0.8719 | -0.098 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | BEELER 3 | 0.9776 | 0.8719 | -0.1057 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | STFRAN 3 | 0.966 | 0.8719 | -0.0941 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | BEELER 3 | 0.9699 | 0.8719 | -0.098 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | BEELER 3 | 0.9776 | 0.8719 | -0.1057 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | STFRAN 3 | 0.966 | 0.8719 | -0.0941 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | BEELER 3 | 0.9699 | 0.8719 | -0.098 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | BEELER 3 | 0.9776 | 0.8719 | -0.1057 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | STFRAN 3 | 0.966 | 0.8719 | -0.0941 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | BEELER 3 | 0.9699 | 0.8719 | -0.098 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | BEELER 3 | 0.9776 | 0.8719 | -0.1057 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | STFRAN 3 | 0.966 | 0.8719 | -0.0941 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | BEELER 3 | 0.9699 | 0.8719 | -0.098 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | BEELER 3 | 0.9776 | 0.8719 | -0.1057 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | STFRAN 3 | 0.966 | 0.8719 | -0.0941 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | BEELER 3 | 0.9699 | 0.8719 | -0.098 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | BEELER 3 | 0.9776 | 0.8719 | -0.1057 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | STFRAN 3 | 0.966 | 0.8719 | -0.0941 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | BEELER 3 | 0.9699 | 0.8719 | -0.098 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | BEELER 3 | 0.9776 | 0.8719 | -0.1057 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | STFRAN 3 | 0.966 | 0.8719 | -0.0941 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | BEELER 3 | 0.9699 | 0.8719 | -0.098 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | BEELER 3 | 0.9776 | 0.8719 | -0.1057 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | STFRAN 3 | 0.966 | 0.8719 | -0.0941 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | BEELER 3 | 0.9699 | 0.8719 | -0.098 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | BEELER 3 | 0.9776 | 0.8719 | -0.1057 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | STFRAN 3 | 0.966 | 0.8719 | -0.0941 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | BEELER 3 | 0.9699 | 0.8719 | -0.098 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | BEELER 3 | 0.9776 | 0.8719 | -0.1057 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | STFRAN 3 | 0.966 | 0.8719 | -0.0941 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | BEELER 3 | 0.9699 | 0.8719 | -0.098 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | BEELER 3 | 0.9776 | 0.8719 | -0.1057 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | STFRAN 3 | 0.966 | 0.8719 | -0.0941 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | BEELER 3 | 0.9699 | 0.8719 | -0.098 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | BEELER 3 | 0.9776 | 0.8719 | -0.1057 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | STFRAN 3 | 0.966 | 0.8719 | -0.0941 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | BEELER 3 | 0.9699 | 0.8719 | -0.098 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | BEELER 3 | 0.9776 | 0.8719 | -0.1057 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | STFRAN 3 | 0.966 | 0.8719 | -0.0941 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | BEELER 3 | 0.9699 | 0.8719 | -0.098 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | BEELER 3 | 0.9776 | 0.8719 | -0.1057 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | STFRAN 3 | 0.966 | 0.8719 | -0.0941 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | BEELER 3 | 0.9699 | 0.8719 | -0.098 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | BEELER 3 | 0.9776 | 0.8719 | -0.1057 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | STFRAN 3 | 0.966 | 0.8719 | -0.0941 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | BEELER 3 | 0.9699 | 0.8719 | -0.098 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | BEELER 3 | 0.9776 | 0.8719 | -0.1057 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | STFRAN 3 | 0.966 | 0.8719 | -0.0941 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | BEELER 3 | 0.9699 | 0.8719 | -0.098 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | BEELER 3 | 0.9776 | 0.8719 | -0.1057 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | NESSCTY3 | 0.9682 | 0.872 | -0.0962 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | NESSCTY3 | 0.9682 | 0.872 | -0.0962 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | NESSCTY3 | 0.9682 | 0.872 | -0.0962 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | NESSCTY3 | 0.9682 | 0.872 | -0.0962 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | NESSCTY3 | 0.9682 | 0.872 | -0.0962 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | NESSCTY3 | 0.9682 | 0.872 | -0.0962 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | NESSCTY3 | 0.9682 | 0.872 | -0.0962 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | NESSCTY3 | 0.9682 | 0.872 | -0.0962 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | NESSCTY3 | 0.9682 | 0.872 | -0.0962 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | NESSCTY3 | 0.9682 | 0.872 | -0.0962 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | NESSCTY3 | 0.9682 | 0.872 | -0.0962 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | NESSCTY3 | 0.9682 | 0.872 | -0.0962 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | NESSCTY3 | 0.9682 | 0.872 | -0.0962 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | NESSCTY3 | 0.9682 | 0.872 | -0.0962 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | NESSCTY3 | 0.9682 | 0.872 | -0.0962 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | NESSCTY3 | 0.9682 | 0.872 | -0.0962 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | NESSCTY3 | 0.9682 | 0.872 | -0.0962 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | NESSCTY3 | 0.9682 | 0.872 | -0.0962 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | NESSCTY3 | 0.9682 | 0.872 | -0.0962 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | NESSCTY3 | 0.9682 | 0.872 | -0.0962 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | NESSCTY3 | 0.9682 | 0.872 | -0.0962 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | NESSCTY3 | 0.9682 | 0.872 | -0.0962 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | NESSCTY3 | 0.9682 | 0.872 | -0.0962 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | NESSCTY3 | 0.9682 | 0.872 | -0.0962 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | NESSCTY3 | 0.9682 | 0.872 | -0.0962 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | NESSCTY3 | 0.9682 | 0.872 | -0.0962 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | NESSCTY3 | 0.9682 | 0.872 | -0.0962 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | NESCTY 3 | 0.9682 | 0.8721 | -0.0961 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | NESCTY 3 | 0.9682 | 0.8721 | -0.0961 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | NESCTY 3 | 0.9682 | 0.8721 | -0.0961 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | NESCTY 3 | 0.9682 | 0.8721 | -0.0961 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | NESCTY 3 | 0.9682 | 0.8721 | -0.0961 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | NESCTY 3 | 0.9682 | 0.8721 | -0.0961 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | NESCTY 3 | 0.9682 | 0.8721 | -0.0961 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | NESCTY 3 | 0.9682 | 0.8721 | -0.0961 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | NESCTY 3 | 0.9682 | 0.8721 | -0.0961 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | NESCTY 3 | 0.9682 | 0.8721 | -0.0961 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | NESCTY 3 | 0.9682 | 0.8721 | -0.0961 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | NESCTY 3 | 0.9682 | 0.8721 | -0.0961 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | NESCTY 3 | 0.9682 | 0.8721 | -0.0961 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | NESCTY 3 | 0.9682 | 0.8721 | -0.0961 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | NESCTY 3 | 0.9682 | 0.8721 | -0.0961 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | NESCTY 3 | 0.9682 | 0.8721 | -0.0961 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | NESCTY 3 | 0.9682 | 0.8721 | -0.0961 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | NESCTY 3 | 0.9682 | 0.8721 | -0.0961 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | NESCTY 3 | 0.9682 | 0.8721 | -0.0961 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | NESCTY 3 | 0.9682 | 0.8721 | -0.0961 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | NESCTY 3 | 0.9682 | 0.8721 | -0.0961 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | NESCTY 3 | 0.9682 | 0.8721 | -0.0961 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | NESCTY 3 | 0.9682 | 0.8721 | -0.0961 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | NESCTY 3 | 0.9682 | 0.8721 | -0.0961 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | NESCTY 3 | 0.9682 | 0.8721 | -0.0961 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | NESCTY 3 | 0.9682 | 0.8721 | -0.0961 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | NESCTY 3 | 0.9682 | 0.8721 | -0.0961 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | RANSOM 3 | 0.9709 | 0.8722 | -0.0987 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | RANSOM 3 | 0.9709 | 0.8722 | -0.0987 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | RANSOM 3 | 0.9709 | 0.8722 | -0.0987 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | RANSOM 3 | 0.9709 | 0.8722 | -0.0987 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | RANSOM 3 | 0.9709 | 0.8722 | -0.0987 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | RANSOM 3 | 0.9709 | 0.8722 | -0.0987 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | RANSOM 3 | 0.9709 | 0.8722 | -0.0987 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | RANSOM 3 | 0.9709 | 0.8722 | -0.0987 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | RANSOM 3 | 0.9709 | 0.8722 | -0.0987 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | RANSOM 3 | 0.9709 | 0.8722 | -0.0987 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | RANSOM 3 | 0.9709 | 0.8722 | -0.0987 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | RANSOM 3 | 0.9709 | 0.8722 | -0.0987 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | RANSOM 3 | 0.9709 | 0.8722 | -0.0987 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | RANSOM 3 | 0.9709 | 0.8722 | -0.0987 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | RANSOM 3 | 0.9709 | 0.8722 | -0.0987 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | RANSOM 3 | 0.9709 | 0.8722 | -0.0987 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | RANSOM 3 | 0.9709 | 0.8722 | -0.0987 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | RANSOM 3 | 0.9709 | 0.8722 | -0.0987 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | RANSOM 3 | 0.9709 | 0.8722 | -0.0987 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | RANSOM 3 | 0.9709 | 0.8722 | -0.0987 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | RANSOM 3 | 0.9709 | 0.8722 | -0.0987 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | RANSOM 3 | 0.9709 | 0.8722 | -0.0987 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | RANSOM 3 | 0.9709 | 0.8722 | -0.0987 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | RANSOM 3 | 0.9709 | 0.8722 | -0.0987 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | RANSOM 3 | 0.9709 | 0.8722 | -0.0987 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | RANSOM 3 | 0.9709 | 0.8722 | -0.0987 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | RANSOM 3 | 0.9709 | 0.8722 | -0.0987 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | GODLNDT3 | 0.9773 | 0.8728 | -0.1045 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | GODLNDT3 | 0.9817 | 0.8728 | -0.1089 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | GODLNDT3 | 0.9773 | 0.8728 | -0.1045 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | GODLNDT3 | 0.9817 | 0.8728 | -0.1089 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | GODLNDT3 | 0.9773 | 0.8728 | -0.1045 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | GODLNDT3 | 0.9817 | 0.8728 | -0.1089 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | GODLNDT3 | 0.9773 | 0.8728 | -0.1045 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | GODLNDT3 | 0.9817 | 0.8728 | -0.1089 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | GODLNDT3 | 0.9773 | 0.8728 | -0.1045 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | GODLNDT3 | 0.9817 | 0.8728 | -0.1089 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | GODLNDT3 | 0.9773 | 0.8728 | -0.1045 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | GODLNDT3 | 0.9817 | 0.8728 | -0.1089 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | GODLNDT3 | 0.9773 | 0.8728 | -0.1045 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | GODLNDT3 | 0.9817 | 0.8728 | -0.1089 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | GODLNDT3 | 0.9773 | 0.8728 | -0.1045 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | GODLNDT3 | 0.9817 | 0.8728 | -0.1089 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | GODLNDT3 | 0.9773 | 0.8728 | -0.1045 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | GODLNDT3 | 0.9817 | 0.8728 | -0.1089 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | GODLNDT3 | 0.9773 | 0.8728 | -0.1045 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | GODLNDT3 | 0.9817 | 0.8728 | -0.1089 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | GODLNDT3 | 0.9773 | 0.8728 | -0.1045 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | GODLNDT3 | 0.9817 | 0.8728 | -0.1089 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | GODLNDT3 | 0.9773 | 0.8728 | -0.1045 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | GODLNDT3 | 0.9817 | 0.8728 | -0.1089 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | GODLNDT3 | 0.9773 | 0.8728 | -0.1045 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | GODLNDT3 | 0.9817 | 0.8728 | -0.1089 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | GODLNDT3 | 0.9773 | 0.8728 | -0.1045 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | GODLNDT3 | 0.9817 | 0.8728 | -0.1089 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | GODLNDT3 | 0.9773 | 0.8728 | -0.1045 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | GODLNDT3 | 0.9817 | 0.8728 | -0.1089 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | GODLNDT3 | 0.9773 | 0.8728 | -0.1045 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | GODLNDT3 | 0.9817 | 0.8728 | -0.1089 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | GODLNDT3 | 0.9773 | 0.8728 | -0.1045 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | GODLNDT3 | 0.9817 | 0.8728 | -0.1089 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | GODLNDT3 | 0.9773 | 0.8728 | -0.1045 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | GODLNDT3 | 0.9817 | 0.8728 | -0.1089 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | GODLNDT3 | 0.9773 | 0.8728 | -0.1045 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | GODLNDT3 | 0.9817 | 0.8728 | -0.1089 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | GODLNDT3 | 0.9773 | 0.8728 | -0.1045 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | GODLNDT3 | 0.9817 | 0.8728 | -0.1089 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | GODLNDT3 | 0.9773 | 0.8728 | -0.1045 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | GODLNDT3 | 0.9817 | 0.8728 | -0.1089 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | GODLNDT3 | 0.9773 | 0.8728 | -0.1045 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | GODLNDT3 | 0.9817 | 0.8728 | -0.1089 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | GODLNDT3 | 0.9773 | 0.8728 | -0.1045 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | GODLNDT3 | 0.9817 | 0.8728 | -0.1089 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | GODLNDT3 | 0.9773 | 0.8728 | -0.1045 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | GODLNDT3 | 0.9817 | 0.8728 | -0.1089 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | GODLNDT3 | 0.9773 | 0.8728 | -0.1045 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | GODLNDT3 | 0.9817 | 0.8728 | -0.1089 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | GODLNDT3 | 0.9773 | 0.8728 | -0.1045 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | GODLNDT3 | 0.9817 | 0.8728 | -0.1089 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | GODLNDT3 | 0.9773 | 0.8728 | -0.1045 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | GODLNDT3 | 0.9817 | 0.8728 | -0.1089 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | LAWNRID3 | 0.9858 | 0.8729 | -0.1129 |  | 0.9 | 1.05 | 0.05095 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | RANSOM 2 | 0.9787 | 0.8729 | -0.1058 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | RANSOM 2 | 0.984 | 0.8729 | -0.1111 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | LAWNRID3 | 0.9858 | 0.8729 | -0.1129 |  | 0.9 | 1.05 | 0.04905 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | RANSOM 2 | 0.9787 | 0.8729 | -0.1058 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | RANSOM 2 | 0.984 | 0.8729 | -0.1111 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | LAWNRID3 | 0.9858 | 0.8729 | -0.1129 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | RANSOM 2 | 0.9787 | 0.8729 | -0.1058 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | RANSOM 2 | 0.984 | 0.8729 | -0.1111 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | LAWNRID3 | 0.9858 | 0.8729 | -0.1129 |  | 0.9 | 1.05 | 0.04262 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | RANSOM 2 | 0.9787 | 0.8729 | -0.1058 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | RANSOM 2 | 0.984 | 0.8729 | -0.1111 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | LAWNRID3 | 0.9858 | 0.8729 | -0.1129 |  | 0.9 | 1.05 | 0.0627 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | RANSOM 2 | 0.9787 | 0.8729 | -0.1058 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | RANSOM 2 | 0.984 | 0.8729 | -0.1111 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | LAWNRID3 | 0.9858 | 0.8729 | -0.1129 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | RANSOM 2 | 0.9787 | 0.8729 | -0.1058 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | RANSOM 2 | 0.984 | 0.8729 | -0.1111 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | LAWNRID3 | 0.9858 | 0.8729 | -0.1129 |  | 0.9 | 1.05 | 0.05043 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | RANSOM 2 | 0.9787 | 0.8729 | -0.1058 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | RANSOM 2 | 0.984 | 0.8729 | -0.1111 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | LAWNRID3 | 0.9858 | 0.8729 | -0.1129 |  | 0.9 | 1.05 | 0.05292 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | RANSOM 2 | 0.9787 | 0.8729 | -0.1058 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | RANSOM 2 | 0.984 | 0.8729 | -0.1111 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | LAWNRID3 | 0.9858 | 0.8729 | -0.1129 |  | 0.9 | 1.05 | 0.0444 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | RANSOM 2 | 0.9787 | 0.8729 | -0.1058 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | RANSOM 2 | 0.984 | 0.8729 | -0.1111 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | LAWNRID3 | 0.9858 | 0.8729 | -0.1129 |  | 0.9 | 1.05 | 0.04788 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | RANSOM 2 | 0.9787 | 0.8729 | -0.1058 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | RANSOM 2 | 0.984 | 0.8729 | -0.1111 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | LAWNRID3 | 0.9858 | 0.8729 | -0.1129 |  | 0.9 | 1.05 | 0.05824 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | RANSOM 2 | 0.9787 | 0.8729 | -0.1058 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | RANSOM 2 | 0.984 | 0.8729 | -0.1111 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | LAWNRID3 | 0.9858 | 0.8729 | -0.1129 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | RANSOM 2 | 0.9787 | 0.8729 | -0.1058 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | RANSOM 2 | 0.984 | 0.8729 | -0.1111 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | LAWNRID3 | 0.9858 | 0.8729 | -0.1129 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | RANSOM 2 | 0.9787 | 0.8729 | -0.1058 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | RANSOM 2 | 0.984 | 0.8729 | -0.1111 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | LAWNRID3 | 0.9858 | 0.8729 | -0.1129 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | RANSOM 2 | 0.9787 | 0.8729 | -0.1058 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | RANSOM 2 | 0.984 | 0.8729 | -0.1111 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | LAWNRID3 | 0.9858 | 0.8729 | -0.1129 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | RANSOM 2 | 0.9787 | 0.8729 | -0.1058 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | RANSOM 2 | 0.984 | 0.8729 | -0.1111 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | LAWNRID3 | 0.9858 | 0.8729 | -0.1129 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | RANSOM 2 | 0.9787 | 0.8729 | -0.1058 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | RANSOM 2 | 0.984 | 0.8729 | -0.1111 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | LAWNRID3 | 0.9858 | 0.8729 | -0.1129 |  | 0.9 | 1.05 | 0.04773 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | RANSOM 2 | 0.9787 | 0.8729 | -0.1058 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | RANSOM 2 | 0.984 | 0.8729 | -0.1111 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | LAWNRID3 | 0.9858 | 0.8729 | -0.1129 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | RANSOM 2 | 0.9787 | 0.8729 | -0.1058 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | RANSOM 2 | 0.984 | 0.8729 | -0.1111 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | LAWNRID3 | 0.9858 | 0.8729 | -0.1129 |  | 0.9 | 1.05 | 0.0348 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | RANSOM 2 | 0.9787 | 0.8729 | -0.1058 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | RANSOM 2 | 0.984 | 0.8729 | -0.1111 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | LAWNRID3 | 0.9858 | 0.8729 | -0.1129 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | RANSOM 2 | 0.9787 | 0.8729 | -0.1058 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | RANSOM 2 | 0.984 | 0.8729 | -0.1111 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | LAWNRID3 | 0.9858 | 0.8729 | -0.1129 |  | 0.9 | 1.05 | 0.04996 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | RANSOM 2 | 0.9787 | 0.8729 | -0.1058 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | RANSOM 2 | 0.984 | 0.8729 | -0.1111 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | LAWNRID3 | 0.9858 | 0.8729 | -0.1129 |  | 0.9 | 1.05 | 0.04835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | RANSOM 2 | 0.9787 | 0.8729 | -0.1058 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | RANSOM 2 | 0.984 | 0.8729 | -0.1111 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | LAWNRID3 | 0.9858 | 0.8729 | -0.1129 |  | 0.9 | 1.05 | 0.05448 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | RANSOM 2 | 0.9787 | 0.8729 | -0.1058 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | RANSOM 2 | 0.984 | 0.8729 | -0.1111 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | LAWNRID3 | 0.9858 | 0.8729 | -0.1129 |  | 0.9 | 1.05 | 0.05382 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | RANSOM 2 | 0.9787 | 0.8729 | -0.1058 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | RANSOM 2 | 0.984 | 0.8729 | -0.1111 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | LAWNRID3 | 0.9858 | 0.8729 | -0.1129 |  | 0.9 | 1.05 | 0.03774 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | RANSOM 2 | 0.9787 | 0.8729 | -0.1058 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | RANSOM 2 | 0.984 | 0.8729 | -0.1111 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | LAWNRID3 | 0.9858 | 0.8729 | -0.1129 |  | 0.9 | 1.05 | 0.04948 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | RANSOM 2 | 0.9787 | 0.8729 | -0.1058 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | RANSOM 2 | 0.984 | 0.8729 | -0.1111 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | LAWNRID3 | 0.9858 | 0.8729 | -0.1129 |  | 0.9 | 1.05 | 0.04054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | RANSOM 2 | 0.9787 | 0.8729 | -0.1058 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | RANSOM 2 | 0.984 | 0.8729 | -0.1111 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | LIBERTY3 | 0.961 | 0.8731 | -0.0879 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | LIBERTY3 | 0.961 | 0.8731 | -0.0879 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | LIBERTY3 | 0.961 | 0.8731 | -0.0879 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | LIBERTY3 | 0.961 | 0.8731 | -0.0879 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | LIBERTY3 | 0.961 | 0.8731 | -0.0879 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | LIBERTY3 | 0.961 | 0.8731 | -0.0879 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | LIBERTY3 | 0.961 | 0.8731 | -0.0879 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | LIBERTY3 | 0.961 | 0.8731 | -0.0879 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | LIBERTY3 | 0.961 | 0.8731 | -0.0879 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | LIBERTY3 | 0.961 | 0.8731 | -0.0879 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | LIBERTY3 | 0.961 | 0.8731 | -0.0879 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | LIBERTY3 | 0.961 | 0.8731 | -0.0879 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | LIBERTY3 | 0.961 | 0.8731 | -0.0879 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | LIBERTY3 | 0.961 | 0.8731 | -0.0879 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | LIBERTY3 | 0.961 | 0.8731 | -0.0879 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | LIBERTY3 | 0.961 | 0.8731 | -0.0879 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | LIBERTY3 | 0.961 | 0.8731 | -0.0879 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | LIBERTY3 | 0.961 | 0.8731 | -0.0879 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | LIBERTY3 | 0.961 | 0.8731 | -0.0879 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | LIBERTY3 | 0.961 | 0.8731 | -0.0879 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | LIBERTY3 | 0.961 | 0.8731 | -0.0879 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | LIBERTY3 | 0.961 | 0.8731 | -0.0879 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | LIBERTY3 | 0.961 | 0.8731 | -0.0879 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | LIBERTY3 | 0.961 | 0.8731 | -0.0879 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | LIBERTY3 | 0.961 | 0.8731 | -0.0879 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | LIBERTY3 | 0.961 | 0.8731 | -0.0879 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | LIBERTY3 | 0.961 | 0.8731 | -0.0879 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | PALMER3 | 0.9709 | 0.8736 | -0.0973 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | NESSCTY3 | 0.975 | 0.8736 | -0.1014 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | NESSCTY3 | 0.981 | 0.8736 | -0.1074 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | PALMER3 | 0.9709 | 0.8736 | -0.0973 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | NESSCTY3 | 0.975 | 0.8736 | -0.1014 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | NESSCTY3 | 0.981 | 0.8736 | -0.1074 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | PALMER3 | 0.9709 | 0.8736 | -0.0973 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | NESSCTY3 | 0.975 | 0.8736 | -0.1014 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | NESSCTY3 | 0.981 | 0.8736 | -0.1074 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | PALMER3 | 0.9709 | 0.8736 | -0.0973 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | NESSCTY3 | 0.975 | 0.8736 | -0.1014 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | NESSCTY3 | 0.981 | 0.8736 | -0.1074 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | PALMER3 | 0.9709 | 0.8736 | -0.0973 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | NESSCTY3 | 0.975 | 0.8736 | -0.1014 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | NESSCTY3 | 0.981 | 0.8736 | -0.1074 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | PALMER3 | 0.9709 | 0.8736 | -0.0973 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | NESSCTY3 | 0.975 | 0.8736 | -0.1014 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | NESSCTY3 | 0.981 | 0.8736 | -0.1074 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | PALMER3 | 0.9709 | 0.8736 | -0.0973 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | NESSCTY3 | 0.975 | 0.8736 | -0.1014 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | NESSCTY3 | 0.981 | 0.8736 | -0.1074 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | PALMER3 | 0.9709 | 0.8736 | -0.0973 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | NESSCTY3 | 0.975 | 0.8736 | -0.1014 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | NESSCTY3 | 0.981 | 0.8736 | -0.1074 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | PALMER3 | 0.9709 | 0.8736 | -0.0973 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | NESSCTY3 | 0.975 | 0.8736 | -0.1014 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | NESSCTY3 | 0.981 | 0.8736 | -0.1074 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | PALMER3 | 0.9709 | 0.8736 | -0.0973 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | NESSCTY3 | 0.975 | 0.8736 | -0.1014 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | NESSCTY3 | 0.981 | 0.8736 | -0.1074 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | PALMER3 | 0.9709 | 0.8736 | -0.0973 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | NESSCTY3 | 0.975 | 0.8736 | -0.1014 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | NESSCTY3 | 0.981 | 0.8736 | -0.1074 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | PALMER3 | 0.9709 | 0.8736 | -0.0973 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | NESSCTY3 | 0.975 | 0.8736 | -0.1014 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | NESSCTY3 | 0.981 | 0.8736 | -0.1074 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | PALMER3 | 0.9709 | 0.8736 | -0.0973 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | NESSCTY3 | 0.975 | 0.8736 | -0.1014 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | NESSCTY3 | 0.981 | 0.8736 | -0.1074 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | PALMER3 | 0.9709 | 0.8736 | -0.0973 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | NESSCTY3 | 0.975 | 0.8736 | -0.1014 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | NESSCTY3 | 0.981 | 0.8736 | -0.1074 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | PALMER3 | 0.9709 | 0.8736 | -0.0973 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | NESSCTY3 | 0.975 | 0.8736 | -0.1014 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | NESSCTY3 | 0.981 | 0.8736 | -0.1074 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | PALMER3 | 0.9709 | 0.8736 | -0.0973 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | NESSCTY3 | 0.975 | 0.8736 | -0.1014 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | NESSCTY3 | 0.981 | 0.8736 | -0.1074 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | PALMER3 | 0.9709 | 0.8736 | -0.0973 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | NESSCTY3 | 0.975 | 0.8736 | -0.1014 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | NESSCTY3 | 0.981 | 0.8736 | -0.1074 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | PALMER3 | 0.9709 | 0.8736 | -0.0973 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | NESSCTY3 | 0.975 | 0.8736 | -0.1014 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | NESSCTY3 | 0.981 | 0.8736 | -0.1074 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | PALMER3 | 0.9709 | 0.8736 | -0.0973 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | NESSCTY3 | 0.975 | 0.8736 | -0.1014 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | NESSCTY3 | 0.981 | 0.8736 | -0.1074 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | PALMER3 | 0.9709 | 0.8736 | -0.0973 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | NESSCTY3 | 0.975 | 0.8736 | -0.1014 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | NESSCTY3 | 0.981 | 0.8736 | -0.1074 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | PALMER3 | 0.9709 | 0.8736 | -0.0973 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | NESSCTY3 | 0.975 | 0.8736 | -0.1014 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | NESSCTY3 | 0.981 | 0.8736 | -0.1074 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | PALMER3 | 0.9709 | 0.8736 | -0.0973 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | NESSCTY3 | 0.975 | 0.8736 | -0.1014 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | NESSCTY3 | 0.981 | 0.8736 | -0.1074 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | PALMER3 | 0.9709 | 0.8736 | -0.0973 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | NESSCTY3 | 0.975 | 0.8736 | -0.1014 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | NESSCTY3 | 0.981 | 0.8736 | -0.1074 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | PALMER3 | 0.9709 | 0.8736 | -0.0973 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | NESSCTY3 | 0.975 | 0.8736 | -0.1014 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | NESSCTY3 | 0.981 | 0.8736 | -0.1074 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | PALMER3 | 0.9709 | 0.8736 | -0.0973 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | NESSCTY3 | 0.975 | 0.8736 | -0.1014 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | NESSCTY3 | 0.981 | 0.8736 | -0.1074 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | PALMER3 | 0.9709 | 0.8736 | -0.0973 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | NESSCTY3 | 0.975 | 0.8736 | -0.1014 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | NESSCTY3 | 0.981 | 0.8736 | -0.1074 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | PALMER3 | 0.9709 | 0.8736 | -0.0973 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | NESSCTY3 | 0.975 | 0.8736 | -0.1014 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | NESSCTY3 | 0.981 | 0.8736 | -0.1074 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | NESCTY 3 | 0.975 | 0.8737 | -0.1013 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | NESCTY 3 | 0.981 | 0.8737 | -0.1073 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | NESCTY 3 | 0.975 | 0.8737 | -0.1013 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | NESCTY 3 | 0.981 | 0.8737 | -0.1073 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | NESCTY 3 | 0.975 | 0.8737 | -0.1013 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | NESCTY 3 | 0.981 | 0.8737 | -0.1073 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | NESCTY 3 | 0.975 | 0.8737 | -0.1013 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | NESCTY 3 | 0.981 | 0.8737 | -0.1073 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | NESCTY 3 | 0.975 | 0.8737 | -0.1013 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | NESCTY 3 | 0.981 | 0.8737 | -0.1073 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | NESCTY 3 | 0.975 | 0.8737 | -0.1013 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | NESCTY 3 | 0.981 | 0.8737 | -0.1073 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | NESCTY 3 | 0.975 | 0.8737 | -0.1013 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | NESCTY 3 | 0.981 | 0.8737 | -0.1073 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | NESCTY 3 | 0.975 | 0.8737 | -0.1013 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | NESCTY 3 | 0.981 | 0.8737 | -0.1073 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | NESCTY 3 | 0.975 | 0.8737 | -0.1013 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | NESCTY 3 | 0.981 | 0.8737 | -0.1073 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | NESCTY 3 | 0.975 | 0.8737 | -0.1013 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | NESCTY 3 | 0.981 | 0.8737 | -0.1073 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | NESCTY 3 | 0.975 | 0.8737 | -0.1013 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | NESCTY 3 | 0.981 | 0.8737 | -0.1073 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | NESCTY 3 | 0.975 | 0.8737 | -0.1013 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | NESCTY 3 | 0.981 | 0.8737 | -0.1073 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | NESCTY 3 | 0.975 | 0.8737 | -0.1013 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | NESCTY 3 | 0.981 | 0.8737 | -0.1073 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | NESCTY 3 | 0.975 | 0.8737 | -0.1013 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | NESCTY 3 | 0.981 | 0.8737 | -0.1073 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | NESCTY 3 | 0.975 | 0.8737 | -0.1013 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | NESCTY 3 | 0.981 | 0.8737 | -0.1073 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | NESCTY 3 | 0.975 | 0.8737 | -0.1013 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | NESCTY 3 | 0.981 | 0.8737 | -0.1073 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | NESCTY 3 | 0.975 | 0.8737 | -0.1013 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | NESCTY 3 | 0.981 | 0.8737 | -0.1073 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | NESCTY 3 | 0.975 | 0.8737 | -0.1013 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | NESCTY 3 | 0.981 | 0.8737 | -0.1073 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | NESCTY 3 | 0.975 | 0.8737 | -0.1013 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | NESCTY 3 | 0.981 | 0.8737 | -0.1073 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | NESCTY 3 | 0.975 | 0.8737 | -0.1013 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | NESCTY 3 | 0.981 | 0.8737 | -0.1073 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | NESCTY 3 | 0.975 | 0.8737 | -0.1013 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | NESCTY 3 | 0.981 | 0.8737 | -0.1073 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | NESCTY 3 | 0.975 | 0.8737 | -0.1013 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | NESCTY 3 | 0.981 | 0.8737 | -0.1073 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | NESCTY 3 | 0.975 | 0.8737 | -0.1013 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | NESCTY 3 | 0.981 | 0.8737 | -0.1073 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | NESCTY 3 | 0.975 | 0.8737 | -0.1013 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | NESCTY 3 | 0.981 | 0.8737 | -0.1073 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | NESCTY 3 | 0.975 | 0.8737 | -0.1013 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | NESCTY 3 | 0.981 | 0.8737 | -0.1073 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | NESCTY 3 | 0.975 | 0.8737 | -0.1013 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | NESCTY 3 | 0.981 | 0.8737 | -0.1073 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | NESCTY 3 | 0.975 | 0.8737 | -0.1013 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | NESCTY 3 | 0.981 | 0.8737 | -0.1073 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | ARNOLD3 | 0.972 | 0.8739 | -0.0981 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | ARNOLD3 | 0.972 | 0.8739 | -0.0981 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | ARNOLD3 | 0.972 | 0.8739 | -0.0981 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | ARNOLD3 | 0.972 | 0.8739 | -0.0981 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | ARNOLD3 | 0.972 | 0.8739 | -0.0981 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | ARNOLD3 | 0.972 | 0.8739 | -0.0981 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | ARNOLD3 | 0.972 | 0.8739 | -0.0981 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | ARNOLD3 | 0.972 | 0.8739 | -0.0981 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | ARNOLD3 | 0.972 | 0.8739 | -0.0981 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | ARNOLD3 | 0.972 | 0.8739 | -0.0981 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | ARNOLD3 | 0.972 | 0.8739 | -0.0981 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | ARNOLD3 | 0.972 | 0.8739 | -0.0981 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | ARNOLD3 | 0.972 | 0.8739 | -0.0981 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | ARNOLD3 | 0.972 | 0.8739 | -0.0981 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | ARNOLD3 | 0.972 | 0.8739 | -0.0981 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | ARNOLD3 | 0.972 | 0.8739 | -0.0981 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | ARNOLD3 | 0.972 | 0.8739 | -0.0981 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | ARNOLD3 | 0.972 | 0.8739 | -0.0981 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | ARNOLD3 | 0.972 | 0.8739 | -0.0981 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | ARNOLD3 | 0.972 | 0.8739 | -0.0981 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | ARNOLD3 | 0.972 | 0.8739 | -0.0981 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | ARNOLD3 | 0.972 | 0.8739 | -0.0981 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | ARNOLD3 | 0.972 | 0.8739 | -0.0981 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | ARNOLD3 | 0.972 | 0.8739 | -0.0981 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | ARNOLD3 | 0.972 | 0.8739 | -0.0981 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | ARNOLD3 | 0.972 | 0.8739 | -0.0981 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | ARNOLD3 | 0.972 | 0.8739 | -0.0981 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | GOODCTY3 | 0.9736 | 0.8742 | -0.0994 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | LIBERTY3 | 0.9655 | 0.8742 | -0.0913 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | LIBERTY3 | 0.9744 | 0.8742 | -0.1002 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | GOODCTY3 | 0.9736 | 0.8742 | -0.0994 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | LIBERTY3 | 0.9655 | 0.8742 | -0.0913 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | LIBERTY3 | 0.9744 | 0.8742 | -0.1002 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | GOODCTY3 | 0.9736 | 0.8742 | -0.0994 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | LIBERTY3 | 0.9655 | 0.8742 | -0.0913 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | LIBERTY3 | 0.9744 | 0.8742 | -0.1002 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | GOODCTY3 | 0.9736 | 0.8742 | -0.0994 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | LIBERTY3 | 0.9655 | 0.8742 | -0.0913 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | LIBERTY3 | 0.9744 | 0.8742 | -0.1002 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | GOODCTY3 | 0.9736 | 0.8742 | -0.0994 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | LIBERTY3 | 0.9655 | 0.8742 | -0.0913 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | LIBERTY3 | 0.9744 | 0.8742 | -0.1002 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | GOODCTY3 | 0.9736 | 0.8742 | -0.0994 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | LIBERTY3 | 0.9655 | 0.8742 | -0.0913 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | LIBERTY3 | 0.9744 | 0.8742 | -0.1002 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | GOODCTY3 | 0.9736 | 0.8742 | -0.0994 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | LIBERTY3 | 0.9655 | 0.8742 | -0.0913 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | LIBERTY3 | 0.9744 | 0.8742 | -0.1002 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | GOODCTY3 | 0.9736 | 0.8742 | -0.0994 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | LIBERTY3 | 0.9655 | 0.8742 | -0.0913 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | LIBERTY3 | 0.9744 | 0.8742 | -0.1002 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | GOODCTY3 | 0.9736 | 0.8742 | -0.0994 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | LIBERTY3 | 0.9655 | 0.8742 | -0.0913 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | LIBERTY3 | 0.9744 | 0.8742 | -0.1002 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | GOODCTY3 | 0.9736 | 0.8742 | -0.0994 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | LIBERTY3 | 0.9655 | 0.8742 | -0.0913 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | LIBERTY3 | 0.9744 | 0.8742 | -0.1002 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | GOODCTY3 | 0.9736 | 0.8742 | -0.0994 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | LIBERTY3 | 0.9655 | 0.8742 | -0.0913 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | LIBERTY3 | 0.9744 | 0.8742 | -0.1002 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | GOODCTY3 | 0.9736 | 0.8742 | -0.0994 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | LIBERTY3 | 0.9655 | 0.8742 | -0.0913 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | LIBERTY3 | 0.9744 | 0.8742 | -0.1002 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | GOODCTY3 | 0.9736 | 0.8742 | -0.0994 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | LIBERTY3 | 0.9655 | 0.8742 | -0.0913 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | LIBERTY3 | 0.9744 | 0.8742 | -0.1002 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | GOODCTY3 | 0.9736 | 0.8742 | -0.0994 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | LIBERTY3 | 0.9655 | 0.8742 | -0.0913 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | LIBERTY3 | 0.9744 | 0.8742 | -0.1002 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | GOODCTY3 | 0.9736 | 0.8742 | -0.0994 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | LIBERTY3 | 0.9655 | 0.8742 | -0.0913 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | LIBERTY3 | 0.9744 | 0.8742 | -0.1002 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | GOODCTY3 | 0.9736 | 0.8742 | -0.0994 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | LIBERTY3 | 0.9655 | 0.8742 | -0.0913 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | LIBERTY3 | 0.9744 | 0.8742 | -0.1002 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | GOODCTY3 | 0.9736 | 0.8742 | -0.0994 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | LIBERTY3 | 0.9655 | 0.8742 | -0.0913 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | LIBERTY3 | 0.9744 | 0.8742 | -0.1002 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | GOODCTY3 | 0.9736 | 0.8742 | -0.0994 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | LIBERTY3 | 0.9655 | 0.8742 | -0.0913 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | LIBERTY3 | 0.9744 | 0.8742 | -0.1002 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | GOODCTY3 | 0.9736 | 0.8742 | -0.0994 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | LIBERTY3 | 0.9655 | 0.8742 | -0.0913 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | LIBERTY3 | 0.9744 | 0.8742 | -0.1002 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | GOODCTY3 | 0.9736 | 0.8742 | -0.0994 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | LIBERTY3 | 0.9655 | 0.8742 | -0.0913 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | LIBERTY3 | 0.9744 | 0.8742 | -0.1002 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | GOODCTY3 | 0.9736 | 0.8742 | -0.0994 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | LIBERTY3 | 0.9655 | 0.8742 | -0.0913 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | LIBERTY3 | 0.9744 | 0.8742 | -0.1002 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | GOODCTY3 | 0.9736 | 0.8742 | -0.0994 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | LIBERTY3 | 0.9655 | 0.8742 | -0.0913 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | LIBERTY3 | 0.9744 | 0.8742 | -0.1002 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | GOODCTY3 | 0.9736 | 0.8742 | -0.0994 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | LIBERTY3 | 0.9655 | 0.8742 | -0.0913 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | LIBERTY3 | 0.9744 | 0.8742 | -0.1002 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | GOODCTY3 | 0.9736 | 0.8742 | -0.0994 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | LIBERTY3 | 0.9655 | 0.8742 | -0.0913 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | LIBERTY3 | 0.9744 | 0.8742 | -0.1002 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | GOODCTY3 | 0.9736 | 0.8742 | -0.0994 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | LIBERTY3 | 0.9655 | 0.8742 | -0.0913 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | LIBERTY3 | 0.9744 | 0.8742 | -0.1002 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | GOODCTY3 | 0.9736 | 0.8742 | -0.0994 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | LIBERTY3 | 0.9655 | 0.8742 | -0.0913 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | LIBERTY3 | 0.9744 | 0.8742 | -0.1002 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | GOODCTY3 | 0.9736 | 0.8742 | -0.0994 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | LIBERTY3 | 0.9655 | 0.8742 | -0.0913 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | LIBERTY3 | 0.9744 | 0.8742 | -0.1002 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | SELKIRK3 | 0.9701 | 0.8748 | -0.0953 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | SELKIRK3 | 0.9701 | 0.8748 | -0.0953 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | SELKIRK3 | 0.9701 | 0.8748 | -0.0953 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | SELKIRK3 | 0.9701 | 0.8748 | -0.0953 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | SELKIRK3 | 0.9701 | 0.8748 | -0.0953 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | SELKIRK3 | 0.9701 | 0.8748 | -0.0953 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | SELKIRK3 | 0.9701 | 0.8748 | -0.0953 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | SELKIRK3 | 0.9701 | 0.8748 | -0.0953 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | SELKIRK3 | 0.9701 | 0.8748 | -0.0953 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | SELKIRK3 | 0.9701 | 0.8748 | -0.0953 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | SELKIRK3 | 0.9701 | 0.8748 | -0.0953 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | SELKIRK3 | 0.9701 | 0.8748 | -0.0953 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | SELKIRK3 | 0.9701 | 0.8748 | -0.0953 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | SELKIRK3 | 0.9701 | 0.8748 | -0.0953 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | SELKIRK3 | 0.9701 | 0.8748 | -0.0953 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | SELKIRK3 | 0.9701 | 0.8748 | -0.0953 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | SELKIRK3 | 0.9701 | 0.8748 | -0.0953 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | SELKIRK3 | 0.9701 | 0.8748 | -0.0953 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | SELKIRK3 | 0.9701 | 0.8748 | -0.0953 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | SELKIRK3 | 0.9701 | 0.8748 | -0.0953 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | SELKIRK3 | 0.9701 | 0.8748 | -0.0953 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | SELKIRK3 | 0.9701 | 0.8748 | -0.0953 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | SELKIRK3 | 0.9701 | 0.8748 | -0.0953 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | SELKIRK3 | 0.9701 | 0.8748 | -0.0953 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | SELKIRK3 | 0.9701 | 0.8748 | -0.0953 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | SELKIRK3 | 0.9701 | 0.8748 | -0.0953 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | SELKIRK3 | 0.9701 | 0.8748 | -0.0953 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | GOODLND3 | 0.9779 | 0.8749 | -0.103 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | GOODLND3 | 0.9823 | 0.8749 | -0.1074 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | GOODLND3 | 0.9779 | 0.8749 | -0.103 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | GOODLND3 | 0.9823 | 0.8749 | -0.1074 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | GOODLND3 | 0.9779 | 0.8749 | -0.103 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | GOODLND3 | 0.9823 | 0.8749 | -0.1074 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | GOODLND3 | 0.9779 | 0.8749 | -0.103 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | GOODLND3 | 0.9823 | 0.8749 | -0.1074 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | GOODLND3 | 0.9779 | 0.8749 | -0.103 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | GOODLND3 | 0.9823 | 0.8749 | -0.1074 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | GOODLND3 | 0.9779 | 0.8749 | -0.103 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | GOODLND3 | 0.9823 | 0.8749 | -0.1074 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | GOODLND3 | 0.9779 | 0.8749 | -0.103 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | GOODLND3 | 0.9823 | 0.8749 | -0.1074 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | GOODLND3 | 0.9779 | 0.8749 | -0.103 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | GOODLND3 | 0.9823 | 0.8749 | -0.1074 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | GOODLND3 | 0.9779 | 0.8749 | -0.103 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | GOODLND3 | 0.9823 | 0.8749 | -0.1074 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | GOODLND3 | 0.9779 | 0.8749 | -0.103 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | GOODLND3 | 0.9823 | 0.8749 | -0.1074 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | GOODLND3 | 0.9779 | 0.8749 | -0.103 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | GOODLND3 | 0.9823 | 0.8749 | -0.1074 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | GOODLND3 | 0.9779 | 0.8749 | -0.103 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | GOODLND3 | 0.9823 | 0.8749 | -0.1074 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | GOODLND3 | 0.9779 | 0.8749 | -0.103 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | GOODLND3 | 0.9823 | 0.8749 | -0.1074 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | GOODLND3 | 0.9779 | 0.8749 | -0.103 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | GOODLND3 | 0.9823 | 0.8749 | -0.1074 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | GOODLND3 | 0.9779 | 0.8749 | -0.103 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | GOODLND3 | 0.9823 | 0.8749 | -0.1074 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | GOODLND3 | 0.9779 | 0.8749 | -0.103 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | GOODLND3 | 0.9823 | 0.8749 | -0.1074 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | GOODLND3 | 0.9779 | 0.8749 | -0.103 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | GOODLND3 | 0.9823 | 0.8749 | -0.1074 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | GOODLND3 | 0.9779 | 0.8749 | -0.103 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | GOODLND3 | 0.9823 | 0.8749 | -0.1074 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | GOODLND3 | 0.9779 | 0.8749 | -0.103 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | GOODLND3 | 0.9823 | 0.8749 | -0.1074 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | GOODLND3 | 0.9779 | 0.8749 | -0.103 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | GOODLND3 | 0.9823 | 0.8749 | -0.1074 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | GOODLND3 | 0.9779 | 0.8749 | -0.103 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | GOODLND3 | 0.9823 | 0.8749 | -0.1074 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | GOODLND3 | 0.9779 | 0.8749 | -0.103 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | GOODLND3 | 0.9823 | 0.8749 | -0.1074 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | GOODLND3 | 0.9779 | 0.8749 | -0.103 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | GOODLND3 | 0.9823 | 0.8749 | -0.1074 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | GOODLND3 | 0.9779 | 0.8749 | -0.103 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | GOODLND3 | 0.9823 | 0.8749 | -0.1074 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | GOODLND3 | 0.9779 | 0.8749 | -0.103 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | GOODLND3 | 0.9823 | 0.8749 | -0.1074 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | GOODLND3 | 0.9779 | 0.8749 | -0.103 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | GOODLND3 | 0.9823 | 0.8749 | -0.1074 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | GOODLND3 | 0.9779 | 0.8749 | -0.103 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | GOODLND3 | 0.9823 | 0.8749 | -0.1074 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | RANSOM 3 | 0.9806 | 0.8754 | -0.1052 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | RANSOM 3 | 0.986 | 0.8754 | -0.1106 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | RANSOM 3 | 0.9806 | 0.8754 | -0.1052 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | RANSOM 3 | 0.986 | 0.8754 | -0.1106 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | RANSOM 3 | 0.9806 | 0.8754 | -0.1052 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | RANSOM 3 | 0.986 | 0.8754 | -0.1106 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | RANSOM 3 | 0.9806 | 0.8754 | -0.1052 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | RANSOM 3 | 0.986 | 0.8754 | -0.1106 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | RANSOM 3 | 0.9806 | 0.8754 | -0.1052 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | RANSOM 3 | 0.986 | 0.8754 | -0.1106 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | RANSOM 3 | 0.9806 | 0.8754 | -0.1052 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | RANSOM 3 | 0.986 | 0.8754 | -0.1106 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | RANSOM 3 | 0.9806 | 0.8754 | -0.1052 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | RANSOM 3 | 0.986 | 0.8754 | -0.1106 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | RANSOM 3 | 0.9806 | 0.8754 | -0.1052 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | RANSOM 3 | 0.986 | 0.8754 | -0.1106 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | RANSOM 3 | 0.9806 | 0.8754 | -0.1052 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | RANSOM 3 | 0.986 | 0.8754 | -0.1106 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | RANSOM 3 | 0.9806 | 0.8754 | -0.1052 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | RANSOM 3 | 0.986 | 0.8754 | -0.1106 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | RANSOM 3 | 0.9806 | 0.8754 | -0.1052 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | RANSOM 3 | 0.986 | 0.8754 | -0.1106 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | RANSOM 3 | 0.9806 | 0.8754 | -0.1052 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | RANSOM 3 | 0.986 | 0.8754 | -0.1106 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | RANSOM 3 | 0.9806 | 0.8754 | -0.1052 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | RANSOM 3 | 0.986 | 0.8754 | -0.1106 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | RANSOM 3 | 0.9806 | 0.8754 | -0.1052 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | RANSOM 3 | 0.986 | 0.8754 | -0.1106 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | RANSOM 3 | 0.9806 | 0.8754 | -0.1052 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | RANSOM 3 | 0.986 | 0.8754 | -0.1106 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | RANSOM 3 | 0.9806 | 0.8754 | -0.1052 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | RANSOM 3 | 0.986 | 0.8754 | -0.1106 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | RANSOM 3 | 0.9806 | 0.8754 | -0.1052 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | RANSOM 3 | 0.986 | 0.8754 | -0.1106 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | RANSOM 3 | 0.9806 | 0.8754 | -0.1052 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | RANSOM 3 | 0.986 | 0.8754 | -0.1106 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | RANSOM 3 | 0.9806 | 0.8754 | -0.1052 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | RANSOM 3 | 0.986 | 0.8754 | -0.1106 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | RANSOM 3 | 0.9806 | 0.8754 | -0.1052 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | RANSOM 3 | 0.986 | 0.8754 | -0.1106 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | RANSOM 3 | 0.9806 | 0.8754 | -0.1052 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | RANSOM 3 | 0.986 | 0.8754 | -0.1106 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | RANSOM 3 | 0.9806 | 0.8754 | -0.1052 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | RANSOM 3 | 0.986 | 0.8754 | -0.1106 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | RANSOM 3 | 0.9806 | 0.8754 | -0.1052 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | RANSOM 3 | 0.986 | 0.8754 | -0.1106 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | RANSOM 3 | 0.9806 | 0.8754 | -0.1052 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | RANSOM 3 | 0.986 | 0.8754 | -0.1106 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | RANSOM 3 | 0.9806 | 0.8754 | -0.1052 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | RANSOM 3 | 0.986 | 0.8754 | -0.1106 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | RANSOM 3 | 0.9806 | 0.8754 | -0.1052 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | RANSOM 3 | 0.986 | 0.8754 | -0.1106 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | RANSOM 3 | 0.9806 | 0.8754 | -0.1052 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | RANSOM 3 | 0.986 | 0.8754 | -0.1106 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | LIBERTYT | 0.9651 | 0.8756 | -0.0895 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | LIBERTYT | 0.9747 | 0.8756 | -0.0991 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | BEELER 3 | 0.9699 | 0.8756 | -0.0943 |  | 0.9 | 1.05 | 0.05095 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | LIBERTYT | 0.9651 | 0.8756 | -0.0895 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | LIBERTYT | 0.9747 | 0.8756 | -0.0991 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | BEELER 3 | 0.9699 | 0.8756 | -0.0943 |  | 0.9 | 1.05 | 0.04905 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | LIBERTYT | 0.9651 | 0.8756 | -0.0895 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | LIBERTYT | 0.9747 | 0.8756 | -0.0991 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | BEELER 3 | 0.9699 | 0.8756 | -0.0943 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | LIBERTYT | 0.9651 | 0.8756 | -0.0895 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | LIBERTYT | 0.9747 | 0.8756 | -0.0991 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | BEELER 3 | 0.9699 | 0.8756 | -0.0943 |  | 0.9 | 1.05 | 0.04262 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | LIBERTYT | 0.9651 | 0.8756 | -0.0895 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | LIBERTYT | 0.9747 | 0.8756 | -0.0991 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | BEELER 3 | 0.9699 | 0.8756 | -0.0943 |  | 0.9 | 1.05 | 0.0627 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | LIBERTYT | 0.9651 | 0.8756 | -0.0895 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | LIBERTYT | 0.9747 | 0.8756 | -0.0991 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | BEELER 3 | 0.9699 | 0.8756 | -0.0943 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | LIBERTYT | 0.9651 | 0.8756 | -0.0895 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | LIBERTYT | 0.9747 | 0.8756 | -0.0991 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | BEELER 3 | 0.9699 | 0.8756 | -0.0943 |  | 0.9 | 1.05 | 0.05043 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | LIBERTYT | 0.9651 | 0.8756 | -0.0895 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | LIBERTYT | 0.9747 | 0.8756 | -0.0991 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | BEELER 3 | 0.9699 | 0.8756 | -0.0943 |  | 0.9 | 1.05 | 0.05292 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | LIBERTYT | 0.9651 | 0.8756 | -0.0895 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | LIBERTYT | 0.9747 | 0.8756 | -0.0991 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | BEELER 3 | 0.9699 | 0.8756 | -0.0943 |  | 0.9 | 1.05 | 0.0444 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | LIBERTYT | 0.9651 | 0.8756 | -0.0895 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | LIBERTYT | 0.9747 | 0.8756 | -0.0991 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | BEELER 3 | 0.9699 | 0.8756 | -0.0943 |  | 0.9 | 1.05 | 0.04788 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | LIBERTYT | 0.9651 | 0.8756 | -0.0895 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | LIBERTYT | 0.9747 | 0.8756 | -0.0991 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | BEELER 3 | 0.9699 | 0.8756 | -0.0943 |  | 0.9 | 1.05 | 0.05824 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | LIBERTYT | 0.9651 | 0.8756 | -0.0895 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | LIBERTYT | 0.9747 | 0.8756 | -0.0991 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | BEELER 3 | 0.9699 | 0.8756 | -0.0943 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | LIBERTYT | 0.9651 | 0.8756 | -0.0895 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | LIBERTYT | 0.9747 | 0.8756 | -0.0991 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | BEELER 3 | 0.9699 | 0.8756 | -0.0943 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | LIBERTYT | 0.9651 | 0.8756 | -0.0895 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | LIBERTYT | 0.9747 | 0.8756 | -0.0991 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | BEELER 3 | 0.9699 | 0.8756 | -0.0943 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | LIBERTYT | 0.9651 | 0.8756 | -0.0895 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | LIBERTYT | 0.9747 | 0.8756 | -0.0991 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | BEELER 3 | 0.9699 | 0.8756 | -0.0943 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | LIBERTYT | 0.9651 | 0.8756 | -0.0895 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | LIBERTYT | 0.9747 | 0.8756 | -0.0991 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | BEELER 3 | 0.9699 | 0.8756 | -0.0943 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | LIBERTYT | 0.9651 | 0.8756 | -0.0895 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | LIBERTYT | 0.9747 | 0.8756 | -0.0991 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | BEELER 3 | 0.9699 | 0.8756 | -0.0943 |  | 0.9 | 1.05 | 0.04773 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | LIBERTYT | 0.9651 | 0.8756 | -0.0895 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | LIBERTYT | 0.9747 | 0.8756 | -0.0991 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | BEELER 3 | 0.9699 | 0.8756 | -0.0943 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | LIBERTYT | 0.9651 | 0.8756 | -0.0895 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | LIBERTYT | 0.9747 | 0.8756 | -0.0991 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | BEELER 3 | 0.9699 | 0.8756 | -0.0943 |  | 0.9 | 1.05 | 0.0348 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | LIBERTYT | 0.9651 | 0.8756 | -0.0895 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | LIBERTYT | 0.9747 | 0.8756 | -0.0991 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | BEELER 3 | 0.9699 | 0.8756 | -0.0943 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | LIBERTYT | 0.9651 | 0.8756 | -0.0895 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | LIBERTYT | 0.9747 | 0.8756 | -0.0991 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | BEELER 3 | 0.9699 | 0.8756 | -0.0943 |  | 0.9 | 1.05 | 0.04996 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | LIBERTYT | 0.9651 | 0.8756 | -0.0895 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | LIBERTYT | 0.9747 | 0.8756 | -0.0991 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | BEELER 3 | 0.9699 | 0.8756 | -0.0943 |  | 0.9 | 1.05 | 0.04835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | LIBERTYT | 0.9651 | 0.8756 | -0.0895 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | LIBERTYT | 0.9747 | 0.8756 | -0.0991 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | BEELER 3 | 0.9699 | 0.8756 | -0.0943 |  | 0.9 | 1.05 | 0.05448 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | LIBERTYT | 0.9651 | 0.8756 | -0.0895 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | LIBERTYT | 0.9747 | 0.8756 | -0.0991 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | BEELER 3 | 0.9699 | 0.8756 | -0.0943 |  | 0.9 | 1.05 | 0.05382 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | LIBERTYT | 0.9651 | 0.8756 | -0.0895 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | LIBERTYT | 0.9747 | 0.8756 | -0.0991 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | BEELER 3 | 0.9699 | 0.8756 | -0.0943 |  | 0.9 | 1.05 | 0.03774 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | LIBERTYT | 0.9651 | 0.8756 | -0.0895 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | LIBERTYT | 0.9747 | 0.8756 | -0.0991 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | BEELER 3 | 0.9699 | 0.8756 | -0.0943 |  | 0.9 | 1.05 | 0.04948 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | LIBERTYT | 0.9651 | 0.8756 | -0.0895 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | LIBERTYT | 0.9747 | 0.8756 | -0.0991 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | BEELER 3 | 0.9699 | 0.8756 | -0.0943 |  | 0.9 | 1.05 | 0.04054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | PALMER3 | 0.9764 | 0.8758 | -0.1006 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | PALMER3 | 0.984 | 0.8758 | -0.1082 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | PALMER3 | 0.9764 | 0.8758 | -0.1006 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | PALMER3 | 0.984 | 0.8758 | -0.1082 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | PALMER3 | 0.9764 | 0.8758 | -0.1006 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | PALMER3 | 0.984 | 0.8758 | -0.1082 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | PALMER3 | 0.9764 | 0.8758 | -0.1006 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | PALMER3 | 0.984 | 0.8758 | -0.1082 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | PALMER3 | 0.9764 | 0.8758 | -0.1006 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | PALMER3 | 0.984 | 0.8758 | -0.1082 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | PALMER3 | 0.9764 | 0.8758 | -0.1006 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | PALMER3 | 0.984 | 0.8758 | -0.1082 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | PALMER3 | 0.9764 | 0.8758 | -0.1006 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | PALMER3 | 0.984 | 0.8758 | -0.1082 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | PALMER3 | 0.9764 | 0.8758 | -0.1006 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | PALMER3 | 0.984 | 0.8758 | -0.1082 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | PALMER3 | 0.9764 | 0.8758 | -0.1006 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | PALMER3 | 0.984 | 0.8758 | -0.1082 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | PALMER3 | 0.9764 | 0.8758 | -0.1006 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | PALMER3 | 0.984 | 0.8758 | -0.1082 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | PALMER3 | 0.9764 | 0.8758 | -0.1006 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | PALMER3 | 0.984 | 0.8758 | -0.1082 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | PALMER3 | 0.9764 | 0.8758 | -0.1006 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | PALMER3 | 0.984 | 0.8758 | -0.1082 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | PALMER3 | 0.9764 | 0.8758 | -0.1006 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | PALMER3 | 0.984 | 0.8758 | -0.1082 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | PALMER3 | 0.9764 | 0.8758 | -0.1006 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | PALMER3 | 0.984 | 0.8758 | -0.1082 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | PALMER3 | 0.9764 | 0.8758 | -0.1006 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | PALMER3 | 0.984 | 0.8758 | -0.1082 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | PALMER3 | 0.9764 | 0.8758 | -0.1006 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | PALMER3 | 0.984 | 0.8758 | -0.1082 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | PALMER3 | 0.9764 | 0.8758 | -0.1006 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | PALMER3 | 0.984 | 0.8758 | -0.1082 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | PALMER3 | 0.9764 | 0.8758 | -0.1006 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | PALMER3 | 0.984 | 0.8758 | -0.1082 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | PALMER3 | 0.9764 | 0.8758 | -0.1006 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | PALMER3 | 0.984 | 0.8758 | -0.1082 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | PALMER3 | 0.9764 | 0.8758 | -0.1006 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | PALMER3 | 0.984 | 0.8758 | -0.1082 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | PALMER3 | 0.9764 | 0.8758 | -0.1006 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | PALMER3 | 0.984 | 0.8758 | -0.1082 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | PALMER3 | 0.9764 | 0.8758 | -0.1006 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | PALMER3 | 0.984 | 0.8758 | -0.1082 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | PALMER3 | 0.9764 | 0.8758 | -0.1006 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | PALMER3 | 0.984 | 0.8758 | -0.1082 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | PALMER3 | 0.9764 | 0.8758 | -0.1006 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | PALMER3 | 0.984 | 0.8758 | -0.1082 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | PALMER3 | 0.9764 | 0.8758 | -0.1006 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | PALMER3 | 0.984 | 0.8758 | -0.1082 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | PALMER3 | 0.9764 | 0.8758 | -0.1006 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | PALMER3 | 0.984 | 0.8758 | -0.1082 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | PALMER3 | 0.9764 | 0.8758 | -0.1006 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | PALMER3 | 0.984 | 0.8758 | -0.1082 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.10414 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.10414 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.0987 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.0987 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.08024 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.08024 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.14298 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.14298 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.10266 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.10266 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.11064 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.11064 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.08095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.08095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.09571 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.09571 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.12796 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.12796 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.09379 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.09379 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.09379 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.09379 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.09507 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.09507 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.10446 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.10446 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.05698 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.05698 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.09445 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.09445 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.10129 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.10129 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.0967 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.0967 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.11534 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.11534 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.11336 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.11336 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.06542 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.06542 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.09991 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.09991 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.0742 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | GRANT 3 | 1.0014 | 0.8767 | -0.1247 |  | 0.9 | 1.05 | 0.0742 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.10414 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.10414 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.0987 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.0987 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.08024 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.08024 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.14298 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.14298 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.10266 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.10266 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.11064 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.11064 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.08095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.08095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.09571 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.09571 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.12796 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.12796 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.09379 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.09379 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.09379 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.09379 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.09507 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.09507 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.10446 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.10446 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.05698 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.05698 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.09445 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.09445 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.10129 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.10129 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.0967 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.0967 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.11534 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.11534 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.11336 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.11336 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.06542 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.06542 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.09991 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.09991 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.0742 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | GRANTTP3 | 1.0017 | 0.877 | -0.1247 |  | 0.9 | 1.05 | 0.0742 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | LIBERTY3 | 0.9655 | 0.8771 | -0.0884 |  | 0.9 | 1.05 | 0.05095 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | LIBERTY3 | 0.9655 | 0.8771 | -0.0884 |  | 0.9 | 1.05 | 0.04905 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | LIBERTY3 | 0.9655 | 0.8771 | -0.0884 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | LIBERTY3 | 0.9655 | 0.8771 | -0.0884 |  | 0.9 | 1.05 | 0.04262 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | LIBERTY3 | 0.9655 | 0.8771 | -0.0884 |  | 0.9 | 1.05 | 0.0627 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | LIBERTY3 | 0.9655 | 0.8771 | -0.0884 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | LIBERTY3 | 0.9655 | 0.8771 | -0.0884 |  | 0.9 | 1.05 | 0.05043 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | LIBERTY3 | 0.9655 | 0.8771 | -0.0884 |  | 0.9 | 1.05 | 0.05292 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | LIBERTY3 | 0.9655 | 0.8771 | -0.0884 |  | 0.9 | 1.05 | 0.0444 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | LIBERTY3 | 0.9655 | 0.8771 | -0.0884 |  | 0.9 | 1.05 | 0.04788 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | LIBERTY3 | 0.9655 | 0.8771 | -0.0884 |  | 0.9 | 1.05 | 0.05824 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | LIBERTY3 | 0.9655 | 0.8771 | -0.0884 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | LIBERTY3 | 0.9655 | 0.8771 | -0.0884 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | LIBERTY3 | 0.9655 | 0.8771 | -0.0884 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | LIBERTY3 | 0.9655 | 0.8771 | -0.0884 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | LIBERTY3 | 0.9655 | 0.8771 | -0.0884 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | LIBERTY3 | 0.9655 | 0.8771 | -0.0884 |  | 0.9 | 1.05 | 0.04773 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | LIBERTY3 | 0.9655 | 0.8771 | -0.0884 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | LIBERTY3 | 0.9655 | 0.8771 | -0.0884 |  | 0.9 | 1.05 | 0.0348 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | LIBERTY3 | 0.9655 | 0.8771 | -0.0884 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | LIBERTY3 | 0.9655 | 0.8771 | -0.0884 |  | 0.9 | 1.05 | 0.04996 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | LIBERTY3 | 0.9655 | 0.8771 | -0.0884 |  | 0.9 | 1.05 | 0.04835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | LIBERTY3 | 0.9655 | 0.8771 | -0.0884 |  | 0.9 | 1.05 | 0.05448 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | LIBERTY3 | 0.9655 | 0.8771 | -0.0884 |  | 0.9 | 1.05 | 0.05382 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | LIBERTY3 | 0.9655 | 0.8771 | -0.0884 |  | 0.9 | 1.05 | 0.03774 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | LIBERTY3 | 0.9655 | 0.8771 | -0.0884 |  | 0.9 | 1.05 | 0.04948 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | LIBERTY3 | 0.9655 | 0.8771 | -0.0884 |  | 0.9 | 1.05 | 0.04054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | GANO 3 | 0.9659 | 0.8772 | -0.0887 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | GANO 3 | 0.9659 | 0.8772 | -0.0887 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | GANO 3 | 0.9659 | 0.8772 | -0.0887 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | GANO 3 | 0.9659 | 0.8772 | -0.0887 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | GANO 3 | 0.9659 | 0.8772 | -0.0887 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | GANO 3 | 0.9659 | 0.8772 | -0.0887 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | GANO 3 | 0.9659 | 0.8772 | -0.0887 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | GANO 3 | 0.9659 | 0.8772 | -0.0887 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | GANO 3 | 0.9659 | 0.8772 | -0.0887 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | GANO 3 | 0.9659 | 0.8772 | -0.0887 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | GANO 3 | 0.9659 | 0.8772 | -0.0887 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | GANO 3 | 0.9659 | 0.8772 | -0.0887 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | GANO 3 | 0.9659 | 0.8772 | -0.0887 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | GANO 3 | 0.9659 | 0.8772 | -0.0887 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | GANO 3 | 0.9659 | 0.8772 | -0.0887 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | GANO 3 | 0.9659 | 0.8772 | -0.0887 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | GANO 3 | 0.9659 | 0.8772 | -0.0887 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | GANO 3 | 0.9659 | 0.8772 | -0.0887 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | GANO 3 | 0.9659 | 0.8772 | -0.0887 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | GANO 3 | 0.9659 | 0.8772 | -0.0887 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | GANO 3 | 0.9659 | 0.8772 | -0.0887 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | GANO 3 | 0.9659 | 0.8772 | -0.0887 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | GANO 3 | 0.9659 | 0.8772 | -0.0887 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | GANO 3 | 0.9659 | 0.8772 | -0.0887 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | GANO 3 | 0.9659 | 0.8772 | -0.0887 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | GANO 3 | 0.9659 | 0.8772 | -0.0887 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | GANO 3 | 0.9659 | 0.8772 | -0.0887 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | CHASE 3 | 0.9603 | 0.8773 | -0.083 |  | 0.9 | 1.05 | 0.05101 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | SHARNSP3 | 0.9604 | 0.8773 | -0.0831 |  | 0.9 | 1.05 | 0.05101 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | LEOTI 3 | 0.9706 | 0.8773 | -0.0933 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | CHASE 3 | 0.9603 | 0.8773 | -0.083 |  | 0.9 | 1.05 | 0.04911 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | SHARNSP3 | 0.9604 | 0.8773 | -0.0831 |  | 0.9 | 1.05 | 0.04911 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | LEOTI 3 | 0.9706 | 0.8773 | -0.0933 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | CHASE 3 | 0.9603 | 0.8773 | -0.083 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | SHARNSP3 | 0.9604 | 0.8773 | -0.0831 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | LEOTI 3 | 0.9706 | 0.8773 | -0.0933 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | CHASE 3 | 0.9603 | 0.8773 | -0.083 |  | 0.9 | 1.05 | 0.04272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | SHARNSP3 | 0.9604 | 0.8773 | -0.0831 |  | 0.9 | 1.05 | 0.04272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | LEOTI 3 | 0.9706 | 0.8773 | -0.0933 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | CHASE 3 | 0.9603 | 0.8773 | -0.083 |  | 0.9 | 1.05 | 0.06272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | SHARNSP3 | 0.9604 | 0.8773 | -0.0831 |  | 0.9 | 1.05 | 0.06272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | LEOTI 3 | 0.9706 | 0.8773 | -0.0933 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | CHASE 3 | 0.9603 | 0.8773 | -0.083 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | SHARNSP3 | 0.9604 | 0.8773 | -0.0831 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | LEOTI 3 | 0.9706 | 0.8773 | -0.0933 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | CHASE 3 | 0.9603 | 0.8773 | -0.083 |  | 0.9 | 1.05 | 0.05049 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | SHARNSP3 | 0.9604 | 0.8773 | -0.0831 |  | 0.9 | 1.05 | 0.05049 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | LEOTI 3 | 0.9706 | 0.8773 | -0.0933 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | CHASE 3 | 0.9603 | 0.8773 | -0.083 |  | 0.9 | 1.05 | 0.05297 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | SHARNSP3 | 0.9604 | 0.8773 | -0.0831 |  | 0.9 | 1.05 | 0.05297 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | LEOTI 3 | 0.9706 | 0.8773 | -0.0933 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | CHASE 3 | 0.9603 | 0.8773 | -0.083 |  | 0.9 | 1.05 | 0.04447 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | SHARNSP3 | 0.9604 | 0.8773 | -0.0831 |  | 0.9 | 1.05 | 0.04447 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | LEOTI 3 | 0.9706 | 0.8773 | -0.0933 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | CHASE 3 | 0.9603 | 0.8773 | -0.083 |  | 0.9 | 1.05 | 0.04795 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | SHARNSP3 | 0.9604 | 0.8773 | -0.0831 |  | 0.9 | 1.05 | 0.04795 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | LEOTI 3 | 0.9706 | 0.8773 | -0.0933 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | CHASE 3 | 0.9603 | 0.8773 | -0.083 |  | 0.9 | 1.05 | 0.05827 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | SHARNSP3 | 0.9604 | 0.8773 | -0.0831 |  | 0.9 | 1.05 | 0.05827 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | LEOTI 3 | 0.9706 | 0.8773 | -0.0933 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | CHASE 3 | 0.9603 | 0.8773 | -0.083 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | SHARNSP3 | 0.9604 | 0.8773 | -0.0831 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | LEOTI 3 | 0.9706 | 0.8773 | -0.0933 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | CHASE 3 | 0.9603 | 0.8773 | -0.083 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | SHARNSP3 | 0.9604 | 0.8773 | -0.0831 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | LEOTI 3 | 0.9706 | 0.8773 | -0.0933 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | CHASE 3 | 0.9603 | 0.8773 | -0.083 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | SHARNSP3 | 0.9604 | 0.8773 | -0.0831 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | LEOTI 3 | 0.9706 | 0.8773 | -0.0933 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | CHASE 3 | 0.9603 | 0.8773 | -0.083 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | SHARNSP3 | 0.9604 | 0.8773 | -0.0831 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | LEOTI 3 | 0.9706 | 0.8773 | -0.0933 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | CHASE 3 | 0.9603 | 0.8773 | -0.083 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | SHARNSP3 | 0.9604 | 0.8773 | -0.0831 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | LEOTI 3 | 0.9706 | 0.8773 | -0.0933 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | CHASE 3 | 0.9603 | 0.8773 | -0.083 |  | 0.9 | 1.05 | 0.04781 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | SHARNSP3 | 0.9604 | 0.8773 | -0.0831 |  | 0.9 | 1.05 | 0.04781 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | LEOTI 3 | 0.9706 | 0.8773 | -0.0933 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | CHASE 3 | 0.9603 | 0.8773 | -0.083 |  | 0.9 | 1.05 | 0.05112 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | SHARNSP3 | 0.9604 | 0.8773 | -0.0831 |  | 0.9 | 1.05 | 0.05112 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | LEOTI 3 | 0.9706 | 0.8773 | -0.0933 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | CHASE 3 | 0.9603 | 0.8773 | -0.083 |  | 0.9 | 1.05 | 0.03494 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | SHARNSP3 | 0.9604 | 0.8773 | -0.0831 |  | 0.9 | 1.05 | 0.03494 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | LEOTI 3 | 0.9706 | 0.8773 | -0.0933 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | CHASE 3 | 0.9603 | 0.8773 | -0.083 |  | 0.9 | 1.05 | 0.04759 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | SHARNSP3 | 0.9604 | 0.8773 | -0.0831 |  | 0.9 | 1.05 | 0.04759 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | LEOTI 3 | 0.9706 | 0.8773 | -0.0933 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | CHASE 3 | 0.9603 | 0.8773 | -0.083 |  | 0.9 | 1.05 | 0.05002 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | SHARNSP3 | 0.9604 | 0.8773 | -0.0831 |  | 0.9 | 1.05 | 0.05002 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | LEOTI 3 | 0.9706 | 0.8773 | -0.0933 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | CHASE 3 | 0.9603 | 0.8773 | -0.083 |  | 0.9 | 1.05 | 0.04842 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | SHARNSP3 | 0.9604 | 0.8773 | -0.0831 |  | 0.9 | 1.05 | 0.04842 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | LEOTI 3 | 0.9706 | 0.8773 | -0.0933 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | CHASE 3 | 0.9603 | 0.8773 | -0.083 |  | 0.9 | 1.05 | 0.05452 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | SHARNSP3 | 0.9604 | 0.8773 | -0.0831 |  | 0.9 | 1.05 | 0.05452 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | LEOTI 3 | 0.9706 | 0.8773 | -0.0933 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | CHASE 3 | 0.9603 | 0.8773 | -0.083 |  | 0.9 | 1.05 | 0.05387 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | SHARNSP3 | 0.9604 | 0.8773 | -0.0831 |  | 0.9 | 1.05 | 0.05387 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | LEOTI 3 | 0.9706 | 0.8773 | -0.0933 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | CHASE 3 | 0.9603 | 0.8773 | -0.083 |  | 0.9 | 1.05 | 0.03786 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | SHARNSP3 | 0.9604 | 0.8773 | -0.0831 |  | 0.9 | 1.05 | 0.03786 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | LEOTI 3 | 0.9706 | 0.8773 | -0.0933 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | CHASE 3 | 0.9603 | 0.8773 | -0.083 |  | 0.9 | 1.05 | 0.04954 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | SHARNSP3 | 0.9604 | 0.8773 | -0.0831 |  | 0.9 | 1.05 | 0.04954 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | LEOTI 3 | 0.9706 | 0.8773 | -0.0933 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | CHASE 3 | 0.9603 | 0.8773 | -0.083 |  | 0.9 | 1.05 | 0.04065 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | SHARNSP3 | 0.9604 | 0.8773 | -0.0831 |  | 0.9 | 1.05 | 0.04065 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | LEOTI 3 | 0.9706 | 0.8773 | -0.0933 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | CSTFRAN3 | 0.9837 | 0.8775 | -0.1062 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | CSTFRAN3 | 0.9873 | 0.8775 | -0.1098 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | CSTFRAN3 | 0.9837 | 0.8775 | -0.1062 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | CSTFRAN3 | 0.9873 | 0.8775 | -0.1098 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | CSTFRAN3 | 0.9837 | 0.8775 | -0.1062 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | CSTFRAN3 | 0.9873 | 0.8775 | -0.1098 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | CSTFRAN3 | 0.9837 | 0.8775 | -0.1062 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | CSTFRAN3 | 0.9873 | 0.8775 | -0.1098 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | CSTFRAN3 | 0.9837 | 0.8775 | -0.1062 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | CSTFRAN3 | 0.9873 | 0.8775 | -0.1098 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | CSTFRAN3 | 0.9837 | 0.8775 | -0.1062 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | CSTFRAN3 | 0.9873 | 0.8775 | -0.1098 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | CSTFRAN3 | 0.9837 | 0.8775 | -0.1062 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | CSTFRAN3 | 0.9873 | 0.8775 | -0.1098 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | CSTFRAN3 | 0.9837 | 0.8775 | -0.1062 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | CSTFRAN3 | 0.9873 | 0.8775 | -0.1098 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | CSTFRAN3 | 0.9837 | 0.8775 | -0.1062 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | CSTFRAN3 | 0.9873 | 0.8775 | -0.1098 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | CSTFRAN3 | 0.9837 | 0.8775 | -0.1062 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | CSTFRAN3 | 0.9873 | 0.8775 | -0.1098 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | CSTFRAN3 | 0.9837 | 0.8775 | -0.1062 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | CSTFRAN3 | 0.9873 | 0.8775 | -0.1098 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | CSTFRAN3 | 0.9837 | 0.8775 | -0.1062 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | CSTFRAN3 | 0.9873 | 0.8775 | -0.1098 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | CSTFRAN3 | 0.9837 | 0.8775 | -0.1062 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | CSTFRAN3 | 0.9873 | 0.8775 | -0.1098 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | CSTFRAN3 | 0.9837 | 0.8775 | -0.1062 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | CSTFRAN3 | 0.9873 | 0.8775 | -0.1098 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | CSTFRAN3 | 0.9837 | 0.8775 | -0.1062 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | CSTFRAN3 | 0.9873 | 0.8775 | -0.1098 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | CSTFRAN3 | 0.9837 | 0.8775 | -0.1062 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | CSTFRAN3 | 0.9873 | 0.8775 | -0.1098 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | CSTFRAN3 | 0.9837 | 0.8775 | -0.1062 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | CSTFRAN3 | 0.9873 | 0.8775 | -0.1098 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | CSTFRAN3 | 0.9837 | 0.8775 | -0.1062 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | CSTFRAN3 | 0.9873 | 0.8775 | -0.1098 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | CSTFRAN3 | 0.9837 | 0.8775 | -0.1062 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | CSTFRAN3 | 0.9873 | 0.8775 | -0.1098 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | CSTFRAN3 | 0.9837 | 0.8775 | -0.1062 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | CSTFRAN3 | 0.9873 | 0.8775 | -0.1098 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | CSTFRAN3 | 0.9837 | 0.8775 | -0.1062 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | CSTFRAN3 | 0.9873 | 0.8775 | -0.1098 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | CSTFRAN3 | 0.9837 | 0.8775 | -0.1062 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | CSTFRAN3 | 0.9873 | 0.8775 | -0.1098 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | CSTFRAN3 | 0.9837 | 0.8775 | -0.1062 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | CSTFRAN3 | 0.9873 | 0.8775 | -0.1098 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | CSTFRAN3 | 0.9837 | 0.8775 | -0.1062 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | CSTFRAN3 | 0.9873 | 0.8775 | -0.1098 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | CSTFRAN3 | 0.9837 | 0.8775 | -0.1062 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | CSTFRAN3 | 0.9873 | 0.8775 | -0.1098 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | CSTFRAN3 | 0.9837 | 0.8775 | -0.1062 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | CSTFRAN3 | 0.9873 | 0.8775 | -0.1098 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | CSTFRAN3 | 0.9837 | 0.8775 | -0.1062 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | CSTFRAN3 | 0.9873 | 0.8775 | -0.1098 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | LIBERTYT | 0.9651 | 0.8776 | -0.0875 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | ARNOLD3 | 0.9827 | 0.8776 | -0.1051 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | ARNOLD3 | 0.9878 | 0.8776 | -0.1102 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | STFRANT3 | 0.9838 | 0.8776 | -0.1062 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | STFRANT3 | 0.9875 | 0.8776 | -0.1099 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | LIBERTYT | 0.9651 | 0.8776 | -0.0875 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | ARNOLD3 | 0.9827 | 0.8776 | -0.1051 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | ARNOLD3 | 0.9878 | 0.8776 | -0.1102 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | STFRANT3 | 0.9838 | 0.8776 | -0.1062 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | STFRANT3 | 0.9875 | 0.8776 | -0.1099 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | LIBERTYT | 0.9651 | 0.8776 | -0.0875 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | ARNOLD3 | 0.9827 | 0.8776 | -0.1051 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | ARNOLD3 | 0.9878 | 0.8776 | -0.1102 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | STFRANT3 | 0.9838 | 0.8776 | -0.1062 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | STFRANT3 | 0.9875 | 0.8776 | -0.1099 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | LIBERTYT | 0.9651 | 0.8776 | -0.0875 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | ARNOLD3 | 0.9827 | 0.8776 | -0.1051 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | ARNOLD3 | 0.9878 | 0.8776 | -0.1102 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | STFRANT3 | 0.9838 | 0.8776 | -0.1062 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | STFRANT3 | 0.9875 | 0.8776 | -0.1099 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | LIBERTYT | 0.9651 | 0.8776 | -0.0875 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | ARNOLD3 | 0.9827 | 0.8776 | -0.1051 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | ARNOLD3 | 0.9878 | 0.8776 | -0.1102 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | STFRANT3 | 0.9838 | 0.8776 | -0.1062 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | STFRANT3 | 0.9875 | 0.8776 | -0.1099 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | LIBERTYT | 0.9651 | 0.8776 | -0.0875 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | ARNOLD3 | 0.9827 | 0.8776 | -0.1051 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | ARNOLD3 | 0.9878 | 0.8776 | -0.1102 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | STFRANT3 | 0.9838 | 0.8776 | -0.1062 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | STFRANT3 | 0.9875 | 0.8776 | -0.1099 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | LIBERTYT | 0.9651 | 0.8776 | -0.0875 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | ARNOLD3 | 0.9827 | 0.8776 | -0.1051 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | ARNOLD3 | 0.9878 | 0.8776 | -0.1102 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | STFRANT3 | 0.9838 | 0.8776 | -0.1062 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | STFRANT3 | 0.9875 | 0.8776 | -0.1099 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | LIBERTYT | 0.9651 | 0.8776 | -0.0875 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | ARNOLD3 | 0.9827 | 0.8776 | -0.1051 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | ARNOLD3 | 0.9878 | 0.8776 | -0.1102 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | STFRANT3 | 0.9838 | 0.8776 | -0.1062 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | STFRANT3 | 0.9875 | 0.8776 | -0.1099 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | LIBERTYT | 0.9651 | 0.8776 | -0.0875 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | ARNOLD3 | 0.9827 | 0.8776 | -0.1051 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | ARNOLD3 | 0.9878 | 0.8776 | -0.1102 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | STFRANT3 | 0.9838 | 0.8776 | -0.1062 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | STFRANT3 | 0.9875 | 0.8776 | -0.1099 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | LIBERTYT | 0.9651 | 0.8776 | -0.0875 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | ARNOLD3 | 0.9827 | 0.8776 | -0.1051 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | ARNOLD3 | 0.9878 | 0.8776 | -0.1102 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | STFRANT3 | 0.9838 | 0.8776 | -0.1062 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | STFRANT3 | 0.9875 | 0.8776 | -0.1099 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | LIBERTYT | 0.9651 | 0.8776 | -0.0875 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | ARNOLD3 | 0.9827 | 0.8776 | -0.1051 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | ARNOLD3 | 0.9878 | 0.8776 | -0.1102 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | STFRANT3 | 0.9838 | 0.8776 | -0.1062 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | STFRANT3 | 0.9875 | 0.8776 | -0.1099 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | LIBERTYT | 0.9651 | 0.8776 | -0.0875 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | ARNOLD3 | 0.9827 | 0.8776 | -0.1051 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | ARNOLD3 | 0.9878 | 0.8776 | -0.1102 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | STFRANT3 | 0.9838 | 0.8776 | -0.1062 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | STFRANT3 | 0.9875 | 0.8776 | -0.1099 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | LIBERTYT | 0.9651 | 0.8776 | -0.0875 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | ARNOLD3 | 0.9827 | 0.8776 | -0.1051 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | ARNOLD3 | 0.9878 | 0.8776 | -0.1102 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | STFRANT3 | 0.9838 | 0.8776 | -0.1062 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | STFRANT3 | 0.9875 | 0.8776 | -0.1099 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | LIBERTYT | 0.9651 | 0.8776 | -0.0875 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | ARNOLD3 | 0.9827 | 0.8776 | -0.1051 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | ARNOLD3 | 0.9878 | 0.8776 | -0.1102 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | STFRANT3 | 0.9838 | 0.8776 | -0.1062 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | STFRANT3 | 0.9875 | 0.8776 | -0.1099 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | LIBERTYT | 0.9651 | 0.8776 | -0.0875 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | ARNOLD3 | 0.9827 | 0.8776 | -0.1051 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | ARNOLD3 | 0.9878 | 0.8776 | -0.1102 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | STFRANT3 | 0.9838 | 0.8776 | -0.1062 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | STFRANT3 | 0.9875 | 0.8776 | -0.1099 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | LIBERTYT | 0.9651 | 0.8776 | -0.0875 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | ARNOLD3 | 0.9827 | 0.8776 | -0.1051 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | ARNOLD3 | 0.9878 | 0.8776 | -0.1102 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | STFRANT3 | 0.9838 | 0.8776 | -0.1062 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | STFRANT3 | 0.9875 | 0.8776 | -0.1099 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | LIBERTYT | 0.9651 | 0.8776 | -0.0875 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | ARNOLD3 | 0.9827 | 0.8776 | -0.1051 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | ARNOLD3 | 0.9878 | 0.8776 | -0.1102 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | STFRANT3 | 0.9838 | 0.8776 | -0.1062 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | STFRANT3 | 0.9875 | 0.8776 | -0.1099 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | LIBERTYT | 0.9651 | 0.8776 | -0.0875 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | ARNOLD3 | 0.9827 | 0.8776 | -0.1051 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | ARNOLD3 | 0.9878 | 0.8776 | -0.1102 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | STFRANT3 | 0.9838 | 0.8776 | -0.1062 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | STFRANT3 | 0.9875 | 0.8776 | -0.1099 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | LIBERTYT | 0.9651 | 0.8776 | -0.0875 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | ARNOLD3 | 0.9827 | 0.8776 | -0.1051 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | ARNOLD3 | 0.9878 | 0.8776 | -0.1102 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | STFRANT3 | 0.9838 | 0.8776 | -0.1062 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | STFRANT3 | 0.9875 | 0.8776 | -0.1099 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | LIBERTYT | 0.9651 | 0.8776 | -0.0875 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | ARNOLD3 | 0.9827 | 0.8776 | -0.1051 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | ARNOLD3 | 0.9878 | 0.8776 | -0.1102 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | STFRANT3 | 0.9838 | 0.8776 | -0.1062 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | STFRANT3 | 0.9875 | 0.8776 | -0.1099 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | LIBERTYT | 0.9651 | 0.8776 | -0.0875 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | ARNOLD3 | 0.9827 | 0.8776 | -0.1051 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | ARNOLD3 | 0.9878 | 0.8776 | -0.1102 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | STFRANT3 | 0.9838 | 0.8776 | -0.1062 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | STFRANT3 | 0.9875 | 0.8776 | -0.1099 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | LIBERTYT | 0.9651 | 0.8776 | -0.0875 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | ARNOLD3 | 0.9827 | 0.8776 | -0.1051 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | ARNOLD3 | 0.9878 | 0.8776 | -0.1102 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | STFRANT3 | 0.9838 | 0.8776 | -0.1062 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | STFRANT3 | 0.9875 | 0.8776 | -0.1099 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | LIBERTYT | 0.9651 | 0.8776 | -0.0875 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | ARNOLD3 | 0.9827 | 0.8776 | -0.1051 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | ARNOLD3 | 0.9878 | 0.8776 | -0.1102 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | STFRANT3 | 0.9838 | 0.8776 | -0.1062 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | STFRANT3 | 0.9875 | 0.8776 | -0.1099 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | LIBERTYT | 0.9651 | 0.8776 | -0.0875 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | ARNOLD3 | 0.9827 | 0.8776 | -0.1051 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | ARNOLD3 | 0.9878 | 0.8776 | -0.1102 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | STFRANT3 | 0.9838 | 0.8776 | -0.1062 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | STFRANT3 | 0.9875 | 0.8776 | -0.1099 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | LIBERTYT | 0.9651 | 0.8776 | -0.0875 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | ARNOLD3 | 0.9827 | 0.8776 | -0.1051 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | ARNOLD3 | 0.9878 | 0.8776 | -0.1102 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | STFRANT3 | 0.9838 | 0.8776 | -0.1062 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | STFRANT3 | 0.9875 | 0.8776 | -0.1099 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | LIBERTYT | 0.9651 | 0.8776 | -0.0875 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | ARNOLD3 | 0.9827 | 0.8776 | -0.1051 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | ARNOLD3 | 0.9878 | 0.8776 | -0.1102 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | STFRANT3 | 0.9838 | 0.8776 | -0.1062 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | STFRANT3 | 0.9875 | 0.8776 | -0.1099 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | LIBERTYT | 0.9651 | 0.8776 | -0.0875 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | ARNOLD3 | 0.9827 | 0.8776 | -0.1051 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | ARNOLD3 | 0.9878 | 0.8776 | -0.1102 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | STFRANT3 | 0.9838 | 0.8776 | -0.1062 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | STFRANT3 | 0.9875 | 0.8776 | -0.1099 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | RANSOM 2 | 0.9787 | 0.8777 | -0.101 |  | 0.9 | 1.05 | 0.05095 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | RANSOM 2 | 0.9787 | 0.8777 | -0.101 |  | 0.9 | 1.05 | 0.04905 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | RANSOM 2 | 0.9787 | 0.8777 | -0.101 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | RANSOM 2 | 0.9787 | 0.8777 | -0.101 |  | 0.9 | 1.05 | 0.04262 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | RANSOM 2 | 0.9787 | 0.8777 | -0.101 |  | 0.9 | 1.05 | 0.0627 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | RANSOM 2 | 0.9787 | 0.8777 | -0.101 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | RANSOM 2 | 0.9787 | 0.8777 | -0.101 |  | 0.9 | 1.05 | 0.05043 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | RANSOM 2 | 0.9787 | 0.8777 | -0.101 |  | 0.9 | 1.05 | 0.05292 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | RANSOM 2 | 0.9787 | 0.8777 | -0.101 |  | 0.9 | 1.05 | 0.0444 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | RANSOM 2 | 0.9787 | 0.8777 | -0.101 |  | 0.9 | 1.05 | 0.04788 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | RANSOM 2 | 0.9787 | 0.8777 | -0.101 |  | 0.9 | 1.05 | 0.05824 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | RANSOM 2 | 0.9787 | 0.8777 | -0.101 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | RANSOM 2 | 0.9787 | 0.8777 | -0.101 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | RANSOM 2 | 0.9787 | 0.8777 | -0.101 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | RANSOM 2 | 0.9787 | 0.8777 | -0.101 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | RANSOM 2 | 0.9787 | 0.8777 | -0.101 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | RANSOM 2 | 0.9787 | 0.8777 | -0.101 |  | 0.9 | 1.05 | 0.04773 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | RANSOM 2 | 0.9787 | 0.8777 | -0.101 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | RANSOM 2 | 0.9787 | 0.8777 | -0.101 |  | 0.9 | 1.05 | 0.0348 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | RANSOM 2 | 0.9787 | 0.8777 | -0.101 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | RANSOM 2 | 0.9787 | 0.8777 | -0.101 |  | 0.9 | 1.05 | 0.04996 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | RANSOM 2 | 0.9787 | 0.8777 | -0.101 |  | 0.9 | 1.05 | 0.04835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | RANSOM 2 | 0.9787 | 0.8777 | -0.101 |  | 0.9 | 1.05 | 0.05448 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | RANSOM 2 | 0.9787 | 0.8777 | -0.101 |  | 0.9 | 1.05 | 0.05382 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | RANSOM 2 | 0.9787 | 0.8777 | -0.101 |  | 0.9 | 1.05 | 0.03774 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | RANSOM 2 | 0.9787 | 0.8777 | -0.101 |  | 0.9 | 1.05 | 0.04948 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | RANSOM 2 | 0.9787 | 0.8777 | -0.101 |  | 0.9 | 1.05 | 0.04054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | NESSCTY3 | 0.975 | 0.8779 | -0.0971 |  | 0.9 | 1.05 | 0.05095 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | NESSCTY3 | 0.975 | 0.8779 | -0.0971 |  | 0.9 | 1.05 | 0.04905 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | NESSCTY3 | 0.975 | 0.8779 | -0.0971 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | NESSCTY3 | 0.975 | 0.8779 | -0.0971 |  | 0.9 | 1.05 | 0.04262 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | NESSCTY3 | 0.975 | 0.8779 | -0.0971 |  | 0.9 | 1.05 | 0.0627 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | NESSCTY3 | 0.975 | 0.8779 | -0.0971 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | NESSCTY3 | 0.975 | 0.8779 | -0.0971 |  | 0.9 | 1.05 | 0.05043 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | NESSCTY3 | 0.975 | 0.8779 | -0.0971 |  | 0.9 | 1.05 | 0.05292 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | NESSCTY3 | 0.975 | 0.8779 | -0.0971 |  | 0.9 | 1.05 | 0.0444 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | NESSCTY3 | 0.975 | 0.8779 | -0.0971 |  | 0.9 | 1.05 | 0.04788 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | NESSCTY3 | 0.975 | 0.8779 | -0.0971 |  | 0.9 | 1.05 | 0.05824 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | NESSCTY3 | 0.975 | 0.8779 | -0.0971 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | NESSCTY3 | 0.975 | 0.8779 | -0.0971 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | NESSCTY3 | 0.975 | 0.8779 | -0.0971 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | NESSCTY3 | 0.975 | 0.8779 | -0.0971 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | NESSCTY3 | 0.975 | 0.8779 | -0.0971 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | NESSCTY3 | 0.975 | 0.8779 | -0.0971 |  | 0.9 | 1.05 | 0.04773 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | NESSCTY3 | 0.975 | 0.8779 | -0.0971 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | NESSCTY3 | 0.975 | 0.8779 | -0.0971 |  | 0.9 | 1.05 | 0.0348 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | NESSCTY3 | 0.975 | 0.8779 | -0.0971 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | NESSCTY3 | 0.975 | 0.8779 | -0.0971 |  | 0.9 | 1.05 | 0.04996 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | NESSCTY3 | 0.975 | 0.8779 | -0.0971 |  | 0.9 | 1.05 | 0.04835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | NESSCTY3 | 0.975 | 0.8779 | -0.0971 |  | 0.9 | 1.05 | 0.05448 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | NESSCTY3 | 0.975 | 0.8779 | -0.0971 |  | 0.9 | 1.05 | 0.05382 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | NESSCTY3 | 0.975 | 0.8779 | -0.0971 |  | 0.9 | 1.05 | 0.03774 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | NESSCTY3 | 0.975 | 0.8779 | -0.0971 |  | 0.9 | 1.05 | 0.04948 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | NESSCTY3 | 0.975 | 0.8779 | -0.0971 |  | 0.9 | 1.05 | 0.04054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | NESCTY 3 | 0.975 | 0.878 | -0.097 |  | 0.9 | 1.05 | 0.05095 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | NESCTY 3 | 0.975 | 0.878 | -0.097 |  | 0.9 | 1.05 | 0.04905 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | NESCTY 3 | 0.975 | 0.878 | -0.097 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | NESCTY 3 | 0.975 | 0.878 | -0.097 |  | 0.9 | 1.05 | 0.04262 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | NESCTY 3 | 0.975 | 0.878 | -0.097 |  | 0.9 | 1.05 | 0.0627 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | NESCTY 3 | 0.975 | 0.878 | -0.097 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | NESCTY 3 | 0.975 | 0.878 | -0.097 |  | 0.9 | 1.05 | 0.05043 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | NESCTY 3 | 0.975 | 0.878 | -0.097 |  | 0.9 | 1.05 | 0.05292 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | NESCTY 3 | 0.975 | 0.878 | -0.097 |  | 0.9 | 1.05 | 0.0444 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | NESCTY 3 | 0.975 | 0.878 | -0.097 |  | 0.9 | 1.05 | 0.04788 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | NESCTY 3 | 0.975 | 0.878 | -0.097 |  | 0.9 | 1.05 | 0.05824 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | NESCTY 3 | 0.975 | 0.878 | -0.097 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | NESCTY 3 | 0.975 | 0.878 | -0.097 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | NESCTY 3 | 0.975 | 0.878 | -0.097 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | NESCTY 3 | 0.975 | 0.878 | -0.097 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | NESCTY 3 | 0.975 | 0.878 | -0.097 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | NESCTY 3 | 0.975 | 0.878 | -0.097 |  | 0.9 | 1.05 | 0.04773 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | NESCTY 3 | 0.975 | 0.878 | -0.097 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | NESCTY 3 | 0.975 | 0.878 | -0.097 |  | 0.9 | 1.05 | 0.0348 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | NESCTY 3 | 0.975 | 0.878 | -0.097 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | NESCTY 3 | 0.975 | 0.878 | -0.097 |  | 0.9 | 1.05 | 0.04996 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | NESCTY 3 | 0.975 | 0.878 | -0.097 |  | 0.9 | 1.05 | 0.04835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | NESCTY 3 | 0.975 | 0.878 | -0.097 |  | 0.9 | 1.05 | 0.05448 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | NESCTY 3 | 0.975 | 0.878 | -0.097 |  | 0.9 | 1.05 | 0.05382 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | NESCTY 3 | 0.975 | 0.878 | -0.097 |  | 0.9 | 1.05 | 0.03774 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | NESCTY 3 | 0.975 | 0.878 | -0.097 |  | 0.9 | 1.05 | 0.04948 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | NESCTY 3 | 0.975 | 0.878 | -0.097 |  | 0.9 | 1.05 | 0.04054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | MANNING3 | 0.9637 | 0.8783 | -0.0854 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | MANNING3 | 0.9637 | 0.8783 | -0.0854 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | MANNING3 | 0.9637 | 0.8783 | -0.0854 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | MANNING3 | 0.9637 | 0.8783 | -0.0854 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | MANNING3 | 0.9637 | 0.8783 | -0.0854 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | MANNING3 | 0.9637 | 0.8783 | -0.0854 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | MANNING3 | 0.9637 | 0.8783 | -0.0854 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | MANNING3 | 0.9637 | 0.8783 | -0.0854 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | MANNING3 | 0.9637 | 0.8783 | -0.0854 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | MANNING3 | 0.9637 | 0.8783 | -0.0854 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | MANNING3 | 0.9637 | 0.8783 | -0.0854 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | MANNING3 | 0.9637 | 0.8783 | -0.0854 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | MANNING3 | 0.9637 | 0.8783 | -0.0854 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | MANNING3 | 0.9637 | 0.8783 | -0.0854 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | MANNING3 | 0.9637 | 0.8783 | -0.0854 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | MANNING3 | 0.9637 | 0.8783 | -0.0854 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | MANNING3 | 0.9637 | 0.8783 | -0.0854 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | MANNING3 | 0.9637 | 0.8783 | -0.0854 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | MANNING3 | 0.9637 | 0.8783 | -0.0854 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | MANNING3 | 0.9637 | 0.8783 | -0.0854 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | MANNING3 | 0.9637 | 0.8783 | -0.0854 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | MANNING3 | 0.9637 | 0.8783 | -0.0854 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | MANNING3 | 0.9637 | 0.8783 | -0.0854 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | MANNING3 | 0.9637 | 0.8783 | -0.0854 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | MANNING3 | 0.9637 | 0.8783 | -0.0854 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | MANNING3 | 0.9637 | 0.8783 | -0.0854 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | MANNING3 | 0.9637 | 0.8783 | -0.0854 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | GODLNDT3 | 0.9773 | 0.8785 | -0.0988 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | GODLNDT3 | 0.9773 | 0.8785 | -0.0988 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | GODLNDT3 | 0.9773 | 0.8785 | -0.0988 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | GODLNDT3 | 0.9773 | 0.8785 | -0.0988 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | GODLNDT3 | 0.9773 | 0.8785 | -0.0988 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | GODLNDT3 | 0.9773 | 0.8785 | -0.0988 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | GODLNDT3 | 0.9773 | 0.8785 | -0.0988 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | GODLNDT3 | 0.9773 | 0.8785 | -0.0988 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | GODLNDT3 | 0.9773 | 0.8785 | -0.0988 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | GODLNDT3 | 0.9773 | 0.8785 | -0.0988 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | GODLNDT3 | 0.9773 | 0.8785 | -0.0988 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | GODLNDT3 | 0.9773 | 0.8785 | -0.0988 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | GODLNDT3 | 0.9773 | 0.8785 | -0.0988 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | GODLNDT3 | 0.9773 | 0.8785 | -0.0988 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | GODLNDT3 | 0.9773 | 0.8785 | -0.0988 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | GODLNDT3 | 0.9773 | 0.8785 | -0.0988 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | GODLNDT3 | 0.9773 | 0.8785 | -0.0988 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | GODLNDT3 | 0.9773 | 0.8785 | -0.0988 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | GODLNDT3 | 0.9773 | 0.8785 | -0.0988 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | GODLNDT3 | 0.9773 | 0.8785 | -0.0988 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | GODLNDT3 | 0.9773 | 0.8785 | -0.0988 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | GODLNDT3 | 0.9773 | 0.8785 | -0.0988 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | GODLNDT3 | 0.9773 | 0.8785 | -0.0988 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | GODLNDT3 | 0.9773 | 0.8785 | -0.0988 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | GODLNDT3 | 0.9773 | 0.8785 | -0.0988 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | GODLNDT3 | 0.9773 | 0.8785 | -0.0988 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | GODLNDT3 | 0.9773 | 0.8785 | -0.0988 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | BIRDCTY3 | 0.9683 | 0.8786 | -0.0897 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | BIRDCTY3 | 0.9723 | 0.8786 | -0.0937 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | PALMER3 | 0.9764 | 0.8786 | -0.0978 |  | 0.9 | 1.05 | 0.05095 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | BIRDCTY3 | 0.9683 | 0.8786 | -0.0897 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | BIRDCTY3 | 0.9723 | 0.8786 | -0.0937 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | PALMER3 | 0.9764 | 0.8786 | -0.0978 |  | 0.9 | 1.05 | 0.04905 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | BIRDCTY3 | 0.9683 | 0.8786 | -0.0897 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | BIRDCTY3 | 0.9723 | 0.8786 | -0.0937 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | PALMER3 | 0.9764 | 0.8786 | -0.0978 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | BIRDCTY3 | 0.9683 | 0.8786 | -0.0897 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | BIRDCTY3 | 0.9723 | 0.8786 | -0.0937 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | PALMER3 | 0.9764 | 0.8786 | -0.0978 |  | 0.9 | 1.05 | 0.04262 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | BIRDCTY3 | 0.9683 | 0.8786 | -0.0897 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | BIRDCTY3 | 0.9723 | 0.8786 | -0.0937 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | PALMER3 | 0.9764 | 0.8786 | -0.0978 |  | 0.9 | 1.05 | 0.0627 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | BIRDCTY3 | 0.9683 | 0.8786 | -0.0897 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | BIRDCTY3 | 0.9723 | 0.8786 | -0.0937 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | PALMER3 | 0.9764 | 0.8786 | -0.0978 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | BIRDCTY3 | 0.9683 | 0.8786 | -0.0897 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | BIRDCTY3 | 0.9723 | 0.8786 | -0.0937 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | PALMER3 | 0.9764 | 0.8786 | -0.0978 |  | 0.9 | 1.05 | 0.05043 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | BIRDCTY3 | 0.9683 | 0.8786 | -0.0897 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | BIRDCTY3 | 0.9723 | 0.8786 | -0.0937 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | PALMER3 | 0.9764 | 0.8786 | -0.0978 |  | 0.9 | 1.05 | 0.05292 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | BIRDCTY3 | 0.9683 | 0.8786 | -0.0897 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | BIRDCTY3 | 0.9723 | 0.8786 | -0.0937 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | PALMER3 | 0.9764 | 0.8786 | -0.0978 |  | 0.9 | 1.05 | 0.0444 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | BIRDCTY3 | 0.9683 | 0.8786 | -0.0897 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | BIRDCTY3 | 0.9723 | 0.8786 | -0.0937 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | PALMER3 | 0.9764 | 0.8786 | -0.0978 |  | 0.9 | 1.05 | 0.04788 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | BIRDCTY3 | 0.9683 | 0.8786 | -0.0897 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | BIRDCTY3 | 0.9723 | 0.8786 | -0.0937 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | PALMER3 | 0.9764 | 0.8786 | -0.0978 |  | 0.9 | 1.05 | 0.05824 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | BIRDCTY3 | 0.9683 | 0.8786 | -0.0897 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | BIRDCTY3 | 0.9723 | 0.8786 | -0.0937 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | PALMER3 | 0.9764 | 0.8786 | -0.0978 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | BIRDCTY3 | 0.9683 | 0.8786 | -0.0897 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | BIRDCTY3 | 0.9723 | 0.8786 | -0.0937 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | PALMER3 | 0.9764 | 0.8786 | -0.0978 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | BIRDCTY3 | 0.9683 | 0.8786 | -0.0897 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | BIRDCTY3 | 0.9723 | 0.8786 | -0.0937 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | PALMER3 | 0.9764 | 0.8786 | -0.0978 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | BIRDCTY3 | 0.9683 | 0.8786 | -0.0897 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | BIRDCTY3 | 0.9723 | 0.8786 | -0.0937 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | PALMER3 | 0.9764 | 0.8786 | -0.0978 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | BIRDCTY3 | 0.9683 | 0.8786 | -0.0897 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | BIRDCTY3 | 0.9723 | 0.8786 | -0.0937 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | PALMER3 | 0.9764 | 0.8786 | -0.0978 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | BIRDCTY3 | 0.9683 | 0.8786 | -0.0897 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | BIRDCTY3 | 0.9723 | 0.8786 | -0.0937 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | PALMER3 | 0.9764 | 0.8786 | -0.0978 |  | 0.9 | 1.05 | 0.04773 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | BIRDCTY3 | 0.9683 | 0.8786 | -0.0897 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | BIRDCTY3 | 0.9723 | 0.8786 | -0.0937 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | PALMER3 | 0.9764 | 0.8786 | -0.0978 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | BIRDCTY3 | 0.9683 | 0.8786 | -0.0897 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | BIRDCTY3 | 0.9723 | 0.8786 | -0.0937 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | PALMER3 | 0.9764 | 0.8786 | -0.0978 |  | 0.9 | 1.05 | 0.0348 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | BIRDCTY3 | 0.9683 | 0.8786 | -0.0897 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | BIRDCTY3 | 0.9723 | 0.8786 | -0.0937 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | PALMER3 | 0.9764 | 0.8786 | -0.0978 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | BIRDCTY3 | 0.9683 | 0.8786 | -0.0897 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | BIRDCTY3 | 0.9723 | 0.8786 | -0.0937 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | PALMER3 | 0.9764 | 0.8786 | -0.0978 |  | 0.9 | 1.05 | 0.04996 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | BIRDCTY3 | 0.9683 | 0.8786 | -0.0897 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | BIRDCTY3 | 0.9723 | 0.8786 | -0.0937 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | PALMER3 | 0.9764 | 0.8786 | -0.0978 |  | 0.9 | 1.05 | 0.04835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | BIRDCTY3 | 0.9683 | 0.8786 | -0.0897 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | BIRDCTY3 | 0.9723 | 0.8786 | -0.0937 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | PALMER3 | 0.9764 | 0.8786 | -0.0978 |  | 0.9 | 1.05 | 0.05448 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | BIRDCTY3 | 0.9683 | 0.8786 | -0.0897 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | BIRDCTY3 | 0.9723 | 0.8786 | -0.0937 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | PALMER3 | 0.9764 | 0.8786 | -0.0978 |  | 0.9 | 1.05 | 0.05382 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | BIRDCTY3 | 0.9683 | 0.8786 | -0.0897 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | BIRDCTY3 | 0.9723 | 0.8786 | -0.0937 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | PALMER3 | 0.9764 | 0.8786 | -0.0978 |  | 0.9 | 1.05 | 0.03774 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | BIRDCTY3 | 0.9683 | 0.8786 | -0.0897 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | BIRDCTY3 | 0.9723 | 0.8786 | -0.0937 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | PALMER3 | 0.9764 | 0.8786 | -0.0978 |  | 0.9 | 1.05 | 0.04948 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | BIRDCTY3 | 0.9683 | 0.8786 | -0.0897 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | BIRDCTY3 | 0.9723 | 0.8786 | -0.0937 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | PALMER3 | 0.9764 | 0.8786 | -0.0978 |  | 0.9 | 1.05 | 0.04054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | LIBERTYT | 0.9696 | 0.8787 | -0.0909 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | LIBERTYT | 0.9784 | 0.8787 | -0.0997 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | LIBERTYT | 0.9696 | 0.8787 | -0.0909 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | LIBERTYT | 0.9784 | 0.8787 | -0.0997 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | LIBERTYT | 0.9696 | 0.8787 | -0.0909 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | LIBERTYT | 0.9784 | 0.8787 | -0.0997 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | LIBERTYT | 0.9696 | 0.8787 | -0.0909 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | LIBERTYT | 0.9784 | 0.8787 | -0.0997 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | LIBERTYT | 0.9696 | 0.8787 | -0.0909 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | LIBERTYT | 0.9784 | 0.8787 | -0.0997 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | LIBERTYT | 0.9696 | 0.8787 | -0.0909 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | LIBERTYT | 0.9784 | 0.8787 | -0.0997 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | LIBERTYT | 0.9696 | 0.8787 | -0.0909 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | LIBERTYT | 0.9784 | 0.8787 | -0.0997 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | LIBERTYT | 0.9696 | 0.8787 | -0.0909 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | LIBERTYT | 0.9784 | 0.8787 | -0.0997 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | LIBERTYT | 0.9696 | 0.8787 | -0.0909 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | LIBERTYT | 0.9784 | 0.8787 | -0.0997 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | LIBERTYT | 0.9696 | 0.8787 | -0.0909 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | LIBERTYT | 0.9784 | 0.8787 | -0.0997 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | LIBERTYT | 0.9696 | 0.8787 | -0.0909 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | LIBERTYT | 0.9784 | 0.8787 | -0.0997 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | LIBERTYT | 0.9696 | 0.8787 | -0.0909 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | LIBERTYT | 0.9784 | 0.8787 | -0.0997 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | LIBERTYT | 0.9696 | 0.8787 | -0.0909 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | LIBERTYT | 0.9784 | 0.8787 | -0.0997 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | LIBERTYT | 0.9696 | 0.8787 | -0.0909 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | LIBERTYT | 0.9784 | 0.8787 | -0.0997 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | LIBERTYT | 0.9696 | 0.8787 | -0.0909 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | LIBERTYT | 0.9784 | 0.8787 | -0.0997 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | LIBERTYT | 0.9696 | 0.8787 | -0.0909 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | LIBERTYT | 0.9784 | 0.8787 | -0.0997 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | LIBERTYT | 0.9696 | 0.8787 | -0.0909 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | LIBERTYT | 0.9784 | 0.8787 | -0.0997 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | LIBERTYT | 0.9696 | 0.8787 | -0.0909 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | LIBERTYT | 0.9784 | 0.8787 | -0.0997 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | LIBERTYT | 0.9696 | 0.8787 | -0.0909 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | LIBERTYT | 0.9784 | 0.8787 | -0.0997 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | LIBERTYT | 0.9696 | 0.8787 | -0.0909 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | LIBERTYT | 0.9784 | 0.8787 | -0.0997 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | LIBERTYT | 0.9696 | 0.8787 | -0.0909 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | LIBERTYT | 0.9784 | 0.8787 | -0.0997 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | LIBERTYT | 0.9696 | 0.8787 | -0.0909 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | LIBERTYT | 0.9784 | 0.8787 | -0.0997 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | LIBERTYT | 0.9696 | 0.8787 | -0.0909 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | LIBERTYT | 0.9784 | 0.8787 | -0.0997 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | LIBERTYT | 0.9696 | 0.8787 | -0.0909 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | LIBERTYT | 0.9784 | 0.8787 | -0.0997 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | LIBERTYT | 0.9696 | 0.8787 | -0.0909 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | LIBERTYT | 0.9784 | 0.8787 | -0.0997 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | LIBERTYT | 0.9696 | 0.8787 | -0.0909 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | LIBERTYT | 0.9784 | 0.8787 | -0.0997 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | LIBERTYT | 0.9696 | 0.8787 | -0.0909 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | LIBERTYT | 0.9784 | 0.8787 | -0.0997 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | MANNGT 3 | 0.9648 | 0.8794 | -0.0854 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | SCOTCTY3 | 0.9681 | 0.8794 | -0.0887 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | MANNGT 3 | 0.9648 | 0.8794 | -0.0854 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | SCOTCTY3 | 0.9681 | 0.8794 | -0.0887 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | MANNGT 3 | 0.9648 | 0.8794 | -0.0854 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | SCOTCTY3 | 0.9681 | 0.8794 | -0.0887 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | MANNGT 3 | 0.9648 | 0.8794 | -0.0854 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | SCOTCTY3 | 0.9681 | 0.8794 | -0.0887 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | MANNGT 3 | 0.9648 | 0.8794 | -0.0854 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | SCOTCTY3 | 0.9681 | 0.8794 | -0.0887 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | MANNGT 3 | 0.9648 | 0.8794 | -0.0854 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | SCOTCTY3 | 0.9681 | 0.8794 | -0.0887 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | MANNGT 3 | 0.9648 | 0.8794 | -0.0854 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | SCOTCTY3 | 0.9681 | 0.8794 | -0.0887 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | MANNGT 3 | 0.9648 | 0.8794 | -0.0854 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | SCOTCTY3 | 0.9681 | 0.8794 | -0.0887 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | MANNGT 3 | 0.9648 | 0.8794 | -0.0854 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | SCOTCTY3 | 0.9681 | 0.8794 | -0.0887 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | MANNGT 3 | 0.9648 | 0.8794 | -0.0854 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | SCOTCTY3 | 0.9681 | 0.8794 | -0.0887 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | MANNGT 3 | 0.9648 | 0.8794 | -0.0854 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | SCOTCTY3 | 0.9681 | 0.8794 | -0.0887 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | MANNGT 3 | 0.9648 | 0.8794 | -0.0854 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | SCOTCTY3 | 0.9681 | 0.8794 | -0.0887 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | MANNGT 3 | 0.9648 | 0.8794 | -0.0854 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | SCOTCTY3 | 0.9681 | 0.8794 | -0.0887 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | MANNGT 3 | 0.9648 | 0.8794 | -0.0854 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | SCOTCTY3 | 0.9681 | 0.8794 | -0.0887 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | MANNGT 3 | 0.9648 | 0.8794 | -0.0854 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | SCOTCTY3 | 0.9681 | 0.8794 | -0.0887 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | MANNGT 3 | 0.9648 | 0.8794 | -0.0854 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | SCOTCTY3 | 0.9681 | 0.8794 | -0.0887 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | MANNGT 3 | 0.9648 | 0.8794 | -0.0854 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | SCOTCTY3 | 0.9681 | 0.8794 | -0.0887 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | MANNGT 3 | 0.9648 | 0.8794 | -0.0854 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | SCOTCTY3 | 0.9681 | 0.8794 | -0.0887 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | MANNGT 3 | 0.9648 | 0.8794 | -0.0854 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | SCOTCTY3 | 0.9681 | 0.8794 | -0.0887 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | MANNGT 3 | 0.9648 | 0.8794 | -0.0854 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | SCOTCTY3 | 0.9681 | 0.8794 | -0.0887 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | MANNGT 3 | 0.9648 | 0.8794 | -0.0854 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | SCOTCTY3 | 0.9681 | 0.8794 | -0.0887 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | MANNGT 3 | 0.9648 | 0.8794 | -0.0854 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | SCOTCTY3 | 0.9681 | 0.8794 | -0.0887 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | MANNGT 3 | 0.9648 | 0.8794 | -0.0854 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | SCOTCTY3 | 0.9681 | 0.8794 | -0.0887 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | MANNGT 3 | 0.9648 | 0.8794 | -0.0854 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | SCOTCTY3 | 0.9681 | 0.8794 | -0.0887 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | MANNGT 3 | 0.9648 | 0.8794 | -0.0854 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | SCOTCTY3 | 0.9681 | 0.8794 | -0.0887 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | MANNGT 3 | 0.9648 | 0.8794 | -0.0854 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | SCOTCTY3 | 0.9681 | 0.8794 | -0.0887 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | MANNGT 3 | 0.9648 | 0.8794 | -0.0854 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | SCOTCTY3 | 0.9681 | 0.8794 | -0.0887 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | KANARAD3 | 0.9653 | 0.8797 | -0.0856 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | KANARAD3 | 0.9653 | 0.8797 | -0.0856 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | KANARAD3 | 0.9653 | 0.8797 | -0.0856 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | KANARAD3 | 0.9653 | 0.8797 | -0.0856 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | KANARAD3 | 0.9653 | 0.8797 | -0.0856 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | KANARAD3 | 0.9653 | 0.8797 | -0.0856 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | KANARAD3 | 0.9653 | 0.8797 | -0.0856 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | KANARAD3 | 0.9653 | 0.8797 | -0.0856 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | KANARAD3 | 0.9653 | 0.8797 | -0.0856 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | KANARAD3 | 0.9653 | 0.8797 | -0.0856 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | KANARAD3 | 0.9653 | 0.8797 | -0.0856 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | KANARAD3 | 0.9653 | 0.8797 | -0.0856 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | KANARAD3 | 0.9653 | 0.8797 | -0.0856 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | KANARAD3 | 0.9653 | 0.8797 | -0.0856 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | KANARAD3 | 0.9653 | 0.8797 | -0.0856 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | KANARAD3 | 0.9653 | 0.8797 | -0.0856 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | KANARAD3 | 0.9653 | 0.8797 | -0.0856 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | KANARAD3 | 0.9653 | 0.8797 | -0.0856 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | KANARAD3 | 0.9653 | 0.8797 | -0.0856 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | KANARAD3 | 0.9653 | 0.8797 | -0.0856 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | KANARAD3 | 0.9653 | 0.8797 | -0.0856 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | KANARAD3 | 0.9653 | 0.8797 | -0.0856 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | KANARAD3 | 0.9653 | 0.8797 | -0.0856 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | KANARAD3 | 0.9653 | 0.8797 | -0.0856 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | KANARAD3 | 0.9653 | 0.8797 | -0.0856 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | KANARAD3 | 0.9653 | 0.8797 | -0.0856 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | KANARAD3 | 0.9653 | 0.8797 | -0.0856 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | STFRAN 3 | 0.9837 | 0.8801 | -0.1036 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | STFRAN 3 | 0.9872 | 0.8801 | -0.1071 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | STFRAN 3 | 0.9837 | 0.8801 | -0.1036 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | STFRAN 3 | 0.9872 | 0.8801 | -0.1071 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | STFRAN 3 | 0.9837 | 0.8801 | -0.1036 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | STFRAN 3 | 0.9872 | 0.8801 | -0.1071 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | STFRAN 3 | 0.9837 | 0.8801 | -0.1036 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | STFRAN 3 | 0.9872 | 0.8801 | -0.1071 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | STFRAN 3 | 0.9837 | 0.8801 | -0.1036 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | STFRAN 3 | 0.9872 | 0.8801 | -0.1071 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | STFRAN 3 | 0.9837 | 0.8801 | -0.1036 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | STFRAN 3 | 0.9872 | 0.8801 | -0.1071 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | STFRAN 3 | 0.9837 | 0.8801 | -0.1036 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | STFRAN 3 | 0.9872 | 0.8801 | -0.1071 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | STFRAN 3 | 0.9837 | 0.8801 | -0.1036 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | STFRAN 3 | 0.9872 | 0.8801 | -0.1071 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | STFRAN 3 | 0.9837 | 0.8801 | -0.1036 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | STFRAN 3 | 0.9872 | 0.8801 | -0.1071 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | STFRAN 3 | 0.9837 | 0.8801 | -0.1036 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | STFRAN 3 | 0.9872 | 0.8801 | -0.1071 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | STFRAN 3 | 0.9837 | 0.8801 | -0.1036 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | STFRAN 3 | 0.9872 | 0.8801 | -0.1071 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | STFRAN 3 | 0.9837 | 0.8801 | -0.1036 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | STFRAN 3 | 0.9872 | 0.8801 | -0.1071 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | STFRAN 3 | 0.9837 | 0.8801 | -0.1036 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | STFRAN 3 | 0.9872 | 0.8801 | -0.1071 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | STFRAN 3 | 0.9837 | 0.8801 | -0.1036 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | STFRAN 3 | 0.9872 | 0.8801 | -0.1071 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | STFRAN 3 | 0.9837 | 0.8801 | -0.1036 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | STFRAN 3 | 0.9872 | 0.8801 | -0.1071 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | STFRAN 3 | 0.9837 | 0.8801 | -0.1036 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | STFRAN 3 | 0.9872 | 0.8801 | -0.1071 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | STFRAN 3 | 0.9837 | 0.8801 | -0.1036 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | STFRAN 3 | 0.9872 | 0.8801 | -0.1071 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | STFRAN 3 | 0.9837 | 0.8801 | -0.1036 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | STFRAN 3 | 0.9872 | 0.8801 | -0.1071 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | STFRAN 3 | 0.9837 | 0.8801 | -0.1036 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | STFRAN 3 | 0.9872 | 0.8801 | -0.1071 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | STFRAN 3 | 0.9837 | 0.8801 | -0.1036 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | STFRAN 3 | 0.9872 | 0.8801 | -0.1071 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | STFRAN 3 | 0.9837 | 0.8801 | -0.1036 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | STFRAN 3 | 0.9872 | 0.8801 | -0.1071 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | STFRAN 3 | 0.9837 | 0.8801 | -0.1036 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | STFRAN 3 | 0.9872 | 0.8801 | -0.1071 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | STFRAN 3 | 0.9837 | 0.8801 | -0.1036 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | STFRAN 3 | 0.9872 | 0.8801 | -0.1071 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | STFRAN 3 | 0.9837 | 0.8801 | -0.1036 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | STFRAN 3 | 0.9872 | 0.8801 | -0.1071 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | STFRAN 3 | 0.9837 | 0.8801 | -0.1036 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | STFRAN 3 | 0.9872 | 0.8801 | -0.1071 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | STFRAN 3 | 0.9837 | 0.8801 | -0.1036 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | STFRAN 3 | 0.9872 | 0.8801 | -0.1071 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | STFRAN 3 | 0.9837 | 0.8801 | -0.1036 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | STFRAN 3 | 0.9872 | 0.8801 | -0.1071 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | RANSOM 3 | 0.9806 | 0.8802 | -0.1004 |  | 0.9 | 1.05 | 0.05095 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | RANSOM 3 | 0.9806 | 0.8802 | -0.1004 |  | 0.9 | 1.05 | 0.04905 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | RANSOM 3 | 0.9806 | 0.8802 | -0.1004 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | RANSOM 3 | 0.9806 | 0.8802 | -0.1004 |  | 0.9 | 1.05 | 0.04262 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | RANSOM 3 | 0.9806 | 0.8802 | -0.1004 |  | 0.9 | 1.05 | 0.0627 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | RANSOM 3 | 0.9806 | 0.8802 | -0.1004 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | RANSOM 3 | 0.9806 | 0.8802 | -0.1004 |  | 0.9 | 1.05 | 0.05043 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | RANSOM 3 | 0.9806 | 0.8802 | -0.1004 |  | 0.9 | 1.05 | 0.05292 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | RANSOM 3 | 0.9806 | 0.8802 | -0.1004 |  | 0.9 | 1.05 | 0.0444 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | RANSOM 3 | 0.9806 | 0.8802 | -0.1004 |  | 0.9 | 1.05 | 0.04788 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | RANSOM 3 | 0.9806 | 0.8802 | -0.1004 |  | 0.9 | 1.05 | 0.05824 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | RANSOM 3 | 0.9806 | 0.8802 | -0.1004 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | RANSOM 3 | 0.9806 | 0.8802 | -0.1004 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | RANSOM 3 | 0.9806 | 0.8802 | -0.1004 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | RANSOM 3 | 0.9806 | 0.8802 | -0.1004 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | RANSOM 3 | 0.9806 | 0.8802 | -0.1004 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | RANSOM 3 | 0.9806 | 0.8802 | -0.1004 |  | 0.9 | 1.05 | 0.04773 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | RANSOM 3 | 0.9806 | 0.8802 | -0.1004 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | RANSOM 3 | 0.9806 | 0.8802 | -0.1004 |  | 0.9 | 1.05 | 0.0348 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | RANSOM 3 | 0.9806 | 0.8802 | -0.1004 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | RANSOM 3 | 0.9806 | 0.8802 | -0.1004 |  | 0.9 | 1.05 | 0.04996 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | RANSOM 3 | 0.9806 | 0.8802 | -0.1004 |  | 0.9 | 1.05 | 0.04835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | RANSOM 3 | 0.9806 | 0.8802 | -0.1004 |  | 0.9 | 1.05 | 0.05448 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | RANSOM 3 | 0.9806 | 0.8802 | -0.1004 |  | 0.9 | 1.05 | 0.05382 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | RANSOM 3 | 0.9806 | 0.8802 | -0.1004 |  | 0.9 | 1.05 | 0.03774 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | RANSOM 3 | 0.9806 | 0.8802 | -0.1004 |  | 0.9 | 1.05 | 0.04948 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | RANSOM 3 | 0.9806 | 0.8802 | -0.1004 |  | 0.9 | 1.05 | 0.04054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | GOODLND3 | 0.9779 | 0.8805 | -0.0974 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | GOODLND3 | 0.9779 | 0.8805 | -0.0974 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | GOODLND3 | 0.9779 | 0.8805 | -0.0974 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | GOODLND3 | 0.9779 | 0.8805 | -0.0974 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | GOODLND3 | 0.9779 | 0.8805 | -0.0974 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | GOODLND3 | 0.9779 | 0.8805 | -0.0974 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | GOODLND3 | 0.9779 | 0.8805 | -0.0974 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | GOODLND3 | 0.9779 | 0.8805 | -0.0974 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | GOODLND3 | 0.9779 | 0.8805 | -0.0974 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | GOODLND3 | 0.9779 | 0.8805 | -0.0974 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | GOODLND3 | 0.9779 | 0.8805 | -0.0974 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | GOODLND3 | 0.9779 | 0.8805 | -0.0974 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | GOODLND3 | 0.9779 | 0.8805 | -0.0974 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | GOODLND3 | 0.9779 | 0.8805 | -0.0974 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | GOODLND3 | 0.9779 | 0.8805 | -0.0974 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | GOODLND3 | 0.9779 | 0.8805 | -0.0974 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | GOODLND3 | 0.9779 | 0.8805 | -0.0974 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | GOODLND3 | 0.9779 | 0.8805 | -0.0974 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | GOODLND3 | 0.9779 | 0.8805 | -0.0974 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | GOODLND3 | 0.9779 | 0.8805 | -0.0974 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | GOODLND3 | 0.9779 | 0.8805 | -0.0974 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | GOODLND3 | 0.9779 | 0.8805 | -0.0974 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | GOODLND3 | 0.9779 | 0.8805 | -0.0974 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | GOODLND3 | 0.9779 | 0.8805 | -0.0974 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | GOODLND3 | 0.9779 | 0.8805 | -0.0974 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | GOODLND3 | 0.9779 | 0.8805 | -0.0974 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | GOODLND3 | 0.9779 | 0.8805 | -0.0974 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | CHASE 3 | 0.9745 | 0.8806 | -0.0939 |  | 0.9 | 1.05 | 0.05115 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | CHASE 3 | 0.9745 | 0.8806 | -0.0939 |  | 0.9 | 1.05 | 0.04926 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | CHASE 3 | 0.9745 | 0.8806 | -0.0939 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | CHASE 3 | 0.9745 | 0.8806 | -0.0939 |  | 0.9 | 1.05 | 0.04287 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | CHASE 3 | 0.9745 | 0.8806 | -0.0939 |  | 0.9 | 1.05 | 0.06285 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | CHASE 3 | 0.9745 | 0.8806 | -0.0939 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | CHASE 3 | 0.9745 | 0.8806 | -0.0939 |  | 0.9 | 1.05 | 0.05063 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | CHASE 3 | 0.9745 | 0.8806 | -0.0939 |  | 0.9 | 1.05 | 0.05311 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | CHASE 3 | 0.9745 | 0.8806 | -0.0939 |  | 0.9 | 1.05 | 0.04461 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | CHASE 3 | 0.9745 | 0.8806 | -0.0939 |  | 0.9 | 1.05 | 0.0481 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | CHASE 3 | 0.9745 | 0.8806 | -0.0939 |  | 0.9 | 1.05 | 0.0584 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | CHASE 3 | 0.9745 | 0.8806 | -0.0939 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | CHASE 3 | 0.9745 | 0.8806 | -0.0939 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | CHASE 3 | 0.9745 | 0.8806 | -0.0939 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | CHASE 3 | 0.9745 | 0.8806 | -0.0939 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | CHASE 3 | 0.9745 | 0.8806 | -0.0939 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | CHASE 3 | 0.9745 | 0.8806 | -0.0939 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | CHASE 3 | 0.9745 | 0.8806 | -0.0939 |  | 0.9 | 1.05 | 0.05126 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | CHASE 3 | 0.9745 | 0.8806 | -0.0939 |  | 0.9 | 1.05 | 0.0351 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | CHASE 3 | 0.9745 | 0.8806 | -0.0939 |  | 0.9 | 1.05 | 0.04774 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | CHASE 3 | 0.9745 | 0.8806 | -0.0939 |  | 0.9 | 1.05 | 0.05016 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | CHASE 3 | 0.9745 | 0.8806 | -0.0939 |  | 0.9 | 1.05 | 0.04857 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | CHASE 3 | 0.9745 | 0.8806 | -0.0939 |  | 0.9 | 1.05 | 0.05466 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | CHASE 3 | 0.9745 | 0.8806 | -0.0939 |  | 0.9 | 1.05 | 0.05401 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | CHASE 3 | 0.9745 | 0.8806 | -0.0939 |  | 0.9 | 1.05 | 0.03802 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | CHASE 3 | 0.9745 | 0.8806 | -0.0939 |  | 0.9 | 1.05 | 0.04968 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | CHASE 3 | 0.9745 | 0.8806 | -0.0939 |  | 0.9 | 1.05 | 0.04081 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | SHARNSP3 | 0.9746 | 0.8807 | -0.0939 |  | 0.9 | 1.05 | 0.05115 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | SHARNSP3 | 0.9746 | 0.8807 | -0.0939 |  | 0.9 | 1.05 | 0.04926 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | SHARNSP3 | 0.9746 | 0.8807 | -0.0939 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | SHARNSP3 | 0.9746 | 0.8807 | -0.0939 |  | 0.9 | 1.05 | 0.04287 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | SHARNSP3 | 0.9746 | 0.8807 | -0.0939 |  | 0.9 | 1.05 | 0.06285 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | SHARNSP3 | 0.9746 | 0.8807 | -0.0939 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | SHARNSP3 | 0.9746 | 0.8807 | -0.0939 |  | 0.9 | 1.05 | 0.05063 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | SHARNSP3 | 0.9746 | 0.8807 | -0.0939 |  | 0.9 | 1.05 | 0.05311 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | SHARNSP3 | 0.9746 | 0.8807 | -0.0939 |  | 0.9 | 1.05 | 0.04461 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | SHARNSP3 | 0.9746 | 0.8807 | -0.0939 |  | 0.9 | 1.05 | 0.0481 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | SHARNSP3 | 0.9746 | 0.8807 | -0.0939 |  | 0.9 | 1.05 | 0.0584 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | SHARNSP3 | 0.9746 | 0.8807 | -0.0939 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | SHARNSP3 | 0.9746 | 0.8807 | -0.0939 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | SHARNSP3 | 0.9746 | 0.8807 | -0.0939 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | SHARNSP3 | 0.9746 | 0.8807 | -0.0939 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | SHARNSP3 | 0.9746 | 0.8807 | -0.0939 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | SHARNSP3 | 0.9746 | 0.8807 | -0.0939 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | SHARNSP3 | 0.9746 | 0.8807 | -0.0939 |  | 0.9 | 1.05 | 0.05126 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | SHARNSP3 | 0.9746 | 0.8807 | -0.0939 |  | 0.9 | 1.05 | 0.0351 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | SHARNSP3 | 0.9746 | 0.8807 | -0.0939 |  | 0.9 | 1.05 | 0.04774 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | SHARNSP3 | 0.9746 | 0.8807 | -0.0939 |  | 0.9 | 1.05 | 0.05016 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | SHARNSP3 | 0.9746 | 0.8807 | -0.0939 |  | 0.9 | 1.05 | 0.04857 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | SHARNSP3 | 0.9746 | 0.8807 | -0.0939 |  | 0.9 | 1.05 | 0.05466 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | SHARNSP3 | 0.9746 | 0.8807 | -0.0939 |  | 0.9 | 1.05 | 0.05401 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | SHARNSP3 | 0.9746 | 0.8807 | -0.0939 |  | 0.9 | 1.05 | 0.03802 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | SHARNSP3 | 0.9746 | 0.8807 | -0.0939 |  | 0.9 | 1.05 | 0.04968 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | SHARNSP3 | 0.9746 | 0.8807 | -0.0939 |  | 0.9 | 1.05 | 0.04081 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | WTCLF 3 | 0.9595 | 0.8808 | -0.0787 |  | 0.9 | 1.05 | 0.05101 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | WTCLF 3 | 0.9595 | 0.8808 | -0.0787 |  | 0.9 | 1.05 | 0.04911 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | WTCLF 3 | 0.9595 | 0.8808 | -0.0787 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | WTCLF 3 | 0.9595 | 0.8808 | -0.0787 |  | 0.9 | 1.05 | 0.04272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | WTCLF 3 | 0.9595 | 0.8808 | -0.0787 |  | 0.9 | 1.05 | 0.06272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | WTCLF 3 | 0.9595 | 0.8808 | -0.0787 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | WTCLF 3 | 0.9595 | 0.8808 | -0.0787 |  | 0.9 | 1.05 | 0.05049 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | WTCLF 3 | 0.9595 | 0.8808 | -0.0787 |  | 0.9 | 1.05 | 0.05297 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | WTCLF 3 | 0.9595 | 0.8808 | -0.0787 |  | 0.9 | 1.05 | 0.04447 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | WTCLF 3 | 0.9595 | 0.8808 | -0.0787 |  | 0.9 | 1.05 | 0.04795 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | WTCLF 3 | 0.9595 | 0.8808 | -0.0787 |  | 0.9 | 1.05 | 0.05827 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | WTCLF 3 | 0.9595 | 0.8808 | -0.0787 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | WTCLF 3 | 0.9595 | 0.8808 | -0.0787 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | WTCLF 3 | 0.9595 | 0.8808 | -0.0787 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | WTCLF 3 | 0.9595 | 0.8808 | -0.0787 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | WTCLF 3 | 0.9595 | 0.8808 | -0.0787 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | WTCLF 3 | 0.9595 | 0.8808 | -0.0787 |  | 0.9 | 1.05 | 0.04781 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | WTCLF 3 | 0.9595 | 0.8808 | -0.0787 |  | 0.9 | 1.05 | 0.05112 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | WTCLF 3 | 0.9595 | 0.8808 | -0.0787 |  | 0.9 | 1.05 | 0.03494 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | WTCLF 3 | 0.9595 | 0.8808 | -0.0787 |  | 0.9 | 1.05 | 0.04759 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | WTCLF 3 | 0.9595 | 0.8808 | -0.0787 |  | 0.9 | 1.05 | 0.05002 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | WTCLF 3 | 0.9595 | 0.8808 | -0.0787 |  | 0.9 | 1.05 | 0.04842 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | WTCLF 3 | 0.9595 | 0.8808 | -0.0787 |  | 0.9 | 1.05 | 0.05452 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | WTCLF 3 | 0.9595 | 0.8808 | -0.0787 |  | 0.9 | 1.05 | 0.05387 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | WTCLF 3 | 0.9595 | 0.8808 | -0.0787 |  | 0.9 | 1.05 | 0.03786 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | WTCLF 3 | 0.9595 | 0.8808 | -0.0787 |  | 0.9 | 1.05 | 0.04954 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | WTCLF 3 | 0.9595 | 0.8808 | -0.0787 |  | 0.9 | 1.05 | 0.04065 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | LIBERTY3 | 0.956 | 0.881 | -0.075 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | LIBERTY3 | 0.956 | 0.881 | -0.075 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | LIBERTY3 | 0.956 | 0.881 | -0.075 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | LIBERTY3 | 0.956 | 0.881 | -0.075 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | LIBERTY3 | 0.956 | 0.881 | -0.075 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | LIBERTY3 | 0.956 | 0.881 | -0.075 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | LIBERTY3 | 0.956 | 0.881 | -0.075 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | LIBERTY3 | 0.956 | 0.881 | -0.075 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | LIBERTY3 | 0.956 | 0.881 | -0.075 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | LIBERTY3 | 0.956 | 0.881 | -0.075 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | LIBERTY3 | 0.956 | 0.881 | -0.075 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | LIBERTY3 | 0.956 | 0.881 | -0.075 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | LIBERTY3 | 0.956 | 0.881 | -0.075 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | LIBERTY3 | 0.956 | 0.881 | -0.075 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | LIBERTY3 | 0.956 | 0.881 | -0.075 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | LIBERTY3 | 0.956 | 0.881 | -0.075 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | LIBERTY3 | 0.956 | 0.881 | -0.075 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | LIBERTY3 | 0.956 | 0.881 | -0.075 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | LIBERTY3 | 0.956 | 0.881 | -0.075 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | LIBERTY3 | 0.956 | 0.881 | -0.075 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | LIBERTY3 | 0.956 | 0.881 | -0.075 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | LIBERTY3 | 0.956 | 0.881 | -0.075 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | LIBERTY3 | 0.956 | 0.881 | -0.075 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | LIBERTY3 | 0.956 | 0.881 | -0.075 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | LIBERTY3 | 0.956 | 0.881 | -0.075 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | LIBERTY3 | 0.956 | 0.881 | -0.075 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | LIBERTY3 | 0.956 | 0.881 | -0.075 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | PILE 3 | 0.9763 | 0.8812 | -0.0951 |  | 0.9 | 1.05 | 0.05115 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | PILE 3 | 0.9763 | 0.8812 | -0.0951 |  | 0.9 | 1.05 | 0.04926 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | PILE 3 | 0.9763 | 0.8812 | -0.0951 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | PILE 3 | 0.9763 | 0.8812 | -0.0951 |  | 0.9 | 1.05 | 0.04287 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | PILE 3 | 0.9763 | 0.8812 | -0.0951 |  | 0.9 | 1.05 | 0.06285 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | PILE 3 | 0.9763 | 0.8812 | -0.0951 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | PILE 3 | 0.9763 | 0.8812 | -0.0951 |  | 0.9 | 1.05 | 0.05063 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | PILE 3 | 0.9763 | 0.8812 | -0.0951 |  | 0.9 | 1.05 | 0.05311 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | PILE 3 | 0.9763 | 0.8812 | -0.0951 |  | 0.9 | 1.05 | 0.04461 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | PILE 3 | 0.9763 | 0.8812 | -0.0951 |  | 0.9 | 1.05 | 0.0481 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | PILE 3 | 0.9763 | 0.8812 | -0.0951 |  | 0.9 | 1.05 | 0.0584 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | PILE 3 | 0.9763 | 0.8812 | -0.0951 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | PILE 3 | 0.9763 | 0.8812 | -0.0951 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | PILE 3 | 0.9763 | 0.8812 | -0.0951 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | PILE 3 | 0.9763 | 0.8812 | -0.0951 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | PILE 3 | 0.9763 | 0.8812 | -0.0951 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | PILE 3 | 0.9763 | 0.8812 | -0.0951 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | PILE 3 | 0.9763 | 0.8812 | -0.0951 |  | 0.9 | 1.05 | 0.05126 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | PILE 3 | 0.9763 | 0.8812 | -0.0951 |  | 0.9 | 1.05 | 0.0351 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | PILE 3 | 0.9763 | 0.8812 | -0.0951 |  | 0.9 | 1.05 | 0.04774 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | PILE 3 | 0.9763 | 0.8812 | -0.0951 |  | 0.9 | 1.05 | 0.05016 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | PILE 3 | 0.9763 | 0.8812 | -0.0951 |  | 0.9 | 1.05 | 0.04857 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | PILE 3 | 0.9763 | 0.8812 | -0.0951 |  | 0.9 | 1.05 | 0.05466 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | PILE 3 | 0.9763 | 0.8812 | -0.0951 |  | 0.9 | 1.05 | 0.05401 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | PILE 3 | 0.9763 | 0.8812 | -0.0951 |  | 0.9 | 1.05 | 0.03802 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | PILE 3 | 0.9763 | 0.8812 | -0.0951 |  | 0.9 | 1.05 | 0.04968 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | PILE 3 | 0.9763 | 0.8812 | -0.0951 |  | 0.9 | 1.05 | 0.04081 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | DIGHTON3 | 0.9618 | 0.8814 | -0.0804 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | DIGHTON3 | 0.9618 | 0.8814 | -0.0804 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | DIGHTON3 | 0.9618 | 0.8814 | -0.0804 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | DIGHTON3 | 0.9618 | 0.8814 | -0.0804 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | DIGHTON3 | 0.9618 | 0.8814 | -0.0804 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | DIGHTON3 | 0.9618 | 0.8814 | -0.0804 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | DIGHTON3 | 0.9618 | 0.8814 | -0.0804 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | DIGHTON3 | 0.9618 | 0.8814 | -0.0804 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | DIGHTON3 | 0.9618 | 0.8814 | -0.0804 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | DIGHTON3 | 0.9618 | 0.8814 | -0.0804 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | DIGHTON3 | 0.9618 | 0.8814 | -0.0804 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | DIGHTON3 | 0.9618 | 0.8814 | -0.0804 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | DIGHTON3 | 0.9618 | 0.8814 | -0.0804 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | DIGHTON3 | 0.9618 | 0.8814 | -0.0804 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | DIGHTON3 | 0.9618 | 0.8814 | -0.0804 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | DIGHTON3 | 0.9618 | 0.8814 | -0.0804 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | DIGHTON3 | 0.9618 | 0.8814 | -0.0804 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | DIGHTON3 | 0.9618 | 0.8814 | -0.0804 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | DIGHTON3 | 0.9618 | 0.8814 | -0.0804 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | DIGHTON3 | 0.9618 | 0.8814 | -0.0804 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | DIGHTON3 | 0.9618 | 0.8814 | -0.0804 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | DIGHTON3 | 0.9618 | 0.8814 | -0.0804 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | DIGHTON3 | 0.9618 | 0.8814 | -0.0804 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | DIGHTON3 | 0.9618 | 0.8814 | -0.0804 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | DIGHTON3 | 0.9618 | 0.8814 | -0.0804 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | DIGHTON3 | 0.9618 | 0.8814 | -0.0804 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | DIGHTON3 | 0.9618 | 0.8814 | -0.0804 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | LIBERTYT | 0.9696 | 0.8816 | -0.088 |  | 0.9 | 1.05 | 0.05095 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | LIBERTYT | 0.9696 | 0.8816 | -0.088 |  | 0.9 | 1.05 | 0.04905 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | LIBERTYT | 0.9696 | 0.8816 | -0.088 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | LIBERTYT | 0.9696 | 0.8816 | -0.088 |  | 0.9 | 1.05 | 0.04262 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | LIBERTYT | 0.9696 | 0.8816 | -0.088 |  | 0.9 | 1.05 | 0.0627 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | LIBERTYT | 0.9696 | 0.8816 | -0.088 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | LIBERTYT | 0.9696 | 0.8816 | -0.088 |  | 0.9 | 1.05 | 0.05043 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | LIBERTYT | 0.9696 | 0.8816 | -0.088 |  | 0.9 | 1.05 | 0.05292 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | LIBERTYT | 0.9696 | 0.8816 | -0.088 |  | 0.9 | 1.05 | 0.0444 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | LIBERTYT | 0.9696 | 0.8816 | -0.088 |  | 0.9 | 1.05 | 0.04788 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | LIBERTYT | 0.9696 | 0.8816 | -0.088 |  | 0.9 | 1.05 | 0.05824 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | LIBERTYT | 0.9696 | 0.8816 | -0.088 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | LIBERTYT | 0.9696 | 0.8816 | -0.088 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | LIBERTYT | 0.9696 | 0.8816 | -0.088 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | LIBERTYT | 0.9696 | 0.8816 | -0.088 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | LIBERTYT | 0.9696 | 0.8816 | -0.088 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | LIBERTYT | 0.9696 | 0.8816 | -0.088 |  | 0.9 | 1.05 | 0.04773 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | LIBERTYT | 0.9696 | 0.8816 | -0.088 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | LIBERTYT | 0.9696 | 0.8816 | -0.088 |  | 0.9 | 1.05 | 0.0348 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | LIBERTYT | 0.9696 | 0.8816 | -0.088 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | LIBERTYT | 0.9696 | 0.8816 | -0.088 |  | 0.9 | 1.05 | 0.04996 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | LIBERTYT | 0.9696 | 0.8816 | -0.088 |  | 0.9 | 1.05 | 0.04835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | LIBERTYT | 0.9696 | 0.8816 | -0.088 |  | 0.9 | 1.05 | 0.05448 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | LIBERTYT | 0.9696 | 0.8816 | -0.088 |  | 0.9 | 1.05 | 0.05382 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | LIBERTYT | 0.9696 | 0.8816 | -0.088 |  | 0.9 | 1.05 | 0.03774 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | LIBERTYT | 0.9696 | 0.8816 | -0.088 |  | 0.9 | 1.05 | 0.04948 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | LIBERTYT | 0.9696 | 0.8816 | -0.088 |  | 0.9 | 1.05 | 0.04054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | WTCLFTP3 | 0.9605 | 0.8818 | -0.0787 |  | 0.9 | 1.05 | 0.05101 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | WTCLFTP3 | 0.9605 | 0.8818 | -0.0787 |  | 0.9 | 1.05 | 0.04911 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | WTCLFTP3 | 0.9605 | 0.8818 | -0.0787 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | WTCLFTP3 | 0.9605 | 0.8818 | -0.0787 |  | 0.9 | 1.05 | 0.04272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | WTCLFTP3 | 0.9605 | 0.8818 | -0.0787 |  | 0.9 | 1.05 | 0.06272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | WTCLFTP3 | 0.9605 | 0.8818 | -0.0787 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | WTCLFTP3 | 0.9605 | 0.8818 | -0.0787 |  | 0.9 | 1.05 | 0.05049 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | WTCLFTP3 | 0.9605 | 0.8818 | -0.0787 |  | 0.9 | 1.05 | 0.05297 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | WTCLFTP3 | 0.9605 | 0.8818 | -0.0787 |  | 0.9 | 1.05 | 0.04447 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | WTCLFTP3 | 0.9605 | 0.8818 | -0.0787 |  | 0.9 | 1.05 | 0.04795 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | WTCLFTP3 | 0.9605 | 0.8818 | -0.0787 |  | 0.9 | 1.05 | 0.05827 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | WTCLFTP3 | 0.9605 | 0.8818 | -0.0787 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | WTCLFTP3 | 0.9605 | 0.8818 | -0.0787 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | WTCLFTP3 | 0.9605 | 0.8818 | -0.0787 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | WTCLFTP3 | 0.9605 | 0.8818 | -0.0787 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2