Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | WTCLFTP3 | 0.9605 | 0.8818 | -0.0787 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | WTCLFTP3 | 0.9605 | 0.8818 | -0.0787 |  | 0.9 | 1.05 | 0.04781 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | WTCLFTP3 | 0.9605 | 0.8818 | -0.0787 |  | 0.9 | 1.05 | 0.05112 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | WTCLFTP3 | 0.9605 | 0.8818 | -0.0787 |  | 0.9 | 1.05 | 0.03494 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | WTCLFTP3 | 0.9605 | 0.8818 | -0.0787 |  | 0.9 | 1.05 | 0.04759 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | WTCLFTP3 | 0.9605 | 0.8818 | -0.0787 |  | 0.9 | 1.05 | 0.05002 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | WTCLFTP3 | 0.9605 | 0.8818 | -0.0787 |  | 0.9 | 1.05 | 0.04842 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | WTCLFTP3 | 0.9605 | 0.8818 | -0.0787 |  | 0.9 | 1.05 | 0.05452 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | WTCLFTP3 | 0.9605 | 0.8818 | -0.0787 |  | 0.9 | 1.05 | 0.05387 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | WTCLFTP3 | 0.9605 | 0.8818 | -0.0787 |  | 0.9 | 1.05 | 0.03786 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | WTCLFTP3 | 0.9605 | 0.8818 | -0.0787 |  | 0.9 | 1.05 | 0.04954 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | WTCLFTP3 | 0.9605 | 0.8818 | -0.0787 |  | 0.9 | 1.05 | 0.04065 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | JAGGER 3 | 0.9624 | 0.8821 | -0.0803 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | JAGGER 3 | 0.9624 | 0.8821 | -0.0803 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | JAGGER 3 | 0.9624 | 0.8821 | -0.0803 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | JAGGER 3 | 0.9624 | 0.8821 | -0.0803 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | JAGGER 3 | 0.9624 | 0.8821 | -0.0803 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | JAGGER 3 | 0.9624 | 0.8821 | -0.0803 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | JAGGER 3 | 0.9624 | 0.8821 | -0.0803 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | JAGGER 3 | 0.9624 | 0.8821 | -0.0803 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | JAGGER 3 | 0.9624 | 0.8821 | -0.0803 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | JAGGER 3 | 0.9624 | 0.8821 | -0.0803 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | JAGGER 3 | 0.9624 | 0.8821 | -0.0803 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | JAGGER 3 | 0.9624 | 0.8821 | -0.0803 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | JAGGER 3 | 0.9624 | 0.8821 | -0.0803 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | JAGGER 3 | 0.9624 | 0.8821 | -0.0803 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | JAGGER 3 | 0.9624 | 0.8821 | -0.0803 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | JAGGER 3 | 0.9624 | 0.8821 | -0.0803 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | JAGGER 3 | 0.9624 | 0.8821 | -0.0803 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | JAGGER 3 | 0.9624 | 0.8821 | -0.0803 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | JAGGER 3 | 0.9624 | 0.8821 | -0.0803 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | JAGGER 3 | 0.9624 | 0.8821 | -0.0803 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | JAGGER 3 | 0.9624 | 0.8821 | -0.0803 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | JAGGER 3 | 0.9624 | 0.8821 | -0.0803 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | JAGGER 3 | 0.9624 | 0.8821 | -0.0803 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | JAGGER 3 | 0.9624 | 0.8821 | -0.0803 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | JAGGER 3 | 0.9624 | 0.8821 | -0.0803 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | JAGGER 3 | 0.9624 | 0.8821 | -0.0803 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | JAGGER 3 | 0.9624 | 0.8821 | -0.0803 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | CHASE 3 | 0.9603 | 0.8823 | -0.078 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | CHASE 3 | 0.9603 | 0.8823 | -0.078 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | CHASE 3 | 0.9603 | 0.8823 | -0.078 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | CHASE 3 | 0.9603 | 0.8823 | -0.078 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | CHASE 3 | 0.9603 | 0.8823 | -0.078 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | CHASE 3 | 0.9603 | 0.8823 | -0.078 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | CHASE 3 | 0.9603 | 0.8823 | -0.078 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | CHASE 3 | 0.9603 | 0.8823 | -0.078 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | CHASE 3 | 0.9603 | 0.8823 | -0.078 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | CHASE 3 | 0.9603 | 0.8823 | -0.078 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | CHASE 3 | 0.9603 | 0.8823 | -0.078 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | CHASE 3 | 0.9603 | 0.8823 | -0.078 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | CHASE 3 | 0.9603 | 0.8823 | -0.078 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | CHASE 3 | 0.9603 | 0.8823 | -0.078 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | CHASE 3 | 0.9603 | 0.8823 | -0.078 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | CHASE 3 | 0.9603 | 0.8823 | -0.078 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | CHASE 3 | 0.9603 | 0.8823 | -0.078 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | CHASE 3 | 0.9603 | 0.8823 | -0.078 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | CHASE 3 | 0.9603 | 0.8823 | -0.078 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | CHASE 3 | 0.9603 | 0.8823 | -0.078 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | CHASE 3 | 0.9603 | 0.8823 | -0.078 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | CHASE 3 | 0.9603 | 0.8823 | -0.078 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | CHASE 3 | 0.9603 | 0.8823 | -0.078 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | CHASE 3 | 0.9603 | 0.8823 | -0.078 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | CHASE 3 | 0.9603 | 0.8823 | -0.078 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | CHASE 3 | 0.9603 | 0.8823 | -0.078 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | CHASE 3 | 0.9603 | 0.8823 | -0.078 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | SHARNSP3 | 0.9604 | 0.8824 | -0.078 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | ARNOLD3 | 0.9827 | 0.8824 | -0.1003 |  | 0.9 | 1.05 | 0.05095 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | SHARNSP3 | 0.9604 | 0.8824 | -0.078 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | ARNOLD3 | 0.9827 | 0.8824 | -0.1003 |  | 0.9 | 1.05 | 0.04905 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | SHARNSP3 | 0.9604 | 0.8824 | -0.078 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | ARNOLD3 | 0.9827 | 0.8824 | -0.1003 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | SHARNSP3 | 0.9604 | 0.8824 | -0.078 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | ARNOLD3 | 0.9827 | 0.8824 | -0.1003 |  | 0.9 | 1.05 | 0.04262 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | SHARNSP3 | 0.9604 | 0.8824 | -0.078 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | ARNOLD3 | 0.9827 | 0.8824 | -0.1003 |  | 0.9 | 1.05 | 0.0627 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | SHARNSP3 | 0.9604 | 0.8824 | -0.078 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | ARNOLD3 | 0.9827 | 0.8824 | -0.1003 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | SHARNSP3 | 0.9604 | 0.8824 | -0.078 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | ARNOLD3 | 0.9827 | 0.8824 | -0.1003 |  | 0.9 | 1.05 | 0.05043 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | SHARNSP3 | 0.9604 | 0.8824 | -0.078 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | ARNOLD3 | 0.9827 | 0.8824 | -0.1003 |  | 0.9 | 1.05 | 0.05292 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | SHARNSP3 | 0.9604 | 0.8824 | -0.078 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | ARNOLD3 | 0.9827 | 0.8824 | -0.1003 |  | 0.9 | 1.05 | 0.0444 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | SHARNSP3 | 0.9604 | 0.8824 | -0.078 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | ARNOLD3 | 0.9827 | 0.8824 | -0.1003 |  | 0.9 | 1.05 | 0.04788 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | SHARNSP3 | 0.9604 | 0.8824 | -0.078 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | ARNOLD3 | 0.9827 | 0.8824 | -0.1003 |  | 0.9 | 1.05 | 0.05824 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | SHARNSP3 | 0.9604 | 0.8824 | -0.078 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | ARNOLD3 | 0.9827 | 0.8824 | -0.1003 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | SHARNSP3 | 0.9604 | 0.8824 | -0.078 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | ARNOLD3 | 0.9827 | 0.8824 | -0.1003 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | SHARNSP3 | 0.9604 | 0.8824 | -0.078 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | ARNOLD3 | 0.9827 | 0.8824 | -0.1003 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | SHARNSP3 | 0.9604 | 0.8824 | -0.078 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | ARNOLD3 | 0.9827 | 0.8824 | -0.1003 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | SHARNSP3 | 0.9604 | 0.8824 | -0.078 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | ARNOLD3 | 0.9827 | 0.8824 | -0.1003 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | SHARNSP3 | 0.9604 | 0.8824 | -0.078 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | ARNOLD3 | 0.9827 | 0.8824 | -0.1003 |  | 0.9 | 1.05 | 0.04773 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | SHARNSP3 | 0.9604 | 0.8824 | -0.078 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | ARNOLD3 | 0.9827 | 0.8824 | -0.1003 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | SHARNSP3 | 0.9604 | 0.8824 | -0.078 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | ARNOLD3 | 0.9827 | 0.8824 | -0.1003 |  | 0.9 | 1.05 | 0.0348 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | SHARNSP3 | 0.9604 | 0.8824 | -0.078 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | ARNOLD3 | 0.9827 | 0.8824 | -0.1003 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | SHARNSP3 | 0.9604 | 0.8824 | -0.078 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | ARNOLD3 | 0.9827 | 0.8824 | -0.1003 |  | 0.9 | 1.05 | 0.04996 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | SHARNSP3 | 0.9604 | 0.8824 | -0.078 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | ARNOLD3 | 0.9827 | 0.8824 | -0.1003 |  | 0.9 | 1.05 | 0.04835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | SHARNSP3 | 0.9604 | 0.8824 | -0.078 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | ARNOLD3 | 0.9827 | 0.8824 | -0.1003 |  | 0.9 | 1.05 | 0.05448 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | SHARNSP3 | 0.9604 | 0.8824 | -0.078 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | ARNOLD3 | 0.9827 | 0.8824 | -0.1003 |  | 0.9 | 1.05 | 0.05382 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | SHARNSP3 | 0.9604 | 0.8824 | -0.078 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | ARNOLD3 | 0.9827 | 0.8824 | -0.1003 |  | 0.9 | 1.05 | 0.03774 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | SHARNSP3 | 0.9604 | 0.8824 | -0.078 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | ARNOLD3 | 0.9827 | 0.8824 | -0.1003 |  | 0.9 | 1.05 | 0.04948 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | SHARNSP3 | 0.9604 | 0.8824 | -0.078 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | ARNOLD3 | 0.9827 | 0.8824 | -0.1003 |  | 0.9 | 1.05 | 0.04054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | PILE 3 | 0.9644 | 0.8828 | -0.0816 |  | 0.9 | 1.05 | 0.05101 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | PILE 3 | 0.9644 | 0.8828 | -0.0816 |  | 0.9 | 1.05 | 0.04911 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | PILE 3 | 0.9644 | 0.8828 | -0.0816 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | PILE 3 | 0.9644 | 0.8828 | -0.0816 |  | 0.9 | 1.05 | 0.04272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | PILE 3 | 0.9644 | 0.8828 | -0.0816 |  | 0.9 | 1.05 | 0.06272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | PILE 3 | 0.9644 | 0.8828 | -0.0816 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | PILE 3 | 0.9644 | 0.8828 | -0.0816 |  | 0.9 | 1.05 | 0.05049 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | PILE 3 | 0.9644 | 0.8828 | -0.0816 |  | 0.9 | 1.05 | 0.05297 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | PILE 3 | 0.9644 | 0.8828 | -0.0816 |  | 0.9 | 1.05 | 0.04447 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | PILE 3 | 0.9644 | 0.8828 | -0.0816 |  | 0.9 | 1.05 | 0.04795 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | PILE 3 | 0.9644 | 0.8828 | -0.0816 |  | 0.9 | 1.05 | 0.05827 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | PILE 3 | 0.9644 | 0.8828 | -0.0816 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | PILE 3 | 0.9644 | 0.8828 | -0.0816 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | PILE 3 | 0.9644 | 0.8828 | -0.0816 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | PILE 3 | 0.9644 | 0.8828 | -0.0816 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | PILE 3 | 0.9644 | 0.8828 | -0.0816 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | PILE 3 | 0.9644 | 0.8828 | -0.0816 |  | 0.9 | 1.05 | 0.04781 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | PILE 3 | 0.9644 | 0.8828 | -0.0816 |  | 0.9 | 1.05 | 0.05112 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | PILE 3 | 0.9644 | 0.8828 | -0.0816 |  | 0.9 | 1.05 | 0.03494 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | PILE 3 | 0.9644 | 0.8828 | -0.0816 |  | 0.9 | 1.05 | 0.04759 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | PILE 3 | 0.9644 | 0.8828 | -0.0816 |  | 0.9 | 1.05 | 0.05002 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | PILE 3 | 0.9644 | 0.8828 | -0.0816 |  | 0.9 | 1.05 | 0.04842 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | PILE 3 | 0.9644 | 0.8828 | -0.0816 |  | 0.9 | 1.05 | 0.05452 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | PILE 3 | 0.9644 | 0.8828 | -0.0816 |  | 0.9 | 1.05 | 0.05387 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | PILE 3 | 0.9644 | 0.8828 | -0.0816 |  | 0.9 | 1.05 | 0.03786 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | PILE 3 | 0.9644 | 0.8828 | -0.0816 |  | 0.9 | 1.05 | 0.04954 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | PILE 3 | 0.9644 | 0.8828 | -0.0816 |  | 0.9 | 1.05 | 0.04065 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | CSTFRAN3 | 0.9837 | 0.883 | -0.1007 |  | 0.9 | 1.05 | 0.05095 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | CSTFRAN3 | 0.9837 | 0.883 | -0.1007 |  | 0.9 | 1.05 | 0.04905 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | CSTFRAN3 | 0.9837 | 0.883 | -0.1007 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | CSTFRAN3 | 0.9837 | 0.883 | -0.1007 |  | 0.9 | 1.05 | 0.04262 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | CSTFRAN3 | 0.9837 | 0.883 | -0.1007 |  | 0.9 | 1.05 | 0.0627 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | CSTFRAN3 | 0.9837 | 0.883 | -0.1007 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | CSTFRAN3 | 0.9837 | 0.883 | -0.1007 |  | 0.9 | 1.05 | 0.05043 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | CSTFRAN3 | 0.9837 | 0.883 | -0.1007 |  | 0.9 | 1.05 | 0.05292 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | CSTFRAN3 | 0.9837 | 0.883 | -0.1007 |  | 0.9 | 1.05 | 0.0444 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | CSTFRAN3 | 0.9837 | 0.883 | -0.1007 |  | 0.9 | 1.05 | 0.04788 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | CSTFRAN3 | 0.9837 | 0.883 | -0.1007 |  | 0.9 | 1.05 | 0.05824 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | CSTFRAN3 | 0.9837 | 0.883 | -0.1007 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | CSTFRAN3 | 0.9837 | 0.883 | -0.1007 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | CSTFRAN3 | 0.9837 | 0.883 | -0.1007 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | CSTFRAN3 | 0.9837 | 0.883 | -0.1007 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | CSTFRAN3 | 0.9837 | 0.883 | -0.1007 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | CSTFRAN3 | 0.9837 | 0.883 | -0.1007 |  | 0.9 | 1.05 | 0.04773 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | CSTFRAN3 | 0.9837 | 0.883 | -0.1007 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | CSTFRAN3 | 0.9837 | 0.883 | -0.1007 |  | 0.9 | 1.05 | 0.0348 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | CSTFRAN3 | 0.9837 | 0.883 | -0.1007 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | CSTFRAN3 | 0.9837 | 0.883 | -0.1007 |  | 0.9 | 1.05 | 0.04996 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | CSTFRAN3 | 0.9837 | 0.883 | -0.1007 |  | 0.9 | 1.05 | 0.04835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | CSTFRAN3 | 0.9837 | 0.883 | -0.1007 |  | 0.9 | 1.05 | 0.05448 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | CSTFRAN3 | 0.9837 | 0.883 | -0.1007 |  | 0.9 | 1.05 | 0.05382 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | CSTFRAN3 | 0.9837 | 0.883 | -0.1007 |  | 0.9 | 1.05 | 0.03774 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | CSTFRAN3 | 0.9837 | 0.883 | -0.1007 |  | 0.9 | 1.05 | 0.04948 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | CSTFRAN3 | 0.9837 | 0.883 | -0.1007 |  | 0.9 | 1.05 | 0.04054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | GOODCTY3 | 0.9943 | 0.8831 | -0.1112 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | GOODCTY3 | 0.998 | 0.8831 | -0.1149 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | GOODCTY3 | 0.9943 | 0.8831 | -0.1112 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | GOODCTY3 | 0.998 | 0.8831 | -0.1149 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | GOODCTY3 | 0.9943 | 0.8831 | -0.1112 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | GOODCTY3 | 0.998 | 0.8831 | -0.1149 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | GOODCTY3 | 0.9943 | 0.8831 | -0.1112 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | GOODCTY3 | 0.998 | 0.8831 | -0.1149 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | GOODCTY3 | 0.9943 | 0.8831 | -0.1112 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | GOODCTY3 | 0.998 | 0.8831 | -0.1149 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | GOODCTY3 | 0.9943 | 0.8831 | -0.1112 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | GOODCTY3 | 0.998 | 0.8831 | -0.1149 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | GOODCTY3 | 0.9943 | 0.8831 | -0.1112 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | GOODCTY3 | 0.998 | 0.8831 | -0.1149 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | GOODCTY3 | 0.9943 | 0.8831 | -0.1112 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | GOODCTY3 | 0.998 | 0.8831 | -0.1149 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | GOODCTY3 | 0.9943 | 0.8831 | -0.1112 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | GOODCTY3 | 0.998 | 0.8831 | -0.1149 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | GOODCTY3 | 0.9943 | 0.8831 | -0.1112 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | GOODCTY3 | 0.998 | 0.8831 | -0.1149 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | GOODCTY3 | 0.9943 | 0.8831 | -0.1112 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | GOODCTY3 | 0.998 | 0.8831 | -0.1149 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | GOODCTY3 | 0.9943 | 0.8831 | -0.1112 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | GOODCTY3 | 0.998 | 0.8831 | -0.1149 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | GOODCTY3 | 0.9943 | 0.8831 | -0.1112 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | GOODCTY3 | 0.998 | 0.8831 | -0.1149 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | GOODCTY3 | 0.9943 | 0.8831 | -0.1112 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | GOODCTY3 | 0.998 | 0.8831 | -0.1149 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | GOODCTY3 | 0.9943 | 0.8831 | -0.1112 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | GOODCTY3 | 0.998 | 0.8831 | -0.1149 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | GOODCTY3 | 0.9943 | 0.8831 | -0.1112 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | GOODCTY3 | 0.998 | 0.8831 | -0.1149 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | GOODCTY3 | 0.9943 | 0.8831 | -0.1112 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | GOODCTY3 | 0.998 | 0.8831 | -0.1149 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | GOODCTY3 | 0.9943 | 0.8831 | -0.1112 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | GOODCTY3 | 0.998 | 0.8831 | -0.1149 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | GOODCTY3 | 0.9943 | 0.8831 | -0.1112 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | GOODCTY3 | 0.998 | 0.8831 | -0.1149 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | GOODCTY3 | 0.9943 | 0.8831 | -0.1112 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | GOODCTY3 | 0.998 | 0.8831 | -0.1149 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | GOODCTY3 | 0.9943 | 0.8831 | -0.1112 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | GOODCTY3 | 0.998 | 0.8831 | -0.1149 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | GOODCTY3 | 0.9943 | 0.8831 | -0.1112 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | GOODCTY3 | 0.998 | 0.8831 | -0.1149 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | GOODCTY3 | 0.9943 | 0.8831 | -0.1112 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | GOODCTY3 | 0.998 | 0.8831 | -0.1149 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | GOODCTY3 | 0.9943 | 0.8831 | -0.1112 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | GOODCTY3 | 0.998 | 0.8831 | -0.1149 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | GOODCTY3 | 0.9943 | 0.8831 | -0.1112 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | GOODCTY3 | 0.998 | 0.8831 | -0.1149 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | GOODCTY3 | 0.9943 | 0.8831 | -0.1112 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | GOODCTY3 | 0.998 | 0.8831 | -0.1149 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | GOODCTY3 | 0.9943 | 0.8831 | -0.1112 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | GOODCTY3 | 0.998 | 0.8831 | -0.1149 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | STFRANT3 | 0.9838 | 0.8832 | -0.1006 |  | 0.9 | 1.05 | 0.05095 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | STFRANT3 | 0.9838 | 0.8832 | -0.1006 |  | 0.9 | 1.05 | 0.04905 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | STFRANT3 | 0.9838 | 0.8832 | -0.1006 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | STFRANT3 | 0.9838 | 0.8832 | -0.1006 |  | 0.9 | 1.05 | 0.04262 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | STFRANT3 | 0.9838 | 0.8832 | -0.1006 |  | 0.9 | 1.05 | 0.0627 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | STFRANT3 | 0.9838 | 0.8832 | -0.1006 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | STFRANT3 | 0.9838 | 0.8832 | -0.1006 |  | 0.9 | 1.05 | 0.05043 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | STFRANT3 | 0.9838 | 0.8832 | -0.1006 |  | 0.9 | 1.05 | 0.05292 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | STFRANT3 | 0.9838 | 0.8832 | -0.1006 |  | 0.9 | 1.05 | 0.0444 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | STFRANT3 | 0.9838 | 0.8832 | -0.1006 |  | 0.9 | 1.05 | 0.04788 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | STFRANT3 | 0.9838 | 0.8832 | -0.1006 |  | 0.9 | 1.05 | 0.05824 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | STFRANT3 | 0.9838 | 0.8832 | -0.1006 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | STFRANT3 | 0.9838 | 0.8832 | -0.1006 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | STFRANT3 | 0.9838 | 0.8832 | -0.1006 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | STFRANT3 | 0.9838 | 0.8832 | -0.1006 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | STFRANT3 | 0.9838 | 0.8832 | -0.1006 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | STFRANT3 | 0.9838 | 0.8832 | -0.1006 |  | 0.9 | 1.05 | 0.04773 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | STFRANT3 | 0.9838 | 0.8832 | -0.1006 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | STFRANT3 | 0.9838 | 0.8832 | -0.1006 |  | 0.9 | 1.05 | 0.0348 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | STFRANT3 | 0.9838 | 0.8832 | -0.1006 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | STFRANT3 | 0.9838 | 0.8832 | -0.1006 |  | 0.9 | 1.05 | 0.04996 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | STFRANT3 | 0.9838 | 0.8832 | -0.1006 |  | 0.9 | 1.05 | 0.04835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | STFRANT3 | 0.9838 | 0.8832 | -0.1006 |  | 0.9 | 1.05 | 0.05448 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | STFRANT3 | 0.9838 | 0.8832 | -0.1006 |  | 0.9 | 1.05 | 0.05382 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | STFRANT3 | 0.9838 | 0.8832 | -0.1006 |  | 0.9 | 1.05 | 0.03774 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | STFRANT3 | 0.9838 | 0.8832 | -0.1006 |  | 0.9 | 1.05 | 0.04948 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | STFRANT3 | 0.9838 | 0.8832 | -0.1006 |  | 0.9 | 1.05 | 0.04054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | PALMER3 | 0.9672 | 0.8835 | -0.0837 |  | 0.9 | 1.05 | 0.05101 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | PALMER3 | 0.9672 | 0.8835 | -0.0837 |  | 0.9 | 1.05 | 0.04911 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | PALMER3 | 0.9672 | 0.8835 | -0.0837 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | PALMER3 | 0.9672 | 0.8835 | -0.0837 |  | 0.9 | 1.05 | 0.04272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | PALMER3 | 0.9672 | 0.8835 | -0.0837 |  | 0.9 | 1.05 | 0.06272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | PALMER3 | 0.9672 | 0.8835 | -0.0837 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | PALMER3 | 0.9672 | 0.8835 | -0.0837 |  | 0.9 | 1.05 | 0.05049 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | PALMER3 | 0.9672 | 0.8835 | -0.0837 |  | 0.9 | 1.05 | 0.05297 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | PALMER3 | 0.9672 | 0.8835 | -0.0837 |  | 0.9 | 1.05 | 0.04447 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | PALMER3 | 0.9672 | 0.8835 | -0.0837 |  | 0.9 | 1.05 | 0.04795 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | PALMER3 | 0.9672 | 0.8835 | -0.0837 |  | 0.9 | 1.05 | 0.05827 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | PALMER3 | 0.9672 | 0.8835 | -0.0837 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | PALMER3 | 0.9672 | 0.8835 | -0.0837 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | PALMER3 | 0.9672 | 0.8835 | -0.0837 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | PALMER3 | 0.9672 | 0.8835 | -0.0837 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | PALMER3 | 0.9672 | 0.8835 | -0.0837 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | PALMER3 | 0.9672 | 0.8835 | -0.0837 |  | 0.9 | 1.05 | 0.04781 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | PALMER3 | 0.9672 | 0.8835 | -0.0837 |  | 0.9 | 1.05 | 0.05112 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | PALMER3 | 0.9672 | 0.8835 | -0.0837 |  | 0.9 | 1.05 | 0.03494 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | PALMER3 | 0.9672 | 0.8835 | -0.0837 |  | 0.9 | 1.05 | 0.04759 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | PALMER3 | 0.9672 | 0.8835 | -0.0837 |  | 0.9 | 1.05 | 0.05002 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | PALMER3 | 0.9672 | 0.8835 | -0.0837 |  | 0.9 | 1.05 | 0.04842 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | PALMER3 | 0.9672 | 0.8835 | -0.0837 |  | 0.9 | 1.05 | 0.05452 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | PALMER3 | 0.9672 | 0.8835 | -0.0837 |  | 0.9 | 1.05 | 0.05387 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | PALMER3 | 0.9672 | 0.8835 | -0.0837 |  | 0.9 | 1.05 | 0.03786 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | PALMER3 | 0.9672 | 0.8835 | -0.0837 |  | 0.9 | 1.05 | 0.04954 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | PALMER3 | 0.9672 | 0.8835 | -0.0837 |  | 0.9 | 1.05 | 0.04065 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | BIRDCTY3 | 0.9683 | 0.8837 | -0.0846 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | BIRDCTY3 | 0.9683 | 0.8837 | -0.0846 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | BIRDCTY3 | 0.9683 | 0.8837 | -0.0846 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | BIRDCTY3 | 0.9683 | 0.8837 | -0.0846 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | BIRDCTY3 | 0.9683 | 0.8837 | -0.0846 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | BIRDCTY3 | 0.9683 | 0.8837 | -0.0846 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | BIRDCTY3 | 0.9683 | 0.8837 | -0.0846 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | BIRDCTY3 | 0.9683 | 0.8837 | -0.0846 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | BIRDCTY3 | 0.9683 | 0.8837 | -0.0846 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | BIRDCTY3 | 0.9683 | 0.8837 | -0.0846 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | BIRDCTY3 | 0.9683 | 0.8837 | -0.0846 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | BIRDCTY3 | 0.9683 | 0.8837 | -0.0846 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | BIRDCTY3 | 0.9683 | 0.8837 | -0.0846 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | BIRDCTY3 | 0.9683 | 0.8837 | -0.0846 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | BIRDCTY3 | 0.9683 | 0.8837 | -0.0846 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | BIRDCTY3 | 0.9683 | 0.8837 | -0.0846 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | BIRDCTY3 | 0.9683 | 0.8837 | -0.0846 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | BIRDCTY3 | 0.9683 | 0.8837 | -0.0846 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | BIRDCTY3 | 0.9683 | 0.8837 | -0.0846 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | BIRDCTY3 | 0.9683 | 0.8837 | -0.0846 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | BIRDCTY3 | 0.9683 | 0.8837 | -0.0846 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | BIRDCTY3 | 0.9683 | 0.8837 | -0.0846 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | BIRDCTY3 | 0.9683 | 0.8837 | -0.0846 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | BIRDCTY3 | 0.9683 | 0.8837 | -0.0846 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | BIRDCTY3 | 0.9683 | 0.8837 | -0.0846 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | BIRDCTY3 | 0.9683 | 0.8837 | -0.0846 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | BIRDCTY3 | 0.9683 | 0.8837 | -0.0846 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | PALMER3 | 0.9792 | 0.8844 | -0.0948 |  | 0.9 | 1.05 | 0.05115 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | PALMER3 | 0.9792 | 0.8844 | -0.0948 |  | 0.9 | 1.05 | 0.04926 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | PALMER3 | 0.9792 | 0.8844 | -0.0948 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | PALMER3 | 0.9792 | 0.8844 | -0.0948 |  | 0.9 | 1.05 | 0.04287 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | PALMER3 | 0.9792 | 0.8844 | -0.0948 |  | 0.9 | 1.05 | 0.06285 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | PALMER3 | 0.9792 | 0.8844 | -0.0948 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | PALMER3 | 0.9792 | 0.8844 | -0.0948 |  | 0.9 | 1.05 | 0.05063 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | PALMER3 | 0.9792 | 0.8844 | -0.0948 |  | 0.9 | 1.05 | 0.05311 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | PALMER3 | 0.9792 | 0.8844 | -0.0948 |  | 0.9 | 1.05 | 0.04461 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | PALMER3 | 0.9792 | 0.8844 | -0.0948 |  | 0.9 | 1.05 | 0.0481 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | PALMER3 | 0.9792 | 0.8844 | -0.0948 |  | 0.9 | 1.05 | 0.0584 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | PALMER3 | 0.9792 | 0.8844 | -0.0948 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | PALMER3 | 0.9792 | 0.8844 | -0.0948 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | PALMER3 | 0.9792 | 0.8844 | -0.0948 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | PALMER3 | 0.9792 | 0.8844 | -0.0948 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | PALMER3 | 0.9792 | 0.8844 | -0.0948 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | PALMER3 | 0.9792 | 0.8844 | -0.0948 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | PALMER3 | 0.9792 | 0.8844 | -0.0948 |  | 0.9 | 1.05 | 0.05126 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | PALMER3 | 0.9792 | 0.8844 | -0.0948 |  | 0.9 | 1.05 | 0.0351 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | PALMER3 | 0.9792 | 0.8844 | -0.0948 |  | 0.9 | 1.05 | 0.04774 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | PALMER3 | 0.9792 | 0.8844 | -0.0948 |  | 0.9 | 1.05 | 0.05016 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | PALMER3 | 0.9792 | 0.8844 | -0.0948 |  | 0.9 | 1.05 | 0.04857 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | PALMER3 | 0.9792 | 0.8844 | -0.0948 |  | 0.9 | 1.05 | 0.05466 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | PALMER3 | 0.9792 | 0.8844 | -0.0948 |  | 0.9 | 1.05 | 0.05401 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | PALMER3 | 0.9792 | 0.8844 | -0.0948 |  | 0.9 | 1.05 | 0.03802 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | PALMER3 | 0.9792 | 0.8844 | -0.0948 |  | 0.9 | 1.05 | 0.04968 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | PALMER3 | 0.9792 | 0.8844 | -0.0948 |  | 0.9 | 1.05 | 0.04081 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | LIBERTYT | 0.9601 | 0.8855 | -0.0746 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | STFRAN 3 | 0.9837 | 0.8855 | -0.0982 |  | 0.9 | 1.05 | 0.05095 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | LIBERTYT | 0.9601 | 0.8855 | -0.0746 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | STFRAN 3 | 0.9837 | 0.8855 | -0.0982 |  | 0.9 | 1.05 | 0.04905 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | LIBERTYT | 0.9601 | 0.8855 | -0.0746 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | STFRAN 3 | 0.9837 | 0.8855 | -0.0982 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | LIBERTYT | 0.9601 | 0.8855 | -0.0746 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | STFRAN 3 | 0.9837 | 0.8855 | -0.0982 |  | 0.9 | 1.05 | 0.04262 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | LIBERTYT | 0.9601 | 0.8855 | -0.0746 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | STFRAN 3 | 0.9837 | 0.8855 | -0.0982 |  | 0.9 | 1.05 | 0.0627 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | LIBERTYT | 0.9601 | 0.8855 | -0.0746 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | STFRAN 3 | 0.9837 | 0.8855 | -0.0982 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | LIBERTYT | 0.9601 | 0.8855 | -0.0746 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | STFRAN 3 | 0.9837 | 0.8855 | -0.0982 |  | 0.9 | 1.05 | 0.05043 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | LIBERTYT | 0.9601 | 0.8855 | -0.0746 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | STFRAN 3 | 0.9837 | 0.8855 | -0.0982 |  | 0.9 | 1.05 | 0.05292 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | LIBERTYT | 0.9601 | 0.8855 | -0.0746 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | STFRAN 3 | 0.9837 | 0.8855 | -0.0982 |  | 0.9 | 1.05 | 0.0444 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | LIBERTYT | 0.9601 | 0.8855 | -0.0746 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | STFRAN 3 | 0.9837 | 0.8855 | -0.0982 |  | 0.9 | 1.05 | 0.04788 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | LIBERTYT | 0.9601 | 0.8855 | -0.0746 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | STFRAN 3 | 0.9837 | 0.8855 | -0.0982 |  | 0.9 | 1.05 | 0.05824 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | LIBERTYT | 0.9601 | 0.8855 | -0.0746 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | STFRAN 3 | 0.9837 | 0.8855 | -0.0982 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | LIBERTYT | 0.9601 | 0.8855 | -0.0746 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | STFRAN 3 | 0.9837 | 0.8855 | -0.0982 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | LIBERTYT | 0.9601 | 0.8855 | -0.0746 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | STFRAN 3 | 0.9837 | 0.8855 | -0.0982 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | LIBERTYT | 0.9601 | 0.8855 | -0.0746 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | STFRAN 3 | 0.9837 | 0.8855 | -0.0982 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | LIBERTYT | 0.9601 | 0.8855 | -0.0746 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | STFRAN 3 | 0.9837 | 0.8855 | -0.0982 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | LIBERTYT | 0.9601 | 0.8855 | -0.0746 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | STFRAN 3 | 0.9837 | 0.8855 | -0.0982 |  | 0.9 | 1.05 | 0.04773 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | LIBERTYT | 0.9601 | 0.8855 | -0.0746 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | STFRAN 3 | 0.9837 | 0.8855 | -0.0982 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | LIBERTYT | 0.9601 | 0.8855 | -0.0746 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | STFRAN 3 | 0.9837 | 0.8855 | -0.0982 |  | 0.9 | 1.05 | 0.0348 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | LIBERTYT | 0.9601 | 0.8855 | -0.0746 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | STFRAN 3 | 0.9837 | 0.8855 | -0.0982 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | LIBERTYT | 0.9601 | 0.8855 | -0.0746 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | STFRAN 3 | 0.9837 | 0.8855 | -0.0982 |  | 0.9 | 1.05 | 0.04996 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | LIBERTYT | 0.9601 | 0.8855 | -0.0746 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | STFRAN 3 | 0.9837 | 0.8855 | -0.0982 |  | 0.9 | 1.05 | 0.04835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | LIBERTYT | 0.9601 | 0.8855 | -0.0746 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | STFRAN 3 | 0.9837 | 0.8855 | -0.0982 |  | 0.9 | 1.05 | 0.05448 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | LIBERTYT | 0.9601 | 0.8855 | -0.0746 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | STFRAN 3 | 0.9837 | 0.8855 | -0.0982 |  | 0.9 | 1.05 | 0.05382 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | LIBERTYT | 0.9601 | 0.8855 | -0.0746 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | STFRAN 3 | 0.9837 | 0.8855 | -0.0982 |  | 0.9 | 1.05 | 0.03774 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | LIBERTYT | 0.9601 | 0.8855 | -0.0746 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | STFRAN 3 | 0.9837 | 0.8855 | -0.0982 |  | 0.9 | 1.05 | 0.04948 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | LIBERTYT | 0.9601 | 0.8855 | -0.0746 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | STFRAN 3 | 0.9837 | 0.8855 | -0.0982 |  | 0.9 | 1.05 | 0.04054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | WTCLF 3 | 0.9595 | 0.8858 | -0.0737 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | WTCLF 3 | 0.9595 | 0.8858 | -0.0737 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | WTCLF 3 | 0.9595 | 0.8858 | -0.0737 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | WTCLF 3 | 0.9595 | 0.8858 | -0.0737 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | WTCLF 3 | 0.9595 | 0.8858 | -0.0737 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | WTCLF 3 | 0.9595 | 0.8858 | -0.0737 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | WTCLF 3 | 0.9595 | 0.8858 | -0.0737 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | WTCLF 3 | 0.9595 | 0.8858 | -0.0737 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | WTCLF 3 | 0.9595 | 0.8858 | -0.0737 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | WTCLF 3 | 0.9595 | 0.8858 | -0.0737 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | WTCLF 3 | 0.9595 | 0.8858 | -0.0737 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | WTCLF 3 | 0.9595 | 0.8858 | -0.0737 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | WTCLF 3 | 0.9595 | 0.8858 | -0.0737 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | WTCLF 3 | 0.9595 | 0.8858 | -0.0737 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | WTCLF 3 | 0.9595 | 0.8858 | -0.0737 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | WTCLF 3 | 0.9595 | 0.8858 | -0.0737 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | WTCLF 3 | 0.9595 | 0.8858 | -0.0737 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | WTCLF 3 | 0.9595 | 0.8858 | -0.0737 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | WTCLF 3 | 0.9595 | 0.8858 | -0.0737 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | WTCLF 3 | 0.9595 | 0.8858 | -0.0737 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | WTCLF 3 | 0.9595 | 0.8858 | -0.0737 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | WTCLF 3 | 0.9595 | 0.8858 | -0.0737 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | WTCLF 3 | 0.9595 | 0.8858 | -0.0737 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | WTCLF 3 | 0.9595 | 0.8858 | -0.0737 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | WTCLF 3 | 0.9595 | 0.8858 | -0.0737 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | WTCLF 3 | 0.9595 | 0.8858 | -0.0737 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | WTCLF 3 | 0.9595 | 0.8858 | -0.0737 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | NSI | 0.9671 | 0.886 | -0.0811 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | NSI | 0.9671 | 0.886 | -0.0811 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | NSI | 0.9671 | 0.886 | -0.0811 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | NSI | 0.9671 | 0.886 | -0.0811 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | NSI | 0.9671 | 0.886 | -0.0811 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | NSI | 0.9671 | 0.886 | -0.0811 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | NSI | 0.9671 | 0.886 | -0.0811 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | NSI | 0.9671 | 0.886 | -0.0811 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | NSI | 0.9671 | 0.886 | -0.0811 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | NSI | 0.9671 | 0.886 | -0.0811 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | NSI | 0.9671 | 0.886 | -0.0811 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | NSI | 0.9671 | 0.886 | -0.0811 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | NSI | 0.9671 | 0.886 | -0.0811 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | NSI | 0.9671 | 0.886 | -0.0811 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | NSI | 0.9671 | 0.886 | -0.0811 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | NSI | 0.9671 | 0.886 | -0.0811 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | NSI | 0.9671 | 0.886 | -0.0811 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | NSI | 0.9671 | 0.886 | -0.0811 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | NSI | 0.9671 | 0.886 | -0.0811 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | NSI | 0.9671 | 0.886 | -0.0811 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | NSI | 0.9671 | 0.886 | -0.0811 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | NSI | 0.9671 | 0.886 | -0.0811 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | NSI | 0.9671 | 0.886 | -0.0811 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | NSI | 0.9671 | 0.886 | -0.0811 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | NSI | 0.9671 | 0.886 | -0.0811 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | NSI | 0.9671 | 0.886 | -0.0811 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | NSI | 0.9671 | 0.886 | -0.0811 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | WTCLF 3 | 0.9757 | 0.8864 | -0.0893 |  | 0.9 | 1.05 | 0.05115 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | WTCLF 3 | 0.9757 | 0.8864 | -0.0893 |  | 0.9 | 1.05 | 0.04926 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | WTCLF 3 | 0.9757 | 0.8864 | -0.0893 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | WTCLF 3 | 0.9757 | 0.8864 | -0.0893 |  | 0.9 | 1.05 | 0.04287 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | WTCLF 3 | 0.9757 | 0.8864 | -0.0893 |  | 0.9 | 1.05 | 0.06285 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | WTCLF 3 | 0.9757 | 0.8864 | -0.0893 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | WTCLF 3 | 0.9757 | 0.8864 | -0.0893 |  | 0.9 | 1.05 | 0.05063 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | WTCLF 3 | 0.9757 | 0.8864 | -0.0893 |  | 0.9 | 1.05 | 0.05311 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | WTCLF 3 | 0.9757 | 0.8864 | -0.0893 |  | 0.9 | 1.05 | 0.04461 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | WTCLF 3 | 0.9757 | 0.8864 | -0.0893 |  | 0.9 | 1.05 | 0.0481 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | WTCLF 3 | 0.9757 | 0.8864 | -0.0893 |  | 0.9 | 1.05 | 0.0584 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | WTCLF 3 | 0.9757 | 0.8864 | -0.0893 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | WTCLF 3 | 0.9757 | 0.8864 | -0.0893 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | WTCLF 3 | 0.9757 | 0.8864 | -0.0893 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | WTCLF 3 | 0.9757 | 0.8864 | -0.0893 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | WTCLF 3 | 0.9757 | 0.8864 | -0.0893 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | WTCLF 3 | 0.9757 | 0.8864 | -0.0893 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | WTCLF 3 | 0.9757 | 0.8864 | -0.0893 |  | 0.9 | 1.05 | 0.05126 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | WTCLF 3 | 0.9757 | 0.8864 | -0.0893 |  | 0.9 | 1.05 | 0.0351 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | WTCLF 3 | 0.9757 | 0.8864 | -0.0893 |  | 0.9 | 1.05 | 0.04774 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | WTCLF 3 | 0.9757 | 0.8864 | -0.0893 |  | 0.9 | 1.05 | 0.05016 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | WTCLF 3 | 0.9757 | 0.8864 | -0.0893 |  | 0.9 | 1.05 | 0.04857 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | WTCLF 3 | 0.9757 | 0.8864 | -0.0893 |  | 0.9 | 1.05 | 0.05466 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | WTCLF 3 | 0.9757 | 0.8864 | -0.0893 |  | 0.9 | 1.05 | 0.05401 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | WTCLF 3 | 0.9757 | 0.8864 | -0.0893 |  | 0.9 | 1.05 | 0.03802 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | WTCLF 3 | 0.9757 | 0.8864 | -0.0893 |  | 0.9 | 1.05 | 0.04968 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | WTCLF 3 | 0.9757 | 0.8864 | -0.0893 |  | 0.9 | 1.05 | 0.04081 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | TRIBUNE3 | 0.97 | 0.8866 | -0.0834 |  | 0.9 | 1.05 | 0.05101 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | TRIBUNE3 | 0.97 | 0.8866 | -0.0834 |  | 0.9 | 1.05 | 0.04911 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | TRIBUNE3 | 0.97 | 0.8866 | -0.0834 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | TRIBUNE3 | 0.97 | 0.8866 | -0.0834 |  | 0.9 | 1.05 | 0.04272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | TRIBUNE3 | 0.97 | 0.8866 | -0.0834 |  | 0.9 | 1.05 | 0.06272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | TRIBUNE3 | 0.97 | 0.8866 | -0.0834 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | TRIBUNE3 | 0.97 | 0.8866 | -0.0834 |  | 0.9 | 1.05 | 0.05049 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | TRIBUNE3 | 0.97 | 0.8866 | -0.0834 |  | 0.9 | 1.05 | 0.05297 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | TRIBUNE3 | 0.97 | 0.8866 | -0.0834 |  | 0.9 | 1.05 | 0.04447 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | TRIBUNE3 | 0.97 | 0.8866 | -0.0834 |  | 0.9 | 1.05 | 0.04795 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | TRIBUNE3 | 0.97 | 0.8866 | -0.0834 |  | 0.9 | 1.05 | 0.05827 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | TRIBUNE3 | 0.97 | 0.8866 | -0.0834 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | TRIBUNE3 | 0.97 | 0.8866 | -0.0834 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | TRIBUNE3 | 0.97 | 0.8866 | -0.0834 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | TRIBUNE3 | 0.97 | 0.8866 | -0.0834 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | TRIBUNE3 | 0.97 | 0.8866 | -0.0834 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | TRIBUNE3 | 0.97 | 0.8866 | -0.0834 |  | 0.9 | 1.05 | 0.04781 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | TRIBUNE3 | 0.97 | 0.8866 | -0.0834 |  | 0.9 | 1.05 | 0.05112 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | TRIBUNE3 | 0.97 | 0.8866 | -0.0834 |  | 0.9 | 1.05 | 0.03494 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | TRIBUNE3 | 0.97 | 0.8866 | -0.0834 |  | 0.9 | 1.05 | 0.04759 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | TRIBUNE3 | 0.97 | 0.8866 | -0.0834 |  | 0.9 | 1.05 | 0.05002 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | TRIBUNE3 | 0.97 | 0.8866 | -0.0834 |  | 0.9 | 1.05 | 0.04842 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | TRIBUNE3 | 0.97 | 0.8866 | -0.0834 |  | 0.9 | 1.05 | 0.05452 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | TRIBUNE3 | 0.97 | 0.8866 | -0.0834 |  | 0.9 | 1.05 | 0.05387 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | TRIBUNE3 | 0.97 | 0.8866 | -0.0834 |  | 0.9 | 1.05 | 0.03786 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | TRIBUNE3 | 0.97 | 0.8866 | -0.0834 |  | 0.9 | 1.05 | 0.04954 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | TRIBUNE3 | 0.97 | 0.8866 | -0.0834 |  | 0.9 | 1.05 | 0.04065 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | TRIBUNE3 | 0.981 | 0.8867 | -0.0943 |  | 0.9 | 1.05 | 0.05115 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | TRIBUNE3 | 0.981 | 0.8867 | -0.0943 |  | 0.9 | 1.05 | 0.04926 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | TRIBUNE3 | 0.981 | 0.8867 | -0.0943 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | TRIBUNE3 | 0.981 | 0.8867 | -0.0943 |  | 0.9 | 1.05 | 0.04287 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | TRIBUNE3 | 0.981 | 0.8867 | -0.0943 |  | 0.9 | 1.05 | 0.06285 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | TRIBUNE3 | 0.981 | 0.8867 | -0.0943 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | TRIBUNE3 | 0.981 | 0.8867 | -0.0943 |  | 0.9 | 1.05 | 0.05063 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | TRIBUNE3 | 0.981 | 0.8867 | -0.0943 |  | 0.9 | 1.05 | 0.05311 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | TRIBUNE3 | 0.981 | 0.8867 | -0.0943 |  | 0.9 | 1.05 | 0.04461 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | TRIBUNE3 | 0.981 | 0.8867 | -0.0943 |  | 0.9 | 1.05 | 0.0481 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | TRIBUNE3 | 0.981 | 0.8867 | -0.0943 |  | 0.9 | 1.05 | 0.0584 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | TRIBUNE3 | 0.981 | 0.8867 | -0.0943 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | TRIBUNE3 | 0.981 | 0.8867 | -0.0943 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | TRIBUNE3 | 0.981 | 0.8867 | -0.0943 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | TRIBUNE3 | 0.981 | 0.8867 | -0.0943 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | TRIBUNE3 | 0.981 | 0.8867 | -0.0943 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | TRIBUNE3 | 0.981 | 0.8867 | -0.0943 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | TRIBUNE3 | 0.981 | 0.8867 | -0.0943 |  | 0.9 | 1.05 | 0.05126 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | TRIBUNE3 | 0.981 | 0.8867 | -0.0943 |  | 0.9 | 1.05 | 0.0351 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | TRIBUNE3 | 0.981 | 0.8867 | -0.0943 |  | 0.9 | 1.05 | 0.04774 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | TRIBUNE3 | 0.981 | 0.8867 | -0.0943 |  | 0.9 | 1.05 | 0.05016 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | TRIBUNE3 | 0.981 | 0.8867 | -0.0943 |  | 0.9 | 1.05 | 0.04857 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | TRIBUNE3 | 0.981 | 0.8867 | -0.0943 |  | 0.9 | 1.05 | 0.05466 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | TRIBUNE3 | 0.981 | 0.8867 | -0.0943 |  | 0.9 | 1.05 | 0.05401 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | TRIBUNE3 | 0.981 | 0.8867 | -0.0943 |  | 0.9 | 1.05 | 0.03802 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | TRIBUNE3 | 0.981 | 0.8867 | -0.0943 |  | 0.9 | 1.05 | 0.04968 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | TRIBUNE3 | 0.981 | 0.8867 | -0.0943 |  | 0.9 | 1.05 | 0.04081 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | WTCLFTP3 | 0.9605 | 0.8869 | -0.0736 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | NSI TAP3 | 0.9679 | 0.8869 | -0.081 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | WTCLFTP3 | 0.9605 | 0.8869 | -0.0736 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | NSI TAP3 | 0.9679 | 0.8869 | -0.081 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | WTCLFTP3 | 0.9605 | 0.8869 | -0.0736 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | NSI TAP3 | 0.9679 | 0.8869 | -0.081 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | WTCLFTP3 | 0.9605 | 0.8869 | -0.0736 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | NSI TAP3 | 0.9679 | 0.8869 | -0.081 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | WTCLFTP3 | 0.9605 | 0.8869 | -0.0736 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | NSI TAP3 | 0.9679 | 0.8869 | -0.081 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | WTCLFTP3 | 0.9605 | 0.8869 | -0.0736 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | NSI TAP3 | 0.9679 | 0.8869 | -0.081 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | WTCLFTP3 | 0.9605 | 0.8869 | -0.0736 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | NSI TAP3 | 0.9679 | 0.8869 | -0.081 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | WTCLFTP3 | 0.9605 | 0.8869 | -0.0736 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | NSI TAP3 | 0.9679 | 0.8869 | -0.081 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | WTCLFTP3 | 0.9605 | 0.8869 | -0.0736 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | NSI TAP3 | 0.9679 | 0.8869 | -0.081 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | WTCLFTP3 | 0.9605 | 0.8869 | -0.0736 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | NSI TAP3 | 0.9679 | 0.8869 | -0.081 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | WTCLFTP3 | 0.9605 | 0.8869 | -0.0736 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | NSI TAP3 | 0.9679 | 0.8869 | -0.081 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | WTCLFTP3 | 0.9605 | 0.8869 | -0.0736 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | NSI TAP3 | 0.9679 | 0.8869 | -0.081 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | WTCLFTP3 | 0.9605 | 0.8869 | -0.0736 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | NSI TAP3 | 0.9679 | 0.8869 | -0.081 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | WTCLFTP3 | 0.9605 | 0.8869 | -0.0736 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | NSI TAP3 | 0.9679 | 0.8869 | -0.081 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | WTCLFTP3 | 0.9605 | 0.8869 | -0.0736 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | NSI TAP3 | 0.9679 | 0.8869 | -0.081 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | WTCLFTP3 | 0.9605 | 0.8869 | -0.0736 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | NSI TAP3 | 0.9679 | 0.8869 | -0.081 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | WTCLFTP3 | 0.9605 | 0.8869 | -0.0736 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | NSI TAP3 | 0.9679 | 0.8869 | -0.081 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | WTCLFTP3 | 0.9605 | 0.8869 | -0.0736 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | NSI TAP3 | 0.9679 | 0.8869 | -0.081 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | WTCLFTP3 | 0.9605 | 0.8869 | -0.0736 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | NSI TAP3 | 0.9679 | 0.8869 | -0.081 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | WTCLFTP3 | 0.9605 | 0.8869 | -0.0736 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | NSI TAP3 | 0.9679 | 0.8869 | -0.081 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | WTCLFTP3 | 0.9605 | 0.8869 | -0.0736 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | NSI TAP3 | 0.9679 | 0.8869 | -0.081 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | WTCLFTP3 | 0.9605 | 0.8869 | -0.0736 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | NSI TAP3 | 0.9679 | 0.8869 | -0.081 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | WTCLFTP3 | 0.9605 | 0.8869 | -0.0736 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | NSI TAP3 | 0.9679 | 0.8869 | -0.081 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | WTCLFTP3 | 0.9605 | 0.8869 | -0.0736 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | NSI TAP3 | 0.9679 | 0.8869 | -0.081 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | WTCLFTP3 | 0.9605 | 0.8869 | -0.0736 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | NSI TAP3 | 0.9679 | 0.8869 | -0.081 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | WTCLFTP3 | 0.9605 | 0.8869 | -0.0736 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | NSI TAP3 | 0.9679 | 0.8869 | -0.081 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | WTCLFTP3 | 0.9605 | 0.8869 | -0.0736 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | NSI TAP3 | 0.9679 | 0.8869 | -0.081 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | TRIB SW3 | 0.97 | 0.8871 | -0.0829 |  | 0.9 | 1.05 | 0.05101 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | TRIB SW3 | 0.97 | 0.8871 | -0.0829 |  | 0.9 | 1.05 | 0.04911 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | TRIB SW3 | 0.97 | 0.8871 | -0.0829 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | TRIB SW3 | 0.97 | 0.8871 | -0.0829 |  | 0.9 | 1.05 | 0.04272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | TRIB SW3 | 0.97 | 0.8871 | -0.0829 |  | 0.9 | 1.05 | 0.06272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | TRIB SW3 | 0.97 | 0.8871 | -0.0829 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | TRIB SW3 | 0.97 | 0.8871 | -0.0829 |  | 0.9 | 1.05 | 0.05049 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | TRIB SW3 | 0.97 | 0.8871 | -0.0829 |  | 0.9 | 1.05 | 0.05297 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | TRIB SW3 | 0.97 | 0.8871 | -0.0829 |  | 0.9 | 1.05 | 0.04447 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | TRIB SW3 | 0.97 | 0.8871 | -0.0829 |  | 0.9 | 1.05 | 0.04795 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | TRIB SW3 | 0.97 | 0.8871 | -0.0829 |  | 0.9 | 1.05 | 0.05827 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | TRIB SW3 | 0.97 | 0.8871 | -0.0829 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | TRIB SW3 | 0.97 | 0.8871 | -0.0829 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | TRIB SW3 | 0.97 | 0.8871 | -0.0829 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | TRIB SW3 | 0.97 | 0.8871 | -0.0829 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | TRIB SW3 | 0.97 | 0.8871 | -0.0829 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | TRIB SW3 | 0.97 | 0.8871 | -0.0829 |  | 0.9 | 1.05 | 0.04781 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | TRIB SW3 | 0.97 | 0.8871 | -0.0829 |  | 0.9 | 1.05 | 0.05112 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | TRIB SW3 | 0.97 | 0.8871 | -0.0829 |  | 0.9 | 1.05 | 0.03494 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | TRIB SW3 | 0.97 | 0.8871 | -0.0829 |  | 0.9 | 1.05 | 0.04759 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | TRIB SW3 | 0.97 | 0.8871 | -0.0829 |  | 0.9 | 1.05 | 0.05002 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | TRIB SW3 | 0.97 | 0.8871 | -0.0829 |  | 0.9 | 1.05 | 0.04842 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | TRIB SW3 | 0.97 | 0.8871 | -0.0829 |  | 0.9 | 1.05 | 0.05452 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | TRIB SW3 | 0.97 | 0.8871 | -0.0829 |  | 0.9 | 1.05 | 0.05387 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | TRIB SW3 | 0.97 | 0.8871 | -0.0829 |  | 0.9 | 1.05 | 0.03786 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | TRIB SW3 | 0.97 | 0.8871 | -0.0829 |  | 0.9 | 1.05 | 0.04954 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | TRIB SW3 | 0.97 | 0.8871 | -0.0829 |  | 0.9 | 1.05 | 0.04065 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | PILE 3 | 0.9644 | 0.8873 | -0.0771 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | TRIB SW3 | 0.9812 | 0.8873 | -0.0939 |  | 0.9 | 1.05 | 0.05115 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | GODLNDT3 | 0.998 | 0.8873 | -0.1107 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | GODLNDT3 | 1.0016 | 0.8873 | -0.1143 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | PILE 3 | 0.9644 | 0.8873 | -0.0771 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | TRIB SW3 | 0.9812 | 0.8873 | -0.0939 |  | 0.9 | 1.05 | 0.04926 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | GODLNDT3 | 0.998 | 0.8873 | -0.1107 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | GODLNDT3 | 1.0016 | 0.8873 | -0.1143 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | PILE 3 | 0.9644 | 0.8873 | -0.0771 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | TRIB SW3 | 0.9812 | 0.8873 | -0.0939 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | GODLNDT3 | 0.998 | 0.8873 | -0.1107 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | GODLNDT3 | 1.0016 | 0.8873 | -0.1143 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | PILE 3 | 0.9644 | 0.8873 | -0.0771 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | TRIB SW3 | 0.9812 | 0.8873 | -0.0939 |  | 0.9 | 1.05 | 0.04287 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | GODLNDT3 | 0.998 | 0.8873 | -0.1107 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | GODLNDT3 | 1.0016 | 0.8873 | -0.1143 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | PILE 3 | 0.9644 | 0.8873 | -0.0771 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | TRIB SW3 | 0.9812 | 0.8873 | -0.0939 |  | 0.9 | 1.05 | 0.06285 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | GODLNDT3 | 0.998 | 0.8873 | -0.1107 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | GODLNDT3 | 1.0016 | 0.8873 | -0.1143 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | PILE 3 | 0.9644 | 0.8873 | -0.0771 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | TRIB SW3 | 0.9812 | 0.8873 | -0.0939 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | GODLNDT3 | 0.998 | 0.8873 | -0.1107 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | GODLNDT3 | 1.0016 | 0.8873 | -0.1143 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | PILE 3 | 0.9644 | 0.8873 | -0.0771 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | TRIB SW3 | 0.9812 | 0.8873 | -0.0939 |  | 0.9 | 1.05 | 0.05063 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | GODLNDT3 | 0.998 | 0.8873 | -0.1107 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | GODLNDT3 | 1.0016 | 0.8873 | -0.1143 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | PILE 3 | 0.9644 | 0.8873 | -0.0771 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | TRIB SW3 | 0.9812 | 0.8873 | -0.0939 |  | 0.9 | 1.05 | 0.05311 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | GODLNDT3 | 0.998 | 0.8873 | -0.1107 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | GODLNDT3 | 1.0016 | 0.8873 | -0.1143 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | PILE 3 | 0.9644 | 0.8873 | -0.0771 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | TRIB SW3 | 0.9812 | 0.8873 | -0.0939 |  | 0.9 | 1.05 | 0.04461 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | GODLNDT3 | 0.998 | 0.8873 | -0.1107 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | GODLNDT3 | 1.0016 | 0.8873 | -0.1143 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | PILE 3 | 0.9644 | 0.8873 | -0.0771 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | TRIB SW3 | 0.9812 | 0.8873 | -0.0939 |  | 0.9 | 1.05 | 0.0481 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | GODLNDT3 | 0.998 | 0.8873 | -0.1107 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | GODLNDT3 | 1.0016 | 0.8873 | -0.1143 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | PILE 3 | 0.9644 | 0.8873 | -0.0771 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | TRIB SW3 | 0.9812 | 0.8873 | -0.0939 |  | 0.9 | 1.05 | 0.0584 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | GODLNDT3 | 0.998 | 0.8873 | -0.1107 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | GODLNDT3 | 1.0016 | 0.8873 | -0.1143 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | PILE 3 | 0.9644 | 0.8873 | -0.0771 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | TRIB SW3 | 0.9812 | 0.8873 | -0.0939 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | GODLNDT3 | 0.998 | 0.8873 | -0.1107 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | GODLNDT3 | 1.0016 | 0.8873 | -0.1143 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | PILE 3 | 0.9644 | 0.8873 | -0.0771 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | TRIB SW3 | 0.9812 | 0.8873 | -0.0939 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | GODLNDT3 | 0.998 | 0.8873 | -0.1107 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | GODLNDT3 | 1.0016 | 0.8873 | -0.1143 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | PILE 3 | 0.9644 | 0.8873 | -0.0771 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | TRIB SW3 | 0.9812 | 0.8873 | -0.0939 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | GODLNDT3 | 0.998 | 0.8873 | -0.1107 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | GODLNDT3 | 1.0016 | 0.8873 | -0.1143 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | PILE 3 | 0.9644 | 0.8873 | -0.0771 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | TRIB SW3 | 0.9812 | 0.8873 | -0.0939 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | GODLNDT3 | 0.998 | 0.8873 | -0.1107 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | GODLNDT3 | 1.0016 | 0.8873 | -0.1143 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | PILE 3 | 0.9644 | 0.8873 | -0.0771 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | TRIB SW3 | 0.9812 | 0.8873 | -0.0939 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | GODLNDT3 | 0.998 | 0.8873 | -0.1107 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | GODLNDT3 | 1.0016 | 0.8873 | -0.1143 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | PILE 3 | 0.9644 | 0.8873 | -0.0771 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | TRIB SW3 | 0.9812 | 0.8873 | -0.0939 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | GODLNDT3 | 0.998 | 0.8873 | -0.1107 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | GODLNDT3 | 1.0016 | 0.8873 | -0.1143 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | PILE 3 | 0.9644 | 0.8873 | -0.0771 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | TRIB SW3 | 0.9812 | 0.8873 | -0.0939 |  | 0.9 | 1.05 | 0.05126 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | GODLNDT3 | 0.998 | 0.8873 | -0.1107 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | GODLNDT3 | 1.0016 | 0.8873 | -0.1143 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | PILE 3 | 0.9644 | 0.8873 | -0.0771 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | TRIB SW3 | 0.9812 | 0.8873 | -0.0939 |  | 0.9 | 1.05 | 0.0351 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | GODLNDT3 | 0.998 | 0.8873 | -0.1107 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | GODLNDT3 | 1.0016 | 0.8873 | -0.1143 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | PILE 3 | 0.9644 | 0.8873 | -0.0771 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | TRIB SW3 | 0.9812 | 0.8873 | -0.0939 |  | 0.9 | 1.05 | 0.04774 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | GODLNDT3 | 0.998 | 0.8873 | -0.1107 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | GODLNDT3 | 1.0016 | 0.8873 | -0.1143 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | PILE 3 | 0.9644 | 0.8873 | -0.0771 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | TRIB SW3 | 0.9812 | 0.8873 | -0.0939 |  | 0.9 | 1.05 | 0.05016 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | GODLNDT3 | 0.998 | 0.8873 | -0.1107 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | GODLNDT3 | 1.0016 | 0.8873 | -0.1143 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | PILE 3 | 0.9644 | 0.8873 | -0.0771 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | TRIB SW3 | 0.9812 | 0.8873 | -0.0939 |  | 0.9 | 1.05 | 0.04857 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | GODLNDT3 | 0.998 | 0.8873 | -0.1107 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | GODLNDT3 | 1.0016 | 0.8873 | -0.1143 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | PILE 3 | 0.9644 | 0.8873 | -0.0771 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | TRIB SW3 | 0.9812 | 0.8873 | -0.0939 |  | 0.9 | 1.05 | 0.05466 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | GODLNDT3 | 0.998 | 0.8873 | -0.1107 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | GODLNDT3 | 1.0016 | 0.8873 | -0.1143 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | PILE 3 | 0.9644 | 0.8873 | -0.0771 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | TRIB SW3 | 0.9812 | 0.8873 | -0.0939 |  | 0.9 | 1.05 | 0.05401 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | GODLNDT3 | 0.998 | 0.8873 | -0.1107 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | GODLNDT3 | 1.0016 | 0.8873 | -0.1143 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | PILE 3 | 0.9644 | 0.8873 | -0.0771 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | TRIB SW3 | 0.9812 | 0.8873 | -0.0939 |  | 0.9 | 1.05 | 0.03802 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | GODLNDT3 | 0.998 | 0.8873 | -0.1107 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | GODLNDT3 | 1.0016 | 0.8873 | -0.1143 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | PILE 3 | 0.9644 | 0.8873 | -0.0771 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | TRIB SW3 | 0.9812 | 0.8873 | -0.0939 |  | 0.9 | 1.05 | 0.04968 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | GODLNDT3 | 0.998 | 0.8873 | -0.1107 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | GODLNDT3 | 1.0016 | 0.8873 | -0.1143 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | PILE 3 | 0.9644 | 0.8873 | -0.0771 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | TRIB SW3 | 0.9812 | 0.8873 | -0.0939 |  | 0.9 | 1.05 | 0.04081 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | GODLNDT3 | 0.998 | 0.8873 | -0.1107 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | GODLNDT3 | 1.0016 | 0.8873 | -0.1143 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | GOVE 3 | 0.9781 | 0.8875 | -0.0906 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | GOVE 3 | 0.9827 | 0.8875 | -0.0952 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | WTCLFTP3 | 0.9767 | 0.8875 | -0.0892 |  | 0.9 | 1.05 | 0.05115 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | GOVE 3 | 0.9781 | 0.8875 | -0.0906 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | GOVE 3 | 0.9827 | 0.8875 | -0.0952 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | WTCLFTP3 | 0.9767 | 0.8875 | -0.0892 |  | 0.9 | 1.05 | 0.04926 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | GOVE 3 | 0.9781 | 0.8875 | -0.0906 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | GOVE 3 | 0.9827 | 0.8875 | -0.0952 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | WTCLFTP3 | 0.9767 | 0.8875 | -0.0892 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | GOVE 3 | 0.9781 | 0.8875 | -0.0906 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | GOVE 3 | 0.9827 | 0.8875 | -0.0952 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | WTCLFTP3 | 0.9767 | 0.8875 | -0.0892 |  | 0.9 | 1.05 | 0.04287 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | GOVE 3 | 0.9781 | 0.8875 | -0.0906 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | GOVE 3 | 0.9827 | 0.8875 | -0.0952 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | WTCLFTP3 | 0.9767 | 0.8875 | -0.0892 |  | 0.9 | 1.05 | 0.06285 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | GOVE 3 | 0.9781 | 0.8875 | -0.0906 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | GOVE 3 | 0.9827 | 0.8875 | -0.0952 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | WTCLFTP3 | 0.9767 | 0.8875 | -0.0892 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | GOVE 3 | 0.9781 | 0.8875 | -0.0906 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | GOVE 3 | 0.9827 | 0.8875 | -0.0952 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | WTCLFTP3 | 0.9767 | 0.8875 | -0.0892 |  | 0.9 | 1.05 | 0.05063 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | GOVE 3 | 0.9781 | 0.8875 | -0.0906 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | GOVE 3 | 0.9827 | 0.8875 | -0.0952 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | WTCLFTP3 | 0.9767 | 0.8875 | -0.0892 |  | 0.9 | 1.05 | 0.05311 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | GOVE 3 | 0.9781 | 0.8875 | -0.0906 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | GOVE 3 | 0.9827 | 0.8875 | -0.0952 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | WTCLFTP3 | 0.9767 | 0.8875 | -0.0892 |  | 0.9 | 1.05 | 0.04461 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | GOVE 3 | 0.9781 | 0.8875 | -0.0906 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | GOVE 3 | 0.9827 | 0.8875 | -0.0952 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | WTCLFTP3 | 0.9767 | 0.8875 | -0.0892 |  | 0.9 | 1.05 | 0.0481 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | GOVE 3 | 0.9781 | 0.8875 | -0.0906 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | GOVE 3 | 0.9827 | 0.8875 | -0.0952 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | WTCLFTP3 | 0.9767 | 0.8875 | -0.0892 |  | 0.9 | 1.05 | 0.0584 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | GOVE 3 | 0.9781 | 0.8875 | -0.0906 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | GOVE 3 | 0.9827 | 0.8875 | -0.0952 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | WTCLFTP3 | 0.9767 | 0.8875 | -0.0892 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | GOVE 3 | 0.9781 | 0.8875 | -0.0906 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | GOVE 3 | 0.9827 | 0.8875 | -0.0952 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | WTCLFTP3 | 0.9767 | 0.8875 | -0.0892 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | GOVE 3 | 0.9781 | 0.8875 | -0.0906 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | GOVE 3 | 0.9827 | 0.8875 | -0.0952 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | WTCLFTP3 | 0.9767 | 0.8875 | -0.0892 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | GOVE 3 | 0.9781 | 0.8875 | -0.0906 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | GOVE 3 | 0.9827 | 0.8875 | -0.0952 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | WTCLFTP3 | 0.9767 | 0.8875 | -0.0892 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | GOVE 3 | 0.9781 | 0.8875 | -0.0906 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | GOVE 3 | 0.9827 | 0.8875 | -0.0952 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | WTCLFTP3 | 0.9767 | 0.8875 | -0.0892 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | GOVE 3 | 0.9781 | 0.8875 | -0.0906 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | GOVE 3 | 0.9827 | 0.8875 | -0.0952 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | WTCLFTP3 | 0.9767 | 0.8875 | -0.0892 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | GOVE 3 | 0.9781 | 0.8875 | -0.0906 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | GOVE 3 | 0.9827 | 0.8875 | -0.0952 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | WTCLFTP3 | 0.9767 | 0.8875 | -0.0892 |  | 0.9 | 1.05 | 0.05126 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | GOVE 3 | 0.9781 | 0.8875 | -0.0906 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | GOVE 3 | 0.9827 | 0.8875 | -0.0952 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | WTCLFTP3 | 0.9767 | 0.8875 | -0.0892 |  | 0.9 | 1.05 | 0.0351 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | GOVE 3 | 0.9781 | 0.8875 | -0.0906 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | GOVE 3 | 0.9827 | 0.8875 | -0.0952 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | WTCLFTP3 | 0.9767 | 0.8875 | -0.0892 |  | 0.9 | 1.05 | 0.04774 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | GOVE 3 | 0.9781 | 0.8875 | -0.0906 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | GOVE 3 | 0.9827 | 0.8875 | -0.0952 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | WTCLFTP3 | 0.9767 | 0.8875 | -0.0892 |  | 0.9 | 1.05 | 0.05016 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | GOVE 3 | 0.9781 | 0.8875 | -0.0906 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | GOVE 3 | 0.9827 | 0.8875 | -0.0952 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | WTCLFTP3 | 0.9767 | 0.8875 | -0.0892 |  | 0.9 | 1.05 | 0.04857 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | GOVE 3 | 0.9781 | 0.8875 | -0.0906 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | GOVE 3 | 0.9827 | 0.8875 | -0.0952 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | WTCLFTP3 | 0.9767 | 0.8875 | -0.0892 |  | 0.9 | 1.05 | 0.05466 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | GOVE 3 | 0.9781 | 0.8875 | -0.0906 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | GOVE 3 | 0.9827 | 0.8875 | -0.0952 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | WTCLFTP3 | 0.9767 | 0.8875 | -0.0892 |  | 0.9 | 1.05 | 0.05401 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | GOVE 3 | 0.9781 | 0.8875 | -0.0906 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | GOVE 3 | 0.9827 | 0.8875 | -0.0952 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | WTCLFTP3 | 0.9767 | 0.8875 | -0.0892 |  | 0.9 | 1.05 | 0.03802 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | GOVE 3 | 0.9781 | 0.8875 | -0.0906 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | GOVE 3 | 0.9827 | 0.8875 | -0.0952 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | WTCLFTP3 | 0.9767 | 0.8875 | -0.0892 |  | 0.9 | 1.05 | 0.04968 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | GOVE 3 | 0.9781 | 0.8875 | -0.0906 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | GOVE 3 | 0.9827 | 0.8875 | -0.0952 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | WTCLFTP3 | 0.9767 | 0.8875 | -0.0892 |  | 0.9 | 1.05 | 0.04081 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | PALMER3 | 0.9672 | 0.8883 | -0.0789 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | PALMER3 | 0.9672 | 0.8883 | -0.0789 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | PALMER3 | 0.9672 | 0.8883 | -0.0789 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | PALMER3 | 0.9672 | 0.8883 | -0.0789 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | PALMER3 | 0.9672 | 0.8883 | -0.0789 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | PALMER3 | 0.9672 | 0.8883 | -0.0789 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | PALMER3 | 0.9672 | 0.8883 | -0.0789 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | PALMER3 | 0.9672 | 0.8883 | -0.0789 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | PALMER3 | 0.9672 | 0.8883 | -0.0789 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | PALMER3 | 0.9672 | 0.8883 | -0.0789 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | PALMER3 | 0.9672 | 0.8883 | -0.0789 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | PALMER3 | 0.9672 | 0.8883 | -0.0789 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | PALMER3 | 0.9672 | 0.8883 | -0.0789 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | PALMER3 | 0.9672 | 0.8883 | -0.0789 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | PALMER3 | 0.9672 | 0.8883 | -0.0789 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | PALMER3 | 0.9672 | 0.8883 | -0.0789 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | PALMER3 | 0.9672 | 0.8883 | -0.0789 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | PALMER3 | 0.9672 | 0.8883 | -0.0789 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | PALMER3 | 0.9672 | 0.8883 | -0.0789 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | PALMER3 | 0.9672 | 0.8883 | -0.0789 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | PALMER3 | 0.9672 | 0.8883 | -0.0789 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | PALMER3 | 0.9672 | 0.8883 | -0.0789 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | PALMER3 | 0.9672 | 0.8883 | -0.0789 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | PALMER3 | 0.9672 | 0.8883 | -0.0789 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | PALMER3 | 0.9672 | 0.8883 | -0.0789 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | PALMER3 | 0.9672 | 0.8883 | -0.0789 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | PALMER3 | 0.9672 | 0.8883 | -0.0789 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | CNTRLPL3 | 0.9762 | 0.8884 | -0.0878 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | CNTRLPL3 | 0.9762 | 0.8884 | -0.0878 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | CNTRLPL3 | 0.9762 | 0.8884 | -0.0878 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | CNTRLPL3 | 0.9762 | 0.8884 | -0.0878 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | CNTRLPL3 | 0.9762 | 0.8884 | -0.0878 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | CNTRLPL3 | 0.9762 | 0.8884 | -0.0878 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | CNTRLPL3 | 0.9762 | 0.8884 | -0.0878 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | CNTRLPL3 | 0.9762 | 0.8884 | -0.0878 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | CNTRLPL3 | 0.9762 | 0.8884 | -0.0878 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | CNTRLPL3 | 0.9762 | 0.8884 | -0.0878 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | CNTRLPL3 | 0.9762 | 0.8884 | -0.0878 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | CNTRLPL3 | 0.9762 | 0.8884 | -0.0878 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | CNTRLPL3 | 0.9762 | 0.8884 | -0.0878 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | CNTRLPL3 | 0.9762 | 0.8884 | -0.0878 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | CNTRLPL3 | 0.9762 | 0.8884 | -0.0878 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | CNTRLPL3 | 0.9762 | 0.8884 | -0.0878 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | CNTRLPL3 | 0.9762 | 0.8884 | -0.0878 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | CNTRLPL3 | 0.9762 | 0.8884 | -0.0878 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | CNTRLPL3 | 0.9762 | 0.8884 | -0.0878 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | CNTRLPL3 | 0.9762 | 0.8884 | -0.0878 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | CNTRLPL3 | 0.9762 | 0.8884 | -0.0878 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | CNTRLPL3 | 0.9762 | 0.8884 | -0.0878 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | CNTRLPL3 | 0.9762 | 0.8884 | -0.0878 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | CNTRLPL3 | 0.9762 | 0.8884 | -0.0878 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | CNTRLPL3 | 0.9762 | 0.8884 | -0.0878 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | CNTRLPL3 | 0.9762 | 0.8884 | -0.0878 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | CNTRLPL3 | 0.9762 | 0.8884 | -0.0878 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | GOODCTY3 | 0.9943 | 0.8889 | -0.1054 |  | 0.9 | 1.05 | 0.05095 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | GOODCTY3 | 0.9943 | 0.8889 | -0.1054 |  | 0.9 | 1.05 | 0.04905 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | GOODCTY3 | 0.9943 | 0.8889 | -0.1054 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | GOODCTY3 | 0.9943 | 0.8889 | -0.1054 |  | 0.9 | 1.05 | 0.04262 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | GOODCTY3 | 0.9943 | 0.8889 | -0.1054 |  | 0.9 | 1.05 | 0.0627 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | GOODCTY3 | 0.9943 | 0.8889 | -0.1054 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | GOODCTY3 | 0.9943 | 0.8889 | -0.1054 |  | 0.9 | 1.05 | 0.05043 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | GOODCTY3 | 0.9943 | 0.8889 | -0.1054 |  | 0.9 | 1.05 | 0.05292 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | GOODCTY3 | 0.9943 | 0.8889 | -0.1054 |  | 0.9 | 1.05 | 0.0444 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | GOODCTY3 | 0.9943 | 0.8889 | -0.1054 |  | 0.9 | 1.05 | 0.04788 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | GOODCTY3 | 0.9943 | 0.8889 | -0.1054 |  | 0.9 | 1.05 | 0.05824 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | GOODCTY3 | 0.9943 | 0.8889 | -0.1054 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | GOODCTY3 | 0.9943 | 0.8889 | -0.1054 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | GOODCTY3 | 0.9943 | 0.8889 | -0.1054 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | GOODCTY3 | 0.9943 | 0.8889 | -0.1054 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | GOODCTY3 | 0.9943 | 0.8889 | -0.1054 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | GOODCTY3 | 0.9943 | 0.8889 | -0.1054 |  | 0.9 | 1.05 | 0.04773 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | GOODCTY3 | 0.9943 | 0.8889 | -0.1054 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | GOODCTY3 | 0.9943 | 0.8889 | -0.1054 |  | 0.9 | 1.05 | 0.0348 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | GOODCTY3 | 0.9943 | 0.8889 | -0.1054 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | GOODCTY3 | 0.9943 | 0.8889 | -0.1054 |  | 0.9 | 1.05 | 0.04996 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | GOODCTY3 | 0.9943 | 0.8889 | -0.1054 |  | 0.9 | 1.05 | 0.04835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | GOODCTY3 | 0.9943 | 0.8889 | -0.1054 |  | 0.9 | 1.05 | 0.05448 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | GOODCTY3 | 0.9943 | 0.8889 | -0.1054 |  | 0.9 | 1.05 | 0.05382 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | GOODCTY3 | 0.9943 | 0.8889 | -0.1054 |  | 0.9 | 1.05 | 0.03774 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | GOODCTY3 | 0.9943 | 0.8889 | -0.1054 |  | 0.9 | 1.05 | 0.04948 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | GOODCTY3 | 0.9943 | 0.8889 | -0.1054 |  | 0.9 | 1.05 | 0.04054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | GOODLND3 | 0.9987 | 0.8893 | -0.1094 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | GOODLND3 | 1.0023 | 0.8893 | -0.113 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | GOODLND3 | 0.9987 | 0.8893 | -0.1094 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | GOODLND3 | 1.0023 | 0.8893 | -0.113 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | GOODLND3 | 0.9987 | 0.8893 | -0.1094 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | GOODLND3 | 1.0023 | 0.8893 | -0.113 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | GOODLND3 | 0.9987 | 0.8893 | -0.1094 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | GOODLND3 | 1.0023 | 0.8893 | -0.113 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | GOODLND3 | 0.9987 | 0.8893 | -0.1094 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | GOODLND3 | 1.0023 | 0.8893 | -0.113 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | GOODLND3 | 0.9987 | 0.8893 | -0.1094 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | GOODLND3 | 1.0023 | 0.8893 | -0.113 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | GOODLND3 | 0.9987 | 0.8893 | -0.1094 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | GOODLND3 | 1.0023 | 0.8893 | -0.113 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | GOODLND3 | 0.9987 | 0.8893 | -0.1094 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | GOODLND3 | 1.0023 | 0.8893 | -0.113 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | GOODLND3 | 0.9987 | 0.8893 | -0.1094 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | GOODLND3 | 1.0023 | 0.8893 | -0.113 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | GOODLND3 | 0.9987 | 0.8893 | -0.1094 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | GOODLND3 | 1.0023 | 0.8893 | -0.113 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | GOODLND3 | 0.9987 | 0.8893 | -0.1094 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | GOODLND3 | 1.0023 | 0.8893 | -0.113 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | GOODLND3 | 0.9987 | 0.8893 | -0.1094 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | GOODLND3 | 1.0023 | 0.8893 | -0.113 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | GOODLND3 | 0.9987 | 0.8893 | -0.1094 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | GOODLND3 | 1.0023 | 0.8893 | -0.113 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | GOODLND3 | 0.9987 | 0.8893 | -0.1094 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | GOODLND3 | 1.0023 | 0.8893 | -0.113 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | GOODLND3 | 0.9987 | 0.8893 | -0.1094 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | GOODLND3 | 1.0023 | 0.8893 | -0.113 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | GOODLND3 | 0.9987 | 0.8893 | -0.1094 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | GOODLND3 | 1.0023 | 0.8893 | -0.113 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | GOODLND3 | 0.9987 | 0.8893 | -0.1094 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | GOODLND3 | 1.0023 | 0.8893 | -0.113 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | GOODLND3 | 0.9987 | 0.8893 | -0.1094 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | GOODLND3 | 1.0023 | 0.8893 | -0.113 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | GOODLND3 | 0.9987 | 0.8893 | -0.1094 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | GOODLND3 | 1.0023 | 0.8893 | -0.113 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | GOODLND3 | 0.9987 | 0.8893 | -0.1094 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | GOODLND3 | 1.0023 | 0.8893 | -0.113 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | GOODLND3 | 0.9987 | 0.8893 | -0.1094 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | GOODLND3 | 1.0023 | 0.8893 | -0.113 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | GOODLND3 | 0.9987 | 0.8893 | -0.1094 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | GOODLND3 | 1.0023 | 0.8893 | -0.113 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | GOODLND3 | 0.9987 | 0.8893 | -0.1094 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | GOODLND3 | 1.0023 | 0.8893 | -0.113 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | GOODLND3 | 0.9987 | 0.8893 | -0.1094 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | GOODLND3 | 1.0023 | 0.8893 | -0.113 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | GOODLND3 | 0.9987 | 0.8893 | -0.1094 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | GOODLND3 | 1.0023 | 0.8893 | -0.113 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | GOODLND3 | 0.9987 | 0.8893 | -0.1094 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | GOODLND3 | 1.0023 | 0.8893 | -0.113 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | GOODLND3 | 0.9987 | 0.8893 | -0.1094 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | GOODLND3 | 1.0023 | 0.8893 | -0.113 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.10414 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.10414 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.0987 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.0987 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.08024 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.08024 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.14298 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.14298 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.10266 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.10266 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.11064 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.11064 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.08095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.08095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.09571 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.09571 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.12796 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.12796 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.09379 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.09379 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.09379 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.09379 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.09507 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.09507 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.10446 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.10446 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.05698 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.05698 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.09445 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.09445 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.10129 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.10129 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.0967 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.0967 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.11534 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.11534 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.11336 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.11336 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.06542 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.06542 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.09991 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.09991 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.0742 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | ROLLA 3 | 1.0028 | 0.8894 | -0.1134 |  | 0.9 | 1.05 | 0.0742 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.10414 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.10414 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.0987 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.0987 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.08024 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.08024 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.14298 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.14298 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.10266 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.10266 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.11064 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.11064 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.08095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.08095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.09571 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.09571 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.12796 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.12796 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.09379 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.09379 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.09379 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.09379 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.09507 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.09507 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.10446 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.10446 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.05698 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.05698 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.09445 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.09445 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.10129 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.10129 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.0967 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.0967 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.11534 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.11534 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.11336 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.11336 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.06542 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.06542 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.09991 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.09991 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.0742 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | HUGOTON3 | 1.0045 | 0.8896 | -0.1149 |  | 0.9 | 1.05 | 0.0742 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.10463 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.10463 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.09917 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.09917 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.09545 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.08062 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.08062 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.1436 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.1436 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.09545 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.10316 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.10316 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.11116 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.11116 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.0814 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.0814 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.09616 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.09616 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.12853 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.12853 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.09545 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.09545 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.09424 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.09424 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.09424 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.09424 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.09545 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.09553 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.09553 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.10494 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.10494 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.0573 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.0573 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.0949 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.0949 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.10178 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.10178 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.09717 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.09717 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.11588 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.11588 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.11389 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.11389 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.06575 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.06575 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.10039 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.10039 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.07455 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | GRANT 3 | 1.0028 | 0.8898 | -0.113 |  | 0.9 | 1.05 | 0.07455 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | SETAB 3 | 0.9723 | 0.8899 | -0.0824 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | SETAB 3 | 0.9723 | 0.8899 | -0.0824 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | SETAB 3 | 0.9723 | 0.8899 | -0.0824 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | SETAB 3 | 0.9723 | 0.8899 | -0.0824 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | SETAB 3 | 0.9723 | 0.8899 | -0.0824 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | SETAB 3 | 0.9723 | 0.8899 | -0.0824 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | SETAB 3 | 0.9723 | 0.8899 | -0.0824 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | SETAB 3 | 0.9723 | 0.8899 | -0.0824 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | SETAB 3 | 0.9723 | 0.8899 | -0.0824 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | SETAB 3 | 0.9723 | 0.8899 | -0.0824 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | SETAB 3 | 0.9723 | 0.8899 | -0.0824 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | SETAB 3 | 0.9723 | 0.8899 | -0.0824 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | SETAB 3 | 0.9723 | 0.8899 | -0.0824 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | SETAB 3 | 0.9723 | 0.8899 | -0.0824 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | SETAB 3 | 0.9723 | 0.8899 | -0.0824 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | SETAB 3 | 0.9723 | 0.8899 | -0.0824 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | SETAB 3 | 0.9723 | 0.8899 | -0.0824 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | SETAB 3 | 0.9723 | 0.8899 | -0.0824 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | SETAB 3 | 0.9723 | 0.8899 | -0.0824 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | SETAB 3 | 0.9723 | 0.8899 | -0.0824 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | SETAB 3 | 0.9723 | 0.8899 | -0.0824 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | SETAB 3 | 0.9723 | 0.8899 | -0.0824 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | SETAB 3 | 0.9723 | 0.8899 | -0.0824 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | SETAB 3 | 0.9723 | 0.8899 | -0.0824 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | SETAB 3 | 0.9723 | 0.8899 | -0.0824 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | SETAB 3 | 0.9723 | 0.8899 | -0.0824 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | SETAB 3 | 0.9723 | 0.8899 | -0.0824 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | GANO 3 | 0.9748 | 0.89 | -0.0848 |  | 0.9 | 1.05 | 0.05115 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | GANO 3 | 0.9748 | 0.89 | -0.0848 |  | 0.9 | 1.05 | 0.04926 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | GANO 3 | 0.9748 | 0.89 | -0.0848 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | GANO 3 | 0.9748 | 0.89 | -0.0848 |  | 0.9 | 1.05 | 0.04287 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | GANO 3 | 0.9748 | 0.89 | -0.0848 |  | 0.9 | 1.05 | 0.06285 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | GANO 3 | 0.9748 | 0.89 | -0.0848 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | GANO 3 | 0.9748 | 0.89 | -0.0848 |  | 0.9 | 1.05 | 0.05063 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | GANO 3 | 0.9748 | 0.89 | -0.0848 |  | 0.9 | 1.05 | 0.05311 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | GANO 3 | 0.9748 | 0.89 | -0.0848 |  | 0.9 | 1.05 | 0.04461 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | GANO 3 | 0.9748 | 0.89 | -0.0848 |  | 0.9 | 1.05 | 0.0481 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | GANO 3 | 0.9748 | 0.89 | -0.0848 |  | 0.9 | 1.05 | 0.0584 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | GANO 3 | 0.9748 | 0.89 | -0.0848 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | GANO 3 | 0.9748 | 0.89 | -0.0848 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | GANO 3 | 0.9748 | 0.89 | -0.0848 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | GANO 3 | 0.9748 | 0.89 | -0.0848 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | GANO 3 | 0.9748 | 0.89 | -0.0848 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | GANO 3 | 0.9748 | 0.89 | -0.0848 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | GANO 3 | 0.9748 | 0.89 | -0.0848 |  | 0.9 | 1.05 | 0.05126 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | GANO 3 | 0.9748 | 0.89 | -0.0848 |  | 0.9 | 1.05 | 0.0351 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | GANO 3 | 0.9748 | 0.89 | -0.0848 |  | 0.9 | 1.05 | 0.04774 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | GANO 3 | 0.9748 | 0.89 | -0.0848 |  | 0.9 | 1.05 | 0.05016 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | GANO 3 | 0.9748 | 0.89 | -0.0848 |  | 0.9 | 1.05 | 0.04857 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | GANO 3 | 0.9748 | 0.89 | -0.0848 |  | 0.9 | 1.05 | 0.05466 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | GANO 3 | 0.9748 | 0.89 | -0.0848 |  | 0.9 | 1.05 | 0.05401 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | GANO 3 | 0.9748 | 0.89 | -0.0848 |  | 0.9 | 1.05 | 0.03802 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | GANO 3 | 0.9748 | 0.89 | -0.0848 |  | 0.9 | 1.05 | 0.04968 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | GANO 3 | 0.9748 | 0.89 | -0.0848 |  | 0.9 | 1.05 | 0.04081 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.10463 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.10463 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.09917 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.09917 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.09545 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.08062 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.08062 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.1436 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.1436 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.09545 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.10316 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.10316 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.11116 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.11116 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.0814 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.0814 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.09616 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.09616 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.12853 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.12853 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.09545 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.09545 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.09424 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.09424 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.09424 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.09424 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.09545 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.09553 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.09553 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.10494 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.10494 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.0573 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.0573 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.0949 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.0949 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.10178 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.10178 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.09717 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.09717 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.11588 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.11588 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.11389 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.11389 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.06575 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.06575 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.10039 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.10039 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.07455 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | GRANTTP3 | 1.0031 | 0.8901 | -0.113 |  | 0.9 | 1.05 | 0.07455 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | TRIB SW3 | 0.9754 | 0.8904 | -0.085 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | TRIB SW3 | 0.9845 | 0.8904 | -0.0941 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | TRIB SW3 | 0.9754 | 0.8904 | -0.085 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | TRIB SW3 | 0.9845 | 0.8904 | -0.0941 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | TRIB SW3 | 0.9754 | 0.8904 | -0.085 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | TRIB SW3 | 0.9845 | 0.8904 | -0.0941 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | TRIB SW3 | 0.9754 | 0.8904 | -0.085 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | TRIB SW3 | 0.9845 | 0.8904 | -0.0941 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | TRIB SW3 | 0.9754 | 0.8904 | -0.085 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | TRIB SW3 | 0.9845 | 0.8904 | -0.0941 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | TRIB SW3 | 0.9754 | 0.8904 | -0.085 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | TRIB SW3 | 0.9845 | 0.8904 | -0.0941 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | TRIB SW3 | 0.9754 | 0.8904 | -0.085 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | TRIB SW3 | 0.9845 | 0.8904 | -0.0941 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | TRIB SW3 | 0.9754 | 0.8904 | -0.085 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | TRIB SW3 | 0.9845 | 0.8904 | -0.0941 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | TRIB SW3 | 0.9754 | 0.8904 | -0.085 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | TRIB SW3 | 0.9845 | 0.8904 | -0.0941 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | TRIB SW3 | 0.9754 | 0.8904 | -0.085 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | TRIB SW3 | 0.9845 | 0.8904 | -0.0941 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | TRIB SW3 | 0.9754 | 0.8904 | -0.085 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | TRIB SW3 | 0.9845 | 0.8904 | -0.0941 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | TRIB SW3 | 0.9754 | 0.8904 | -0.085 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | TRIB SW3 | 0.9845 | 0.8904 | -0.0941 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | TRIB SW3 | 0.9754 | 0.8904 | -0.085 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | TRIB SW3 | 0.9845 | 0.8904 | -0.0941 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | TRIB SW3 | 0.9754 | 0.8904 | -0.085 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | TRIB SW3 | 0.9845 | 0.8904 | -0.0941 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | TRIB SW3 | 0.9754 | 0.8904 | -0.085 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | TRIB SW3 | 0.9845 | 0.8904 | -0.0941 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | TRIB SW3 | 0.9754 | 0.8904 | -0.085 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | TRIB SW3 | 0.9845 | 0.8904 | -0.0941 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | TRIB SW3 | 0.9754 | 0.8904 | -0.085 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | TRIB SW3 | 0.9845 | 0.8904 | -0.0941 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | TRIB SW3 | 0.9754 | 0.8904 | -0.085 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | TRIB SW3 | 0.9845 | 0.8904 | -0.0941 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | TRIB SW3 | 0.9754 | 0.8904 | -0.085 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | TRIB SW3 | 0.9845 | 0.8904 | -0.0941 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | TRIB SW3 | 0.9754 | 0.8904 | -0.085 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | TRIB SW3 | 0.9845 | 0.8904 | -0.0941 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | TRIB SW3 | 0.9754 | 0.8904 | -0.085 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | TRIB SW3 | 0.9845 | 0.8904 | -0.0941 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | TRIB SW3 | 0.9754 | 0.8904 | -0.085 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | TRIB SW3 | 0.9845 | 0.8904 | -0.0941 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | TRIB SW3 | 0.9754 | 0.8904 | -0.085 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | TRIB SW3 | 0.9845 | 0.8904 | -0.0941 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | TRIB SW3 | 0.9754 | 0.8904 | -0.085 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | TRIB SW3 | 0.9845 | 0.8904 | -0.0941 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | TRIB SW3 | 0.9754 | 0.8904 | -0.085 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | TRIB SW3 | 0.9845 | 0.8904 | -0.0941 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | TRIB SW3 | 0.9754 | 0.8904 | -0.085 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | TRIB SW3 | 0.9845 | 0.8904 | -0.0941 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | TRIB SW3 | 0.9754 | 0.8904 | -0.085 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | TRIB SW3 | 0.9845 | 0.8904 | -0.0941 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | GANO 3 | 0.9659 | 0.8906 | -0.0753 |  | 0.9 | 1.05 | 0.05101 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | GANO 3 | 0.9659 | 0.8906 | -0.0753 |  | 0.9 | 1.05 | 0.04911 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | GANO 3 | 0.9659 | 0.8906 | -0.0753 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | GANO 3 | 0.9659 | 0.8906 | -0.0753 |  | 0.9 | 1.05 | 0.04272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | GANO 3 | 0.9659 | 0.8906 | -0.0753 |  | 0.9 | 1.05 | 0.06272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | GANO 3 | 0.9659 | 0.8906 | -0.0753 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | GANO 3 | 0.9659 | 0.8906 | -0.0753 |  | 0.9 | 1.05 | 0.05049 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | GANO 3 | 0.9659 | 0.8906 | -0.0753 |  | 0.9 | 1.05 | 0.05297 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | GANO 3 | 0.9659 | 0.8906 | -0.0753 |  | 0.9 | 1.05 | 0.04447 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | GANO 3 | 0.9659 | 0.8906 | -0.0753 |  | 0.9 | 1.05 | 0.04795 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | GANO 3 | 0.9659 | 0.8906 | -0.0753 |  | 0.9 | 1.05 | 0.05827 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | GANO 3 | 0.9659 | 0.8906 | -0.0753 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | GANO 3 | 0.9659 | 0.8906 | -0.0753 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | GANO 3 | 0.9659 | 0.8906 | -0.0753 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | GANO 3 | 0.9659 | 0.8906 | -0.0753 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | GANO 3 | 0.9659 | 0.8906 | -0.0753 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | GANO 3 | 0.9659 | 0.8906 | -0.0753 |  | 0.9 | 1.05 | 0.04781 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | GANO 3 | 0.9659 | 0.8906 | -0.0753 |  | 0.9 | 1.05 | 0.05112 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | GANO 3 | 0.9659 | 0.8906 | -0.0753 |  | 0.9 | 1.05 | 0.03494 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | GANO 3 | 0.9659 | 0.8906 | -0.0753 |  | 0.9 | 1.05 | 0.04759 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | GANO 3 | 0.9659 | 0.8906 | -0.0753 |  | 0.9 | 1.05 | 0.05002 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | GANO 3 | 0.9659 | 0.8906 | -0.0753 |  | 0.9 | 1.05 | 0.04842 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | GANO 3 | 0.9659 | 0.8906 | -0.0753 |  | 0.9 | 1.05 | 0.05452 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | GANO 3 | 0.9659 | 0.8906 | -0.0753 |  | 0.9 | 1.05 | 0.05387 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | GANO 3 | 0.9659 | 0.8906 | -0.0753 |  | 0.9 | 1.05 | 0.03786 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | GANO 3 | 0.9659 | 0.8906 | -0.0753 |  | 0.9 | 1.05 | 0.04954 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | GANO 3 | 0.9659 | 0.8906 | -0.0753 |  | 0.9 | 1.05 | 0.04065 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.10414 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.10414 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.10414 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.10414 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.0987 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.0987 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.0987 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.0987 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.08024 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.08024 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.08024 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.08024 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.14298 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.14298 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.14298 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.14298 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.10266 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.10266 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.10266 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.10266 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.11064 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.11064 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.11064 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.11064 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.08095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.08095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.08095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.08095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.09571 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.09571 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.09571 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.09571 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.12796 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.12796 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.12796 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.12796 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.09379 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.09379 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.09379 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.09379 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.09379 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.09379 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.09379 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.09379 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.09507 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.09507 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.09507 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.09507 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.10446 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.10446 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.10446 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.10446 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.05698 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.05698 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.05698 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.05698 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.09445 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.09445 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.09445 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.09445 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.10129 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.10129 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.10129 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.10129 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.0967 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.0967 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.0967 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.0967 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.11534 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.11534 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.11534 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.11534 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.11336 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.11336 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.11336 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.11336 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.06542 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.06542 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.06542 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.06542 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.09991 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.09991 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.09991 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.09991 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.0742 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | ABBK 3 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.0742 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.0742 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | ASGI_12_06 | 1.0044 | 0.8912 | -0.1132 |  | 0.9 | 1.05 | 0.0742 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | TRIBUNE3 | 0.97 | 0.8913 | -0.0787 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | TRIBUNE3 | 0.97 | 0.8913 | -0.0787 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | TRIBUNE3 | 0.97 | 0.8913 | -0.0787 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | TRIBUNE3 | 0.97 | 0.8913 | -0.0787 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | TRIBUNE3 | 0.97 | 0.8913 | -0.0787 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | TRIBUNE3 | 0.97 | 0.8913 | -0.0787 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | TRIBUNE3 | 0.97 | 0.8913 | -0.0787 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | TRIBUNE3 | 0.97 | 0.8913 | -0.0787 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | TRIBUNE3 | 0.97 | 0.8913 | -0.0787 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | TRIBUNE3 | 0.97 | 0.8913 | -0.0787 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | TRIBUNE3 | 0.97 | 0.8913 | -0.0787 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | TRIBUNE3 | 0.97 | 0.8913 | -0.0787 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | TRIBUNE3 | 0.97 | 0.8913 | -0.0787 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | TRIBUNE3 | 0.97 | 0.8913 | -0.0787 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | TRIBUNE3 | 0.97 | 0.8913 | -0.0787 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | TRIBUNE3 | 0.97 | 0.8913 | -0.0787 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | TRIBUNE3 | 0.97 | 0.8913 | -0.0787 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | TRIBUNE3 | 0.97 | 0.8913 | -0.0787 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | TRIBUNE3 | 0.97 | 0.8913 | -0.0787 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | TRIBUNE3 | 0.97 | 0.8913 | -0.0787 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | TRIBUNE3 | 0.97 | 0.8913 | -0.0787 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | TRIBUNE3 | 0.97 | 0.8913 | -0.0787 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | TRIBUNE3 | 0.97 | 0.8913 | -0.0787 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | TRIBUNE3 | 0.97 | 0.8913 | -0.0787 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | TRIBUNE3 | 0.97 | 0.8913 | -0.0787 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | TRIBUNE3 | 0.97 | 0.8913 | -0.0787 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | TRIBUNE3 | 0.97 | 0.8913 | -0.0787 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | GOVE 3 | 0.9781 | 0.8918 | -0.0863 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | TRIB SW3 | 0.97 | 0.8918 | -0.0782 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | MCDONLD3 | 0.9709 | 0.8918 | -0.0791 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | MCDONLD3 | 0.9746 | 0.8918 | -0.0828 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | GOVE 3 | 0.9781 | 0.8918 | -0.0863 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | TRIB SW3 | 0.97 | 0.8918 | -0.0782 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | MCDONLD3 | 0.9709 | 0.8918 | -0.0791 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | MCDONLD3 | 0.9746 | 0.8918 | -0.0828 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | GOVE 3 | 0.9781 | 0.8918 | -0.0863 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | TRIB SW3 | 0.97 | 0.8918 | -0.0782 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | MCDONLD3 | 0.9709 | 0.8918 | -0.0791 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | MCDONLD3 | 0.9746 | 0.8918 | -0.0828 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | GOVE 3 | 0.9781 | 0.8918 | -0.0863 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | TRIB SW3 | 0.97 | 0.8918 | -0.0782 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | MCDONLD3 | 0.9709 | 0.8918 | -0.0791 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | MCDONLD3 | 0.9746 | 0.8918 | -0.0828 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | GOVE 3 | 0.9781 | 0.8918 | -0.0863 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | TRIB SW3 | 0.97 | 0.8918 | -0.0782 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | MCDONLD3 | 0.9709 | 0.8918 | -0.0791 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | MCDONLD3 | 0.9746 | 0.8918 | -0.0828 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | GOVE 3 | 0.9781 | 0.8918 | -0.0863 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | TRIB SW3 | 0.97 | 0.8918 | -0.0782 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | MCDONLD3 | 0.9709 | 0.8918 | -0.0791 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | MCDONLD3 | 0.9746 | 0.8918 | -0.0828 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | GOVE 3 | 0.9781 | 0.8918 | -0.0863 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | TRIB SW3 | 0.97 | 0.8918 | -0.0782 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | MCDONLD3 | 0.9709 | 0.8918 | -0.0791 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | MCDONLD3 | 0.9746 | 0.8918 | -0.0828 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | GOVE 3 | 0.9781 | 0.8918 | -0.0863 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | TRIB SW3 | 0.97 | 0.8918 | -0.0782 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | MCDONLD3 | 0.9709 | 0.8918 | -0.0791 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | MCDONLD3 | 0.9746 | 0.8918 | -0.0828 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | GOVE 3 | 0.9781 | 0.8918 | -0.0863 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | TRIB SW3 | 0.97 | 0.8918 | -0.0782 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | MCDONLD3 | 0.9709 | 0.8918 | -0.0791 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | MCDONLD3 | 0.9746 | 0.8918 | -0.0828 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | GOVE 3 | 0.9781 | 0.8918 | -0.0863 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | TRIB SW3 | 0.97 | 0.8918 | -0.0782 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | MCDONLD3 | 0.9709 | 0.8918 | -0.0791 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | MCDONLD3 | 0.9746 | 0.8918 | -0.0828 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | GOVE 3 | 0.9781 | 0.8918 | -0.0863 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | TRIB SW3 | 0.97 | 0.8918 | -0.0782 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | MCDONLD3 | 0.9709 | 0.8918 | -0.0791 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | MCDONLD3 | 0.9746 | 0.8918 | -0.0828 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | GOVE 3 | 0.9781 | 0.8918 | -0.0863 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | TRIB SW3 | 0.97 | 0.8918 | -0.0782 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | MCDONLD3 | 0.9709 | 0.8918 | -0.0791 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | MCDONLD3 | 0.9746 | 0.8918 | -0.0828 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | GOVE 3 | 0.9781 | 0.8918 | -0.0863 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | TRIB SW3 | 0.97 | 0.8918 | -0.0782 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | MCDONLD3 | 0.9709 | 0.8918 | -0.0791 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | MCDONLD3 | 0.9746 | 0.8918 | -0.0828 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | GOVE 3 | 0.9781 | 0.8918 | -0.0863 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | TRIB SW3 | 0.97 | 0.8918 | -0.0782 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | MCDONLD3 | 0.9709 | 0.8918 | -0.0791 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | MCDONLD3 | 0.9746 | 0.8918 | -0.0828 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | GOVE 3 | 0.9781 | 0.8918 | -0.0863 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | TRIB SW3 | 0.97 | 0.8918 | -0.0782 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | MCDONLD3 | 0.9709 | 0.8918 | -0.0791 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | MCDONLD3 | 0.9746 | 0.8918 | -0.0828 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | GOVE 3 | 0.9781 | 0.8918 | -0.0863 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | TRIB SW3 | 0.97 | 0.8918 | -0.0782 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | MCDONLD3 | 0.9709 | 0.8918 | -0.0791 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | MCDONLD3 | 0.9746 | 0.8918 | -0.0828 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | GOVE 3 | 0.9781 | 0.8918 | -0.0863 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | TRIB SW3 | 0.97 | 0.8918 | -0.0782 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | MCDONLD3 | 0.9709 | 0.8918 | -0.0791 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | MCDONLD3 | 0.9746 | 0.8918 | -0.0828 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | GOVE 3 | 0.9781 | 0.8918 | -0.0863 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | TRIB SW3 | 0.97 | 0.8918 | -0.0782 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | MCDONLD3 | 0.9709 | 0.8918 | -0.0791 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | MCDONLD3 | 0.9746 | 0.8918 | -0.0828 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | GOVE 3 | 0.9781 | 0.8918 | -0.0863 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | TRIB SW3 | 0.97 | 0.8918 | -0.0782 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | MCDONLD3 | 0.9709 | 0.8918 | -0.0791 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | MCDONLD3 | 0.9746 | 0.8918 | -0.0828 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | GOVE 3 | 0.9781 | 0.8918 | -0.0863 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | TRIB SW3 | 0.97 | 0.8918 | -0.0782 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | MCDONLD3 | 0.9709 | 0.8918 | -0.0791 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | MCDONLD3 | 0.9746 | 0.8918 | -0.0828 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | GOVE 3 | 0.9781 | 0.8918 | -0.0863 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | TRIB SW3 | 0.97 | 0.8918 | -0.0782 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | MCDONLD3 | 0.9709 | 0.8918 | -0.0791 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | MCDONLD3 | 0.9746 | 0.8918 | -0.0828 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | GOVE 3 | 0.9781 | 0.8918 | -0.0863 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | TRIB SW3 | 0.97 | 0.8918 | -0.0782 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | MCDONLD3 | 0.9709 | 0.8918 | -0.0791 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | MCDONLD3 | 0.9746 | 0.8918 | -0.0828 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | GOVE 3 | 0.9781 | 0.8918 | -0.0863 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | TRIB SW3 | 0.97 | 0.8918 | -0.0782 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | MCDONLD3 | 0.9709 | 0.8918 | -0.0791 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | MCDONLD3 | 0.9746 | 0.8918 | -0.0828 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | GOVE 3 | 0.9781 | 0.8918 | -0.0863 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | TRIB SW3 | 0.97 | 0.8918 | -0.0782 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | MCDONLD3 | 0.9709 | 0.8918 | -0.0791 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | MCDONLD3 | 0.9746 | 0.8918 | -0.0828 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | GOVE 3 | 0.9781 | 0.8918 | -0.0863 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | TRIB SW3 | 0.97 | 0.8918 | -0.0782 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | MCDONLD3 | 0.9709 | 0.8918 | -0.0791 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | MCDONLD3 | 0.9746 | 0.8918 | -0.0828 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | GOVE 3 | 0.9781 | 0.8918 | -0.0863 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | TRIB SW3 | 0.97 | 0.8918 | -0.0782 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | MCDONLD3 | 0.9709 | 0.8918 | -0.0791 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | MCDONLD3 | 0.9746 | 0.8918 | -0.0828 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | GOVE 3 | 0.9781 | 0.8918 | -0.0863 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | TRIB SW3 | 0.97 | 0.8918 | -0.0782 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | MCDONLD3 | 0.9709 | 0.8918 | -0.0791 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | MCDONLD3 | 0.9746 | 0.8918 | -0.0828 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | BIRDCTY3 | 0.9856 | 0.8919 | -0.0937 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | BIRDCTY3 | 0.989 | 0.8919 | -0.0971 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | BIRDCTY3 | 0.9856 | 0.8919 | -0.0937 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | BIRDCTY3 | 0.989 | 0.8919 | -0.0971 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | BIRDCTY3 | 0.9856 | 0.8919 | -0.0937 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | BIRDCTY3 | 0.989 | 0.8919 | -0.0971 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | BIRDCTY3 | 0.9856 | 0.8919 | -0.0937 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | BIRDCTY3 | 0.989 | 0.8919 | -0.0971 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | BIRDCTY3 | 0.9856 | 0.8919 | -0.0937 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | BIRDCTY3 | 0.989 | 0.8919 | -0.0971 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | BIRDCTY3 | 0.9856 | 0.8919 | -0.0937 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | BIRDCTY3 | 0.989 | 0.8919 | -0.0971 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | BIRDCTY3 | 0.9856 | 0.8919 | -0.0937 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | BIRDCTY3 | 0.989 | 0.8919 | -0.0971 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | BIRDCTY3 | 0.9856 | 0.8919 | -0.0937 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | BIRDCTY3 | 0.989 | 0.8919 | -0.0971 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | BIRDCTY3 | 0.9856 | 0.8919 | -0.0937 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | BIRDCTY3 | 0.989 | 0.8919 | -0.0971 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | BIRDCTY3 | 0.9856 | 0.8919 | -0.0937 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | BIRDCTY3 | 0.989 | 0.8919 | -0.0971 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | BIRDCTY3 | 0.9856 | 0.8919 | -0.0937 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | BIRDCTY3 | 0.989 | 0.8919 | -0.0971 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | BIRDCTY3 | 0.9856 | 0.8919 | -0.0937 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | BIRDCTY3 | 0.989 | 0.8919 | -0.0971 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | BIRDCTY3 | 0.9856 | 0.8919 | -0.0937 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | BIRDCTY3 | 0.989 | 0.8919 | -0.0971 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | BIRDCTY3 | 0.9856 | 0.8919 | -0.0937 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | BIRDCTY3 | 0.989 | 0.8919 | -0.0971 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | BIRDCTY3 | 0.9856 | 0.8919 | -0.0937 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | BIRDCTY3 | 0.989 | 0.8919 | -0.0971 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | BIRDCTY3 | 0.9856 | 0.8919 | -0.0937 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | BIRDCTY3 | 0.989 | 0.8919 | -0.0971 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | BIRDCTY3 | 0.9856 | 0.8919 | -0.0937 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | BIRDCTY3 | 0.989 | 0.8919 | -0.0971 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | BIRDCTY3 | 0.9856 | 0.8919 | -0.0937 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | BIRDCTY3 | 0.989 | 0.8919 | -0.0971 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | BIRDCTY3 | 0.9856 | 0.8919 | -0.0937 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | BIRDCTY3 | 0.989 | 0.8919 | -0.0971 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | BIRDCTY3 | 0.9856 | 0.8919 | -0.0937 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | BIRDCTY3 | 0.989 | 0.8919 | -0.0971 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | BIRDCTY3 | 0.9856 | 0.8919 | -0.0937 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | BIRDCTY3 | 0.989 | 0.8919 | -0.0971 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | BIRDCTY3 | 0.9856 | 0.8919 | -0.0937 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | BIRDCTY3 | 0.989 | 0.8919 | -0.0971 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | BIRDCTY3 | 0.9856 | 0.8919 | -0.0937 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | BIRDCTY3 | 0.989 | 0.8919 | -0.0971 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | BIRDCTY3 | 0.9856 | 0.8919 | -0.0937 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | BIRDCTY3 | 0.989 | 0.8919 | -0.0971 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | BIRDCTY3 | 0.9856 | 0.8919 | -0.0937 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | BIRDCTY3 | 0.989 | 0.8919 | -0.0971 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | BIRDCTY3 | 0.9856 | 0.8919 | -0.0937 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | BIRDCTY3 | 0.989 | 0.8919 | -0.0971 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | BIRDCTY3 | 0.9856 | 0.8919 | -0.0937 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | BIRDCTY3 | 0.989 | 0.8919 | -0.0971 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | TRIBUNE3 | 0.9756 | 0.892 | -0.0836 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | TRIBUNE3 | 0.9846 | 0.892 | -0.0926 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | TRIBUNE3 | 0.9756 | 0.892 | -0.0836 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | TRIBUNE3 | 0.9846 | 0.892 | -0.0926 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | TRIBUNE3 | 0.9756 | 0.892 | -0.0836 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | TRIBUNE3 | 0.9846 | 0.892 | -0.0926 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | TRIBUNE3 | 0.9756 | 0.892 | -0.0836 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | TRIBUNE3 | 0.9846 | 0.892 | -0.0926 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | TRIBUNE3 | 0.9756 | 0.892 | -0.0836 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | TRIBUNE3 | 0.9846 | 0.892 | -0.0926 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | TRIBUNE3 | 0.9756 | 0.892 | -0.0836 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | TRIBUNE3 | 0.9846 | 0.892 | -0.0926 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | TRIBUNE3 | 0.9756 | 0.892 | -0.0836 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | TRIBUNE3 | 0.9846 | 0.892 | -0.0926 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | TRIBUNE3 | 0.9756 | 0.892 | -0.0836 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | TRIBUNE3 | 0.9846 | 0.892 | -0.0926 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | TRIBUNE3 | 0.9756 | 0.892 | -0.0836 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | TRIBUNE3 | 0.9846 | 0.892 | -0.0926 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | TRIBUNE3 | 0.9756 | 0.892 | -0.0836 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | TRIBUNE3 | 0.9846 | 0.892 | -0.0926 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | TRIBUNE3 | 0.9756 | 0.892 | -0.0836 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | TRIBUNE3 | 0.9846 | 0.892 | -0.0926 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | TRIBUNE3 | 0.9756 | 0.892 | -0.0836 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | TRIBUNE3 | 0.9846 | 0.892 | -0.0926 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | TRIBUNE3 | 0.9756 | 0.892 | -0.0836 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | TRIBUNE3 | 0.9846 | 0.892 | -0.0926 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | TRIBUNE3 | 0.9756 | 0.892 | -0.0836 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | TRIBUNE3 | 0.9846 | 0.892 | -0.0926 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | TRIBUNE3 | 0.9756 | 0.892 | -0.0836 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | TRIBUNE3 | 0.9846 | 0.892 | -0.0926 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | TRIBUNE3 | 0.9756 | 0.892 | -0.0836 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | TRIBUNE3 | 0.9846 | 0.892 | -0.0926 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | TRIBUNE3 | 0.9756 | 0.892 | -0.0836 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | TRIBUNE3 | 0.9846 | 0.892 | -0.0926 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | TRIBUNE3 | 0.9756 | 0.892 | -0.0836 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | TRIBUNE3 | 0.9846 | 0.892 | -0.0926 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | TRIBUNE3 | 0.9756 | 0.892 | -0.0836 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | TRIBUNE3 | 0.9846 | 0.892 | -0.0926 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | TRIBUNE3 | 0.9756 | 0.892 | -0.0836 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | TRIBUNE3 | 0.9846 | 0.892 | -0.0926 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | TRIBUNE3 | 0.9756 | 0.892 | -0.0836 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | TRIBUNE3 | 0.9846 | 0.892 | -0.0926 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | TRIBUNE3 | 0.9756 | 0.892 | -0.0836 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | TRIBUNE3 | 0.9846 | 0.892 | -0.0926 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | TRIBUNE3 | 0.9756 | 0.892 | -0.0836 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | TRIBUNE3 | 0.9846 | 0.892 | -0.0926 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | TRIBUNE3 | 0.9756 | 0.892 | -0.0836 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | TRIBUNE3 | 0.9846 | 0.892 | -0.0926 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | TRIBUNE3 | 0.9756 | 0.892 | -0.0836 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | TRIBUNE3 | 0.9846 | 0.892 | -0.0926 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | TRIBUNE3 | 0.9756 | 0.892 | -0.0836 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | TRIBUNE3 | 0.9846 | 0.892 | -0.0926 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | TRIBUNE3 | 0.9756 | 0.892 | -0.0836 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | TRIBUNE3 | 0.9846 | 0.892 | -0.0926 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | SYRACUS3 | 0.9766 | 0.8921 | -0.0845 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | TRIB SW3 | 0.9754 | 0.8921 | -0.0833 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | SYRACUS3 | 0.9766 | 0.8921 | -0.0845 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | TRIB SW3 | 0.9754 | 0.8921 | -0.0833 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | SYRACUS3 | 0.9766 | 0.8921 | -0.0845 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | TRIB SW3 | 0.9754 | 0.8921 | -0.0833 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | SYRACUS3 | 0.9766 | 0.8921 | -0.0845 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | TRIB SW3 | 0.9754 | 0.8921 | -0.0833 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | SYRACUS3 | 0.9766 | 0.8921 | -0.0845 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | TRIB SW3 | 0.9754 | 0.8921 | -0.0833 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | SYRACUS3 | 0.9766 | 0.8921 | -0.0845 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | TRIB SW3 | 0.9754 | 0.8921 | -0.0833 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | SYRACUS3 | 0.9766 | 0.8921 | -0.0845 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | TRIB SW3 | 0.9754 | 0.8921 | -0.0833 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | SYRACUS3 | 0.9766 | 0.8921 | -0.0845 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | TRIB SW3 | 0.9754 | 0.8921 | -0.0833 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | SYRACUS3 | 0.9766 | 0.8921 | -0.0845 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | TRIB SW3 | 0.9754 | 0.8921 | -0.0833 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | SYRACUS3 | 0.9766 | 0.8921 | -0.0845 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | TRIB SW3 | 0.9754 | 0.8921 | -0.0833 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | SYRACUS3 | 0.9766 | 0.8921 | -0.0845 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | TRIB SW3 | 0.9754 | 0.8921 | -0.0833 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | SYRACUS3 | 0.9766 | 0.8921 | -0.0845 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | TRIB SW3 | 0.9754 | 0.8921 | -0.0833 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | SYRACUS3 | 0.9766 | 0.8921 | -0.0845 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | TRIB SW3 | 0.9754 | 0.8921 | -0.0833 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | SYRACUS3 | 0.9766 | 0.8921 | -0.0845 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | TRIB SW3 | 0.9754 | 0.8921 | -0.0833 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | SYRACUS3 | 0.9766 | 0.8921 | -0.0845 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | TRIB SW3 | 0.9754 | 0.8921 | -0.0833 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | SYRACUS3 | 0.9766 | 0.8921 | -0.0845 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | TRIB SW3 | 0.9754 | 0.8921 | -0.0833 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | SYRACUS3 | 0.9766 | 0.8921 | -0.0845 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | TRIB SW3 | 0.9754 | 0.8921 | -0.0833 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | SYRACUS3 | 0.9766 | 0.8921 | -0.0845 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | TRIB SW3 | 0.9754 | 0.8921 | -0.0833 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | SYRACUS3 | 0.9766 | 0.8921 | -0.0845 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | TRIB SW3 | 0.9754 | 0.8921 | -0.0833 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | SYRACUS3 | 0.9766 | 0.8921 | -0.0845 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | TRIB SW3 | 0.9754 | 0.8921 | -0.0833 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | SYRACUS3 | 0.9766 | 0.8921 | -0.0845 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | TRIB SW3 | 0.9754 | 0.8921 | -0.0833 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | SYRACUS3 | 0.9766 | 0.8921 | -0.0845 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | TRIB SW3 | 0.9754 | 0.8921 | -0.0833 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | SYRACUS3 | 0.9766 | 0.8921 | -0.0845 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | TRIB SW3 | 0.9754 | 0.8921 | -0.0833 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | SYRACUS3 | 0.9766 | 0.8921 | -0.0845 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | TRIB SW3 | 0.9754 | 0.8921 | -0.0833 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | SYRACUS3 | 0.9766 | 0.8921 | -0.0845 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | TRIB SW3 | 0.9754 | 0.8921 | -0.0833 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | SYRACUS3 | 0.9766 | 0.8921 | -0.0845 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | TRIB SW3 | 0.9754 | 0.8921 | -0.0833 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | SYRACUS3 | 0.9766 | 0.8921 | -0.0845 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | TRIB SW3 | 0.9754 | 0.8921 | -0.0833 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | BEELER 3 | 0.9626 | 0.8922 | -0.0704 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | BEELER 3 | 0.9626 | 0.8922 | -0.0704 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | BEELER 3 | 0.9626 | 0.8922 | -0.0704 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | BEELER 3 | 0.9626 | 0.8922 | -0.0704 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | BEELER 3 | 0.9626 | 0.8922 | -0.0704 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | BEELER 3 | 0.9626 | 0.8922 | -0.0704 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | BEELER 3 | 0.9626 | 0.8922 | -0.0704 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | BEELER 3 | 0.9626 | 0.8922 | -0.0704 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | BEELER 3 | 0.9626 | 0.8922 | -0.0704 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | BEELER 3 | 0.9626 | 0.8922 | -0.0704 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | BEELER 3 | 0.9626 | 0.8922 | -0.0704 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | BEELER 3 | 0.9626 | 0.8922 | -0.0704 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | BEELER 3 | 0.9626 | 0.8922 | -0.0704 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | BEELER 3 | 0.9626 | 0.8922 | -0.0704 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | BEELER 3 | 0.9626 | 0.8922 | -0.0704 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | BEELER 3 | 0.9626 | 0.8922 | -0.0704 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | BEELER 3 | 0.9626 | 0.8922 | -0.0704 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | BEELER 3 | 0.9626 | 0.8922 | -0.0704 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | BEELER 3 | 0.9626 | 0.8922 | -0.0704 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | BEELER 3 | 0.9626 | 0.8922 | -0.0704 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | BEELER 3 | 0.9626 | 0.8922 | -0.0704 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | BEELER 3 | 0.9626 | 0.8922 | -0.0704 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | BEELER 3 | 0.9626 | 0.8922 | -0.0704 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | BEELER 3 | 0.9626 | 0.8922 | -0.0704 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | BEELER 3 | 0.9626 | 0.8922 | -0.0704 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | BEELER 3 | 0.9626 | 0.8922 | -0.0704 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | BEELER 3 | 0.9626 | 0.8922 | -0.0704 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | SELKIRK3 | 0.9701 | 0.8929 | -0.0772 |  | 0.9 | 1.05 | 0.05101 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | SELKIRK3 | 0.9824 | 0.8929 | -0.0895 |  | 0.9 | 1.05 | 0.05115 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | SELKIRK3 | 0.9701 | 0.8929 | -0.0772 |  | 0.9 | 1.05 | 0.04911 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | SELKIRK3 | 0.9824 | 0.8929 | -0.0895 |  | 0.9 | 1.05 | 0.04926 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | SELKIRK3 | 0.9701 | 0.8929 | -0.0772 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | SELKIRK3 | 0.9824 | 0.8929 | -0.0895 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | SELKIRK3 | 0.9701 | 0.8929 | -0.0772 |  | 0.9 | 1.05 | 0.04272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | SELKIRK3 | 0.9824 | 0.8929 | -0.0895 |  | 0.9 | 1.05 | 0.04287 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | SELKIRK3 | 0.9701 | 0.8929 | -0.0772 |  | 0.9 | 1.05 | 0.06272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | SELKIRK3 | 0.9824 | 0.8929 | -0.0895 |  | 0.9 | 1.05 | 0.06285 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | SELKIRK3 | 0.9701 | 0.8929 | -0.0772 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | SELKIRK3 | 0.9824 | 0.8929 | -0.0895 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | SELKIRK3 | 0.9701 | 0.8929 | -0.0772 |  | 0.9 | 1.05 | 0.05049 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | SELKIRK3 | 0.9824 | 0.8929 | -0.0895 |  | 0.9 | 1.05 | 0.05063 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | SELKIRK3 | 0.9701 | 0.8929 | -0.0772 |  | 0.9 | 1.05 | 0.05297 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | SELKIRK3 | 0.9824 | 0.8929 | -0.0895 |  | 0.9 | 1.05 | 0.05311 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | SELKIRK3 | 0.9701 | 0.8929 | -0.0772 |  | 0.9 | 1.05 | 0.04447 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | SELKIRK3 | 0.9824 | 0.8929 | -0.0895 |  | 0.9 | 1.05 | 0.04461 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | SELKIRK3 | 0.9701 | 0.8929 | -0.0772 |  | 0.9 | 1.05 | 0.04795 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | SELKIRK3 | 0.9824 | 0.8929 | -0.0895 |  | 0.9 | 1.05 | 0.0481 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | SELKIRK3 | 0.9701 | 0.8929 | -0.0772 |  | 0.9 | 1.05 | 0.05827 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | SELKIRK3 | 0.9824 | 0.8929 | -0.0895 |  | 0.9 | 1.05 | 0.0584 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | SELKIRK3 | 0.9701 | 0.8929 | -0.0772 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | SELKIRK3 | 0.9824 | 0.8929 | -0.0895 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | SELKIRK3 | 0.9701 | 0.8929 | -0.0772 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | SELKIRK3 | 0.9824 | 0.8929 | -0.0895 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | SELKIRK3 | 0.9701 | 0.8929 | -0.0772 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | SELKIRK3 | 0.9824 | 0.8929 | -0.0895 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | SELKIRK3 | 0.9701 | 0.8929 | -0.0772 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | SELKIRK3 | 0.9824 | 0.8929 | -0.0895 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | SELKIRK3 | 0.9701 | 0.8929 | -0.0772 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | SELKIRK3 | 0.9824 | 0.8929 | -0.0895 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | SELKIRK3 | 0.9701 | 0.8929 | -0.0772 |  | 0.9 | 1.05 | 0.04781 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | SELKIRK3 | 0.9824 | 0.8929 | -0.0895 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | SELKIRK3 | 0.9701 | 0.8929 | -0.0772 |  | 0.9 | 1.05 | 0.05112 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | SELKIRK3 | 0.9824 | 0.8929 | -0.0895 |  | 0.9 | 1.05 | 0.05126 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | SELKIRK3 | 0.9701 | 0.8929 | -0.0772 |  | 0.9 | 1.05 | 0.03494 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | SELKIRK3 | 0.9824 | 0.8929 | -0.0895 |  | 0.9 | 1.05 | 0.0351 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | SELKIRK3 | 0.9701 | 0.8929 | -0.0772 |  | 0.9 | 1.05 | 0.04759 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | SELKIRK3 | 0.9824 | 0.8929 | -0.0895 |  | 0.9 | 1.05 | 0.04774 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | SELKIRK3 | 0.9701 | 0.8929 | -0.0772 |  | 0.9 | 1.05 | 0.05002 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | SELKIRK3 | 0.9824 | 0.8929 | -0.0895 |  | 0.9 | 1.05 | 0.05016 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | SELKIRK3 | 0.9701 | 0.8929 | -0.0772 |  | 0.9 | 1.05 | 0.04842 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | SELKIRK3 | 0.9824 | 0.8929 | -0.0895 |  | 0.9 | 1.05 | 0.04857 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | SELKIRK3 | 0.9701 | 0.8929 | -0.0772 |  | 0.9 | 1.05 | 0.05452 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | SELKIRK3 | 0.9824 | 0.8929 | -0.0895 |  | 0.9 | 1.05 | 0.05466 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | SELKIRK3 | 0.9701 | 0.8929 | -0.0772 |  | 0.9 | 1.05 | 0.05387 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | SELKIRK3 | 0.9824 | 0.8929 | -0.0895 |  | 0.9 | 1.05 | 0.05401 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | SELKIRK3 | 0.9701 | 0.8929 | -0.0772 |  | 0.9 | 1.05 | 0.03786 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | SELKIRK3 | 0.9824 | 0.8929 | -0.0895 |  | 0.9 | 1.05 | 0.03802 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | SELKIRK3 | 0.9701 | 0.8929 | -0.0772 |  | 0.9 | 1.05 | 0.04954 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | SELKIRK3 | 0.9824 | 0.8929 | -0.0895 |  | 0.9 | 1.05 | 0.04968 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | SELKIRK3 | 0.9701 | 0.8929 | -0.0772 |  | 0.9 | 1.05 | 0.04065 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | SELKIRK3 | 0.9824 | 0.8929 | -0.0895 |  | 0.9 | 1.05 | 0.04081 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | GODLNDT3 | 0.998 | 0.893 | -0.105 |  | 0.9 | 1.05 | 0.05095 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | GODLNDT3 | 0.998 | 0.893 | -0.105 |  | 0.9 | 1.05 | 0.04905 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | GODLNDT3 | 0.998 | 0.893 | -0.105 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | GODLNDT3 | 0.998 | 0.893 | -0.105 |  | 0.9 | 1.05 | 0.04262 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | GODLNDT3 | 0.998 | 0.893 | -0.105 |  | 0.9 | 1.05 | 0.0627 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | GODLNDT3 | 0.998 | 0.893 | -0.105 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | GODLNDT3 | 0.998 | 0.893 | -0.105 |  | 0.9 | 1.05 | 0.05043 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | GODLNDT3 | 0.998 | 0.893 | -0.105 |  | 0.9 | 1.05 | 0.05292 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | GODLNDT3 | 0.998 | 0.893 | -0.105 |  | 0.9 | 1.05 | 0.0444 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | GODLNDT3 | 0.998 | 0.893 | -0.105 |  | 0.9 | 1.05 | 0.04788 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | GODLNDT3 | 0.998 | 0.893 | -0.105 |  | 0.9 | 1.05 | 0.05824 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | GODLNDT3 | 0.998 | 0.893 | -0.105 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | GODLNDT3 | 0.998 | 0.893 | -0.105 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | GODLNDT3 | 0.998 | 0.893 | -0.105 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | GODLNDT3 | 0.998 | 0.893 | -0.105 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | GODLNDT3 | 0.998 | 0.893 | -0.105 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | GODLNDT3 | 0.998 | 0.893 | -0.105 |  | 0.9 | 1.05 | 0.04773 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | GODLNDT3 | 0.998 | 0.893 | -0.105 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | GODLNDT3 | 0.998 | 0.893 | -0.105 |  | 0.9 | 1.05 | 0.0348 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | GODLNDT3 | 0.998 | 0.893 | -0.105 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | GODLNDT3 | 0.998 | 0.893 | -0.105 |  | 0.9 | 1.05 | 0.04996 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | GODLNDT3 | 0.998 | 0.893 | -0.105 |  | 0.9 | 1.05 | 0.04835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | GODLNDT3 | 0.998 | 0.893 | -0.105 |  | 0.9 | 1.05 | 0.05448 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | GODLNDT3 | 0.998 | 0.893 | -0.105 |  | 0.9 | 1.05 | 0.05382 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | GODLNDT3 | 0.998 | 0.893 | -0.105 |  | 0.9 | 1.05 | 0.03774 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | GODLNDT3 | 0.998 | 0.893 | -0.105 |  | 0.9 | 1.05 | 0.04948 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | GODLNDT3 | 0.998 | 0.893 | -0.105 |  | 0.9 | 1.05 | 0.04054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | TRIBUNE3 | 0.9756 | 0.8936 | -0.082 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | TRIBUNE3 | 0.9756 | 0.8936 | -0.082 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | TRIBUNE3 | 0.9756 | 0.8936 | -0.082 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | TRIBUNE3 | 0.9756 | 0.8936 | -0.082 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | TRIBUNE3 | 0.9756 | 0.8936 | -0.082 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | TRIBUNE3 | 0.9756 | 0.8936 | -0.082 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | TRIBUNE3 | 0.9756 | 0.8936 | -0.082 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | TRIBUNE3 | 0.9756 | 0.8936 | -0.082 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | TRIBUNE3 | 0.9756 | 0.8936 | -0.082 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | TRIBUNE3 | 0.9756 | 0.8936 | -0.082 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | TRIBUNE3 | 0.9756 | 0.8936 | -0.082 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | TRIBUNE3 | 0.9756 | 0.8936 | -0.082 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | TRIBUNE3 | 0.9756 | 0.8936 | -0.082 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | TRIBUNE3 | 0.9756 | 0.8936 | -0.082 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | TRIBUNE3 | 0.9756 | 0.8936 | -0.082 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | TRIBUNE3 | 0.9756 | 0.8936 | -0.082 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | TRIBUNE3 | 0.9756 | 0.8936 | -0.082 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | TRIBUNE3 | 0.9756 | 0.8936 | -0.082 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | TRIBUNE3 | 0.9756 | 0.8936 | -0.082 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | TRIBUNE3 | 0.9756 | 0.8936 | -0.082 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | TRIBUNE3 | 0.9756 | 0.8936 | -0.082 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | TRIBUNE3 | 0.9756 | 0.8936 | -0.082 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | TRIBUNE3 | 0.9756 | 0.8936 | -0.082 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | TRIBUNE3 | 0.9756 | 0.8936 | -0.082 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | TRIBUNE3 | 0.9756 | 0.8936 | -0.082 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | TRIBUNE3 | 0.9756 | 0.8936 | -0.082 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | TRIBUNE3 | 0.9756 | 0.8936 | -0.082 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | TRIB SW3 | 0.9796 | 0.8941 | -0.0855 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | TRIB SW3 | 0.9875 | 0.8941 | -0.0934 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | TRIB SW3 | 0.9796 | 0.8941 | -0.0855 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | TRIB SW3 | 0.9875 | 0.8941 | -0.0934 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | TRIB SW3 | 0.9796 | 0.8941 | -0.0855 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | TRIB SW3 | 0.9875 | 0.8941 | -0.0934 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | TRIB SW3 | 0.9796 | 0.8941 | -0.0855 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | TRIB SW3 | 0.9875 | 0.8941 | -0.0934 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | TRIB SW3 | 0.9796 | 0.8941 | -0.0855 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | TRIB SW3 | 0.9875 | 0.8941 | -0.0934 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | TRIB SW3 | 0.9796 | 0.8941 | -0.0855 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | TRIB SW3 | 0.9875 | 0.8941 | -0.0934 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | TRIB SW3 | 0.9796 | 0.8941 | -0.0855 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | TRIB SW3 | 0.9875 | 0.8941 | -0.0934 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | TRIB SW3 | 0.9796 | 0.8941 | -0.0855 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | TRIB SW3 | 0.9875 | 0.8941 | -0.0934 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | TRIB SW3 | 0.9796 | 0.8941 | -0.0855 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | TRIB SW3 | 0.9875 | 0.8941 | -0.0934 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | TRIB SW3 | 0.9796 | 0.8941 | -0.0855 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | TRIB SW3 | 0.9875 | 0.8941 | -0.0934 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | TRIB SW3 | 0.9796 | 0.8941 | -0.0855 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | TRIB SW3 | 0.9875 | 0.8941 | -0.0934 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | TRIB SW3 | 0.9796 | 0.8941 | -0.0855 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | TRIB SW3 | 0.9875 | 0.8941 | -0.0934 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | TRIB SW3 | 0.9796 | 0.8941 | -0.0855 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | TRIB SW3 | 0.9875 | 0.8941 | -0.0934 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | TRIB SW3 | 0.9796 | 0.8941 | -0.0855 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | TRIB SW3 | 0.9875 | 0.8941 | -0.0934 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | TRIB SW3 | 0.9796 | 0.8941 | -0.0855 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | TRIB SW3 | 0.9875 | 0.8941 | -0.0934 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | TRIB SW3 | 0.9796 | 0.8941 | -0.0855 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | TRIB SW3 | 0.9875 | 0.8941 | -0.0934 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | TRIB SW3 | 0.9796 | 0.8941 | -0.0855 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | TRIB SW3 | 0.9875 | 0.8941 | -0.0934 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | TRIB SW3 | 0.9796 | 0.8941 | -0.0855 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | TRIB SW3 | 0.9875 | 0.8941 | -0.0934 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | TRIB SW3 | 0.9796 | 0.8941 | -0.0855 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | TRIB SW3 | 0.9875 | 0.8941 | -0.0934 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | TRIB SW3 | 0.9796 | 0.8941 | -0.0855 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | TRIB SW3 | 0.9875 | 0.8941 | -0.0934 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | TRIB SW3 | 0.9796 | 0.8941 | -0.0855 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | TRIB SW3 | 0.9875 | 0.8941 | -0.0934 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | TRIB SW3 | 0.9796 | 0.8941 | -0.0855 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | TRIB SW3 | 0.9875 | 0.8941 | -0.0934 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | TRIB SW3 | 0.9796 | 0.8941 | -0.0855 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | TRIB SW3 | 0.9875 | 0.8941 | -0.0934 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | TRIB SW3 | 0.9796 | 0.8941 | -0.0855 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | TRIB SW3 | 0.9875 | 0.8941 | -0.0934 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | TRIB SW3 | 0.9796 | 0.8941 | -0.0855 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | TRIB SW3 | 0.9875 | 0.8941 | -0.0934 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | TRIB SW3 | 0.9796 | 0.8941 | -0.0855 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | TRIB SW3 | 0.9875 | 0.8941 | -0.0934 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | TRIB SW3 | 0.9796 | 0.8941 | -0.0855 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | TRIB SW3 | 0.9875 | 0.8941 | -0.0934 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | GANO 3 | 0.9659 | 0.8942 | -0.0717 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | GANO 3 | 0.9659 | 0.8942 | -0.0717 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | GANO 3 | 0.9659 | 0.8942 | -0.0717 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | GANO 3 | 0.9659 | 0.8942 | -0.0717 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | GANO 3 | 0.9659 | 0.8942 | -0.0717 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | GANO 3 | 0.9659 | 0.8942 | -0.0717 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | GANO 3 | 0.9659 | 0.8942 | -0.0717 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | GANO 3 | 0.9659 | 0.8942 | -0.0717 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | GANO 3 | 0.9659 | 0.8942 | -0.0717 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | GANO 3 | 0.9659 | 0.8942 | -0.0717 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | GANO 3 | 0.9659 | 0.8942 | -0.0717 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | GANO 3 | 0.9659 | 0.8942 | -0.0717 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | GANO 3 | 0.9659 | 0.8942 | -0.0717 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | GANO 3 | 0.9659 | 0.8942 | -0.0717 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | GANO 3 | 0.9659 | 0.8942 | -0.0717 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | GANO 3 | 0.9659 | 0.8942 | -0.0717 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | GANO 3 | 0.9659 | 0.8942 | -0.0717 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | GANO 3 | 0.9659 | 0.8942 | -0.0717 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | GANO 3 | 0.9659 | 0.8942 | -0.0717 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | GANO 3 | 0.9659 | 0.8942 | -0.0717 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | GANO 3 | 0.9659 | 0.8942 | -0.0717 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | GANO 3 | 0.9659 | 0.8942 | -0.0717 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | GANO 3 | 0.9659 | 0.8942 | -0.0717 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | GANO 3 | 0.9659 | 0.8942 | -0.0717 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | GANO 3 | 0.9659 | 0.8942 | -0.0717 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | GANO 3 | 0.9659 | 0.8942 | -0.0717 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | GANO 3 | 0.9659 | 0.8942 | -0.0717 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | KANARAD3 | 0.9653 | 0.8943 | -0.071 |  | 0.9 | 1.05 | 0.05101 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | KANARAD3 | 0.9653 | 0.8943 | -0.071 |  | 0.9 | 1.05 | 0.04911 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | KANARAD3 | 0.9653 | 0.8943 | -0.071 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | KANARAD3 | 0.9653 | 0.8943 | -0.071 |  | 0.9 | 1.05 | 0.04272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | KANARAD3 | 0.9653 | 0.8943 | -0.071 |  | 0.9 | 1.05 | 0.06272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | KANARAD3 | 0.9653 | 0.8943 | -0.071 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | KANARAD3 | 0.9653 | 0.8943 | -0.071 |  | 0.9 | 1.05 | 0.05049 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | KANARAD3 | 0.9653 | 0.8943 | -0.071 |  | 0.9 | 1.05 | 0.05297 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | KANARAD3 | 0.9653 | 0.8943 | -0.071 |  | 0.9 | 1.05 | 0.04447 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | KANARAD3 | 0.9653 | 0.8943 | -0.071 |  | 0.9 | 1.05 | 0.04795 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | KANARAD3 | 0.9653 | 0.8943 | -0.071 |  | 0.9 | 1.05 | 0.05827 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | KANARAD3 | 0.9653 | 0.8943 | -0.071 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | KANARAD3 | 0.9653 | 0.8943 | -0.071 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | KANARAD3 | 0.9653 | 0.8943 | -0.071 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | KANARAD3 | 0.9653 | 0.8943 | -0.071 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | KANARAD3 | 0.9653 | 0.8943 | -0.071 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | KANARAD3 | 0.9653 | 0.8943 | -0.071 |  | 0.9 | 1.05 | 0.04781 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | KANARAD3 | 0.9653 | 0.8943 | -0.071 |  | 0.9 | 1.05 | 0.05112 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | KANARAD3 | 0.9653 | 0.8943 | -0.071 |  | 0.9 | 1.05 | 0.03494 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | KANARAD3 | 0.9653 | 0.8943 | -0.071 |  | 0.9 | 1.05 | 0.04759 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | KANARAD3 | 0.9653 | 0.8943 | -0.071 |  | 0.9 | 1.05 | 0.05002 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | KANARAD3 | 0.9653 | 0.8943 | -0.071 |  | 0.9 | 1.05 | 0.04842 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | KANARAD3 | 0.9653 | 0.8943 | -0.071 |  | 0.9 | 1.05 | 0.05452 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | KANARAD3 | 0.9653 | 0.8943 | -0.071 |  | 0.9 | 1.05 | 0.05387 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | KANARAD3 | 0.9653 | 0.8943 | -0.071 |  | 0.9 | 1.05 | 0.03786 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | KANARAD3 | 0.9653 | 0.8943 | -0.071 |  | 0.9 | 1.05 | 0.04954 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | KANARAD3 | 0.9653 | 0.8943 | -0.071 |  | 0.9 | 1.05 | 0.04065 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | LIBERTY3 | 0.956 | 0.8944 | -0.0616 |  | 0.9 | 1.05 | 0.05101 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | LIBERTY3 | 0.956 | 0.8944 | -0.0616 |  | 0.9 | 1.05 | 0.04911 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | LIBERTY3 | 0.956 | 0.8944 | -0.0616 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | LIBERTY3 | 0.956 | 0.8944 | -0.0616 |  | 0.9 | 1.05 | 0.04272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | LIBERTY3 | 0.956 | 0.8944 | -0.0616 |  | 0.9 | 1.05 | 0.06272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | LIBERTY3 | 0.956 | 0.8944 | -0.0616 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | LIBERTY3 | 0.956 | 0.8944 | -0.0616 |  | 0.9 | 1.05 | 0.05049 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | LIBERTY3 | 0.956 | 0.8944 | -0.0616 |  | 0.9 | 1.05 | 0.05297 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | LIBERTY3 | 0.956 | 0.8944 | -0.0616 |  | 0.9 | 1.05 | 0.04447 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | LIBERTY3 | 0.956 | 0.8944 | -0.0616 |  | 0.9 | 1.05 | 0.04795 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | LIBERTY3 | 0.956 | 0.8944 | -0.0616 |  | 0.9 | 1.05 | 0.05827 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | LIBERTY3 | 0.956 | 0.8944 | -0.0616 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | LIBERTY3 | 0.956 | 0.8944 | -0.0616 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | LIBERTY3 | 0.956 | 0.8944 | -0.0616 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | LIBERTY3 | 0.956 | 0.8944 | -0.0616 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | LIBERTY3 | 0.956 | 0.8944 | -0.0616 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | LIBERTY3 | 0.956 | 0.8944 | -0.0616 |  | 0.9 | 1.05 | 0.04781 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | LIBERTY3 | 0.956 | 0.8944 | -0.0616 |  | 0.9 | 1.05 | 0.05112 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | LIBERTY3 | 0.956 | 0.8944 | -0.0616 |  | 0.9 | 1.05 | 0.03494 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | LIBERTY3 | 0.956 | 0.8944 | -0.0616 |  | 0.9 | 1.05 | 0.04759 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | LIBERTY3 | 0.956 | 0.8944 | -0.0616 |  | 0.9 | 1.05 | 0.05002 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | LIBERTY3 | 0.956 | 0.8944 | -0.0616 |  | 0.9 | 1.05 | 0.04842 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | LIBERTY3 | 0.956 | 0.8944 | -0.0616 |  | 0.9 | 1.05 | 0.05452 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | LIBERTY3 | 0.956 | 0.8944 | -0.0616 |  | 0.9 | 1.05 | 0.05387 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | LIBERTY3 | 0.956 | 0.8944 | -0.0616 |  | 0.9 | 1.05 | 0.03786 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | LIBERTY3 | 0.956 | 0.8944 | -0.0616 |  | 0.9 | 1.05 | 0.04954 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | LIBERTY3 | 0.956 | 0.8944 | -0.0616 |  | 0.9 | 1.05 | 0.04065 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | GOODLND3 | 0.9987 | 0.895 | -0.1037 |  | 0.9 | 1.05 | 0.05095 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | GOODLND3 | 0.9987 | 0.895 | -0.1037 |  | 0.9 | 1.05 | 0.04905 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | GOODLND3 | 0.9987 | 0.895 | -0.1037 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | GOODLND3 | 0.9987 | 0.895 | -0.1037 |  | 0.9 | 1.05 | 0.04262 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | GOODLND3 | 0.9987 | 0.895 | -0.1037 |  | 0.9 | 1.05 | 0.0627 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | GOODLND3 | 0.9987 | 0.895 | -0.1037 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | GOODLND3 | 0.9987 | 0.895 | -0.1037 |  | 0.9 | 1.05 | 0.05043 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | GOODLND3 | 0.9987 | 0.895 | -0.1037 |  | 0.9 | 1.05 | 0.05292 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | GOODLND3 | 0.9987 | 0.895 | -0.1037 |  | 0.9 | 1.05 | 0.0444 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | GOODLND3 | 0.9987 | 0.895 | -0.1037 |  | 0.9 | 1.05 | 0.04788 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | GOODLND3 | 0.9987 | 0.895 | -0.1037 |  | 0.9 | 1.05 | 0.05824 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | GOODLND3 | 0.9987 | 0.895 | -0.1037 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | GOODLND3 | 0.9987 | 0.895 | -0.1037 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | GOODLND3 | 0.9987 | 0.895 | -0.1037 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | GOODLND3 | 0.9987 | 0.895 | -0.1037 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | GOODLND3 | 0.9987 | 0.895 | -0.1037 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | GOODLND3 | 0.9987 | 0.895 | -0.1037 |  | 0.9 | 1.05 | 0.04773 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | GOODLND3 | 0.9987 | 0.895 | -0.1037 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | GOODLND3 | 0.9987 | 0.895 | -0.1037 |  | 0.9 | 1.05 | 0.0348 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | GOODLND3 | 0.9987 | 0.895 | -0.1037 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | GOODLND3 | 0.9987 | 0.895 | -0.1037 |  | 0.9 | 1.05 | 0.04996 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | GOODLND3 | 0.9987 | 0.895 | -0.1037 |  | 0.9 | 1.05 | 0.04835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | GOODLND3 | 0.9987 | 0.895 | -0.1037 |  | 0.9 | 1.05 | 0.05448 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | GOODLND3 | 0.9987 | 0.895 | -0.1037 |  | 0.9 | 1.05 | 0.05382 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | GOODLND3 | 0.9987 | 0.895 | -0.1037 |  | 0.9 | 1.05 | 0.03774 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | GOODLND3 | 0.9987 | 0.895 | -0.1037 |  | 0.9 | 1.05 | 0.04948 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | GOODLND3 | 0.9987 | 0.895 | -0.1037 |  | 0.9 | 1.05 | 0.04054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | RULETON3 | 0.9711 | 0.8952 | -0.0759 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | ONEOK 3 | 0.971 | 0.8952 | -0.0758 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | ONEOK 3 | 0.9747 | 0.8952 | -0.0795 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | RULETON3 | 0.9711 | 0.8952 | -0.0759 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | ONEOK 3 | 0.971 | 0.8952 | -0.0758 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | ONEOK 3 | 0.9747 | 0.8952 | -0.0795 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | RULETON3 | 0.9711 | 0.8952 | -0.0759 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | ONEOK 3 | 0.971 | 0.8952 | -0.0758 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | ONEOK 3 | 0.9747 | 0.8952 | -0.0795 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | RULETON3 | 0.9711 | 0.8952 | -0.0759 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | ONEOK 3 | 0.971 | 0.8952 | -0.0758 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | ONEOK 3 | 0.9747 | 0.8952 | -0.0795 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | RULETON3 | 0.9711 | 0.8952 | -0.0759 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | ONEOK 3 | 0.971 | 0.8952 | -0.0758 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | ONEOK 3 | 0.9747 | 0.8952 | -0.0795 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | RULETON3 | 0.9711 | 0.8952 | -0.0759 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | ONEOK 3 | 0.971 | 0.8952 | -0.0758 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | ONEOK 3 | 0.9747 | 0.8952 | -0.0795 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | RULETON3 | 0.9711 | 0.8952 | -0.0759 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | ONEOK 3 | 0.971 | 0.8952 | -0.0758 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | ONEOK 3 | 0.9747 | 0.8952 | -0.0795 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | RULETON3 | 0.9711 | 0.8952 | -0.0759 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | ONEOK 3 | 0.971 | 0.8952 | -0.0758 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | ONEOK 3 | 0.9747 | 0.8952 | -0.0795 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | RULETON3 | 0.9711 | 0.8952 | -0.0759 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | ONEOK 3 | 0.971 | 0.8952 | -0.0758 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | ONEOK 3 | 0.9747 | 0.8952 | -0.0795 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | RULETON3 | 0.9711 | 0.8952 | -0.0759 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | ONEOK 3 | 0.971 | 0.8952 | -0.0758 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | ONEOK 3 | 0.9747 | 0.8952 | -0.0795 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | RULETON3 | 0.9711 | 0.8952 | -0.0759 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | ONEOK 3 | 0.971 | 0.8952 | -0.0758 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | ONEOK 3 | 0.9747 | 0.8952 | -0.0795 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | RULETON3 | 0.9711 | 0.8952 | -0.0759 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | ONEOK 3 | 0.971 | 0.8952 | -0.0758 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | ONEOK 3 | 0.9747 | 0.8952 | -0.0795 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | RULETON3 | 0.9711 | 0.8952 | -0.0759 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | ONEOK 3 | 0.971 | 0.8952 | -0.0758 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | ONEOK 3 | 0.9747 | 0.8952 | -0.0795 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | RULETON3 | 0.9711 | 0.8952 | -0.0759 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | ONEOK 3 | 0.971 | 0.8952 | -0.0758 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | ONEOK 3 | 0.9747 | 0.8952 | -0.0795 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | RULETON3 | 0.9711 | 0.8952 | -0.0759 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | ONEOK 3 | 0.971 | 0.8952 | -0.0758 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | ONEOK 3 | 0.9747 | 0.8952 | -0.0795 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | RULETON3 | 0.9711 | 0.8952 | -0.0759 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | ONEOK 3 | 0.971 | 0.8952 | -0.0758 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | ONEOK 3 | 0.9747 | 0.8952 | -0.0795 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | RULETON3 | 0.9711 | 0.8952 | -0.0759 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | ONEOK 3 | 0.971 | 0.8952 | -0.0758 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | ONEOK 3 | 0.9747 | 0.8952 | -0.0795 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | RULETON3 | 0.9711 | 0.8952 | -0.0759 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | ONEOK 3 | 0.971 | 0.8952 | -0.0758 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | ONEOK 3 | 0.9747 | 0.8952 | -0.0795 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | RULETON3 | 0.9711 | 0.8952 | -0.0759 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | ONEOK 3 | 0.971 | 0.8952 | -0.0758 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | ONEOK 3 | 0.9747 | 0.8952 | -0.0795 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | RULETON3 | 0.9711 | 0.8952 | -0.0759 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | ONEOK 3 | 0.971 | 0.8952 | -0.0758 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | ONEOK 3 | 0.9747 | 0.8952 | -0.0795 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | RULETON3 | 0.9711 | 0.8952 | -0.0759 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | ONEOK 3 | 0.971 | 0.8952 | -0.0758 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | ONEOK 3 | 0.9747 | 0.8952 | -0.0795 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | RULETON3 | 0.9711 | 0.8952 | -0.0759 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | ONEOK 3 | 0.971 | 0.8952 | -0.0758 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | ONEOK 3 | 0.9747 | 0.8952 | -0.0795 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | RULETON3 | 0.9711 | 0.8952 | -0.0759 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | ONEOK 3 | 0.971 | 0.8952 | -0.0758 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | ONEOK 3 | 0.9747 | 0.8952 | -0.0795 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | RULETON3 | 0.9711 | 0.8952 | -0.0759 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | ONEOK 3 | 0.971 | 0.8952 | -0.0758 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | ONEOK 3 | 0.9747 | 0.8952 | -0.0795 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | RULETON3 | 0.9711 | 0.8952 | -0.0759 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | ONEOK 3 | 0.971 | 0.8952 | -0.0758 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | ONEOK 3 | 0.9747 | 0.8952 | -0.0795 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | RULETON3 | 0.9711 | 0.8952 | -0.0759 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | ONEOK 3 | 0.971 | 0.8952 | -0.0758 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | ONEOK 3 | 0.9747 | 0.8952 | -0.0795 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | RULETON3 | 0.9711 | 0.8952 | -0.0759 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | ONEOK 3 | 0.971 | 0.8952 | -0.0758 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | ONEOK 3 | 0.9747 | 0.8952 | -0.0795 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | LAWNRID3 | 0.9655 | 0.8953 | -0.0702 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | LAWNRID3 | 0.9655 | 0.8953 | -0.0702 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | LAWNRID3 | 0.9655 | 0.8953 | -0.0702 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | LAWNRID3 | 0.9655 | 0.8953 | -0.0702 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | LAWNRID3 | 0.9655 | 0.8953 | -0.0702 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | LAWNRID3 | 0.9655 | 0.8953 | -0.0702 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | LAWNRID3 | 0.9655 | 0.8953 | -0.0702 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | LAWNRID3 | 0.9655 | 0.8953 | -0.0702 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | LAWNRID3 | 0.9655 | 0.8953 | -0.0702 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | LAWNRID3 | 0.9655 | 0.8953 | -0.0702 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | LAWNRID3 | 0.9655 | 0.8953 | -0.0702 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | LAWNRID3 | 0.9655 | 0.8953 | -0.0702 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | LAWNRID3 | 0.9655 | 0.8953 | -0.0702 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | LAWNRID3 | 0.9655 | 0.8953 | -0.0702 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | LAWNRID3 | 0.9655 | 0.8953 | -0.0702 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | LAWNRID3 | 0.9655 | 0.8953 | -0.0702 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | LAWNRID3 | 0.9655 | 0.8953 | -0.0702 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | LAWNRID3 | 0.9655 | 0.8953 | -0.0702 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | LAWNRID3 | 0.9655 | 0.8953 | -0.0702 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | LAWNRID3 | 0.9655 | 0.8953 | -0.0702 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | LAWNRID3 | 0.9655 | 0.8953 | -0.0702 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | LAWNRID3 | 0.9655 | 0.8953 | -0.0702 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | LAWNRID3 | 0.9655 | 0.8953 | -0.0702 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | LAWNRID3 | 0.9655 | 0.8953 | -0.0702 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | LAWNRID3 | 0.9655 | 0.8953 | -0.0702 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | LAWNRID3 | 0.9655 | 0.8953 | -0.0702 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | LAWNRID3 | 0.9655 | 0.8953 | -0.0702 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | TRIBUNE3 | 0.9797 | 0.8956 | -0.0841 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | TRIBUNE3 | 0.9875 | 0.8956 | -0.0919 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | TRIBUNE3 | 0.9797 | 0.8956 | -0.0841 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | TRIBUNE3 | 0.9875 | 0.8956 | -0.0919 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | TRIBUNE3 | 0.9797 | 0.8956 | -0.0841 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | TRIBUNE3 | 0.9875 | 0.8956 | -0.0919 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | TRIBUNE3 | 0.9797 | 0.8956 | -0.0841 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | TRIBUNE3 | 0.9875 | 0.8956 | -0.0919 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | TRIBUNE3 | 0.9797 | 0.8956 | -0.0841 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | TRIBUNE3 | 0.9875 | 0.8956 | -0.0919 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | TRIBUNE3 | 0.9797 | 0.8956 | -0.0841 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | TRIBUNE3 | 0.9875 | 0.8956 | -0.0919 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | TRIBUNE3 | 0.9797 | 0.8956 | -0.0841 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | TRIBUNE3 | 0.9875 | 0.8956 | -0.0919 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | TRIBUNE3 | 0.9797 | 0.8956 | -0.0841 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | TRIBUNE3 | 0.9875 | 0.8956 | -0.0919 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | TRIBUNE3 | 0.9797 | 0.8956 | -0.0841 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | TRIBUNE3 | 0.9875 | 0.8956 | -0.0919 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | TRIBUNE3 | 0.9797 | 0.8956 | -0.0841 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | TRIBUNE3 | 0.9875 | 0.8956 | -0.0919 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | TRIBUNE3 | 0.9797 | 0.8956 | -0.0841 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | TRIBUNE3 | 0.9875 | 0.8956 | -0.0919 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | TRIBUNE3 | 0.9797 | 0.8956 | -0.0841 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | TRIBUNE3 | 0.9875 | 0.8956 | -0.0919 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | TRIBUNE3 | 0.9797 | 0.8956 | -0.0841 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | TRIBUNE3 | 0.9875 | 0.8956 | -0.0919 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | TRIBUNE3 | 0.9797 | 0.8956 | -0.0841 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | TRIBUNE3 | 0.9875 | 0.8956 | -0.0919 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | TRIBUNE3 | 0.9797 | 0.8956 | -0.0841 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | TRIBUNE3 | 0.9875 | 0.8956 | -0.0919 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | TRIBUNE3 | 0.9797 | 0.8956 | -0.0841 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | TRIBUNE3 | 0.9875 | 0.8956 | -0.0919 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | TRIBUNE3 | 0.9797 | 0.8956 | -0.0841 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | TRIBUNE3 | 0.9875 | 0.8956 | -0.0919 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | TRIBUNE3 | 0.9797 | 0.8956 | -0.0841 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | TRIBUNE3 | 0.9875 | 0.8956 | -0.0919 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | TRIBUNE3 | 0.9797 | 0.8956 | -0.0841 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | TRIBUNE3 | 0.9875 | 0.8956 | -0.0919 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | TRIBUNE3 | 0.9797 | 0.8956 | -0.0841 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | TRIBUNE3 | 0.9875 | 0.8956 | -0.0919 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | TRIBUNE3 | 0.9797 | 0.8956 | -0.0841 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | TRIBUNE3 | 0.9875 | 0.8956 | -0.0919 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | TRIBUNE3 | 0.9797 | 0.8956 | -0.0841 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | TRIBUNE3 | 0.9875 | 0.8956 | -0.0919 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | TRIBUNE3 | 0.9797 | 0.8956 | -0.0841 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | TRIBUNE3 | 0.9875 | 0.8956 | -0.0919 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | TRIBUNE3 | 0.9797 | 0.8956 | -0.0841 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | TRIBUNE3 | 0.9875 | 0.8956 | -0.0919 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | TRIBUNE3 | 0.9797 | 0.8956 | -0.0841 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | TRIBUNE3 | 0.9875 | 0.8956 | -0.0919 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | TRIBUNE3 | 0.9797 | 0.8956 | -0.0841 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | TRIBUNE3 | 0.9875 | 0.8956 | -0.0919 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | TRIBUNE3 | 0.9797 | 0.8956 | -0.0841 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | TRIBUNE3 | 0.9875 | 0.8956 | -0.0919 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | LEOTI 3 | 0.9706 | 0.8957 | -0.0749 |  | 0.9 | 1.05 | 0.05101 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | LEOTI 3 | 0.9706 | 0.8957 | -0.0749 |  | 0.9 | 1.05 | 0.04911 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | LEOTI 3 | 0.9706 | 0.8957 | -0.0749 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | LEOTI 3 | 0.9706 | 0.8957 | -0.0749 |  | 0.9 | 1.05 | 0.04272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | LEOTI 3 | 0.9706 | 0.8957 | -0.0749 |  | 0.9 | 1.05 | 0.06272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | LEOTI 3 | 0.9706 | 0.8957 | -0.0749 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | LEOTI 3 | 0.9706 | 0.8957 | -0.0749 |  | 0.9 | 1.05 | 0.05049 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | LEOTI 3 | 0.9706 | 0.8957 | -0.0749 |  | 0.9 | 1.05 | 0.05297 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | LEOTI 3 | 0.9706 | 0.8957 | -0.0749 |  | 0.9 | 1.05 | 0.04447 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | LEOTI 3 | 0.9706 | 0.8957 | -0.0749 |  | 0.9 | 1.05 | 0.04795 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | LEOTI 3 | 0.9706 | 0.8957 | -0.0749 |  | 0.9 | 1.05 | 0.05827 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | LEOTI 3 | 0.9706 | 0.8957 | -0.0749 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | LEOTI 3 | 0.9706 | 0.8957 | -0.0749 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | LEOTI 3 | 0.9706 | 0.8957 | -0.0749 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | LEOTI 3 | 0.9706 | 0.8957 | -0.0749 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | LEOTI 3 | 0.9706 | 0.8957 | -0.0749 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | LEOTI 3 | 0.9706 | 0.8957 | -0.0749 |  | 0.9 | 1.05 | 0.04781 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | LEOTI 3 | 0.9706 | 0.8957 | -0.0749 |  | 0.9 | 1.05 | 0.05112 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | LEOTI 3 | 0.9706 | 0.8957 | -0.0749 |  | 0.9 | 1.05 | 0.03494 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | LEOTI 3 | 0.9706 | 0.8957 | -0.0749 |  | 0.9 | 1.05 | 0.04759 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | LEOTI 3 | 0.9706 | 0.8957 | -0.0749 |  | 0.9 | 1.05 | 0.05002 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | LEOTI 3 | 0.9706 | 0.8957 | -0.0749 |  | 0.9 | 1.05 | 0.04842 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | LEOTI 3 | 0.9706 | 0.8957 | -0.0749 |  | 0.9 | 1.05 | 0.05452 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | LEOTI 3 | 0.9706 | 0.8957 | -0.0749 |  | 0.9 | 1.05 | 0.05387 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | LEOTI 3 | 0.9706 | 0.8957 | -0.0749 |  | 0.9 | 1.05 | 0.03786 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | LEOTI 3 | 0.9706 | 0.8957 | -0.0749 |  | 0.9 | 1.05 | 0.04954 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | LEOTI 3 | 0.9706 | 0.8957 | -0.0749 |  | 0.9 | 1.05 | 0.04065 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | LEOTI 3 | 0.9833 | 0.8958 | -0.0875 |  | 0.9 | 1.05 | 0.05115 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | LEOTI 3 | 0.9833 | 0.8958 | -0.0875 |  | 0.9 | 1.05 | 0.04926 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | LEOTI 3 | 0.9833 | 0.8958 | -0.0875 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | LEOTI 3 | 0.9833 | 0.8958 | -0.0875 |  | 0.9 | 1.05 | 0.04287 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | LEOTI 3 | 0.9833 | 0.8958 | -0.0875 |  | 0.9 | 1.05 | 0.06285 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | LEOTI 3 | 0.9833 | 0.8958 | -0.0875 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | LEOTI 3 | 0.9833 | 0.8958 | -0.0875 |  | 0.9 | 1.05 | 0.05063 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | LEOTI 3 | 0.9833 | 0.8958 | -0.0875 |  | 0.9 | 1.05 | 0.05311 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | LEOTI 3 | 0.9833 | 0.8958 | -0.0875 |  | 0.9 | 1.05 | 0.04461 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | LEOTI 3 | 0.9833 | 0.8958 | -0.0875 |  | 0.9 | 1.05 | 0.0481 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | LEOTI 3 | 0.9833 | 0.8958 | -0.0875 |  | 0.9 | 1.05 | 0.0584 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | LEOTI 3 | 0.9833 | 0.8958 | -0.0875 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | LEOTI 3 | 0.9833 | 0.8958 | -0.0875 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | LEOTI 3 | 0.9833 | 0.8958 | -0.0875 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | LEOTI 3 | 0.9833 | 0.8958 | -0.0875 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | LEOTI 3 | 0.9833 | 0.8958 | -0.0875 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | LEOTI 3 | 0.9833 | 0.8958 | -0.0875 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | LEOTI 3 | 0.9833 | 0.8958 | -0.0875 |  | 0.9 | 1.05 | 0.05126 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | LEOTI 3 | 0.9833 | 0.8958 | -0.0875 |  | 0.9 | 1.05 | 0.0351 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | LEOTI 3 | 0.9833 | 0.8958 | -0.0875 |  | 0.9 | 1.05 | 0.04774 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | LEOTI 3 | 0.9833 | 0.8958 | -0.0875 |  | 0.9 | 1.05 | 0.05016 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | LEOTI 3 | 0.9833 | 0.8958 | -0.0875 |  | 0.9 | 1.05 | 0.04857 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | LEOTI 3 | 0.9833 | 0.8958 | -0.0875 |  | 0.9 | 1.05 | 0.05466 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | LEOTI 3 | 0.9833 | 0.8958 | -0.0875 |  | 0.9 | 1.05 | 0.05401 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | LEOTI 3 | 0.9833 | 0.8958 | -0.0875 |  | 0.9 | 1.05 | 0.03802 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | LEOTI 3 | 0.9833 | 0.8958 | -0.0875 |  | 0.9 | 1.05 | 0.04968 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | LEOTI 3 | 0.9833 | 0.8958 | -0.0875 |  | 0.9 | 1.05 | 0.04081 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | MANNING3 | 0.9637 | 0.896 | -0.0677 |  | 0.9 | 1.05 | 0.05101 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | MANNING3 | 0.9792 | 0.896 | -0.0832 |  | 0.9 | 1.05 | 0.05115 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | TRIB SW3 | 0.9796 | 0.896 | -0.0836 |  | 0.9 | 1.05 | 0.05095 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | LIBERTY3 | 0.97 | 0.896 | -0.074 |  | 0.9 | 1.05 | 0.05115 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | MANNING3 | 0.9637 | 0.896 | -0.0677 |  | 0.9 | 1.05 | 0.04911 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | MANNING3 | 0.9792 | 0.896 | -0.0832 |  | 0.9 | 1.05 | 0.04926 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | TRIB SW3 | 0.9796 | 0.896 | -0.0836 |  | 0.9 | 1.05 | 0.04905 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | LIBERTY3 | 0.97 | 0.896 | -0.074 |  | 0.9 | 1.05 | 0.04926 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | MANNING3 | 0.9637 | 0.896 | -0.0677 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | MANNING3 | 0.9792 | 0.896 | -0.0832 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | TRIB SW3 | 0.9796 | 0.896 | -0.0836 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | LIBERTY3 | 0.97 | 0.896 | -0.074 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | MANNING3 | 0.9637 | 0.896 | -0.0677 |  | 0.9 | 1.05 | 0.04272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | MANNING3 | 0.9792 | 0.896 | -0.0832 |  | 0.9 | 1.05 | 0.04287 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | TRIB SW3 | 0.9796 | 0.896 | -0.0836 |  | 0.9 | 1.05 | 0.04262 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | LIBERTY3 | 0.97 | 0.896 | -0.074 |  | 0.9 | 1.05 | 0.04287 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | MANNING3 | 0.9637 | 0.896 | -0.0677 |  | 0.9 | 1.05 | 0.06272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | MANNING3 | 0.9792 | 0.896 | -0.0832 |  | 0.9 | 1.05 | 0.06285 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | TRIB SW3 | 0.9796 | 0.896 | -0.0836 |  | 0.9 | 1.05 | 0.0627 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | LIBERTY3 | 0.97 | 0.896 | -0.074 |  | 0.9 | 1.05 | 0.06285 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | MANNING3 | 0.9637 | 0.896 | -0.0677 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | MANNING3 | 0.9792 | 0.896 | -0.0832 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | TRIB SW3 | 0.9796 | 0.896 | -0.0836 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | LIBERTY3 | 0.97 | 0.896 | -0.074 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | MANNING3 | 0.9637 | 0.896 | -0.0677 |  | 0.9 | 1.05 | 0.05049 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | MANNING3 | 0.9792 | 0.896 | -0.0832 |  | 0.9 | 1.05 | 0.05063 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | TRIB SW3 | 0.9796 | 0.896 | -0.0836 |  | 0.9 | 1.05 | 0.05043 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | LIBERTY3 | 0.97 | 0.896 | -0.074 |  | 0.9 | 1.05 | 0.05063 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | MANNING3 | 0.9637 | 0.896 | -0.0677 |  | 0.9 | 1.05 | 0.05297 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | MANNING3 | 0.9792 | 0.896 | -0.0832 |  | 0.9 | 1.05 | 0.05311 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | TRIB SW3 | 0.9796 | 0.896 | -0.0836 |  | 0.9 | 1.05 | 0.05292 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | LIBERTY3 | 0.97 | 0.896 | -0.074 |  | 0.9 | 1.05 | 0.05311 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | MANNING3 | 0.9637 | 0.896 | -0.0677 |  | 0.9 | 1.05 | 0.04447 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | MANNING3 | 0.9792 | 0.896 | -0.0832 |  | 0.9 | 1.05 | 0.04461 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | TRIB SW3 | 0.9796 | 0.896 | -0.0836 |  | 0.9 | 1.05 | 0.0444 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | LIBERTY3 | 0.97 | 0.896 | -0.074 |  | 0.9 | 1.05 | 0.04461 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | MANNING3 | 0.9637 | 0.896 | -0.0677 |  | 0.9 | 1.05 | 0.04795 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | MANNING3 | 0.9792 | 0.896 | -0.0832 |  | 0.9 | 1.05 | 0.0481 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | TRIB SW3 | 0.9796 | 0.896 | -0.0836 |  | 0.9 | 1.05 | 0.04788 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | LIBERTY3 | 0.97 | 0.896 | -0.074 |  | 0.9 | 1.05 | 0.0481 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | MANNING3 | 0.9637 | 0.896 | -0.0677 |  | 0.9 | 1.05 | 0.05827 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | MANNING3 | 0.9792 | 0.896 | -0.0832 |  | 0.9 | 1.05 | 0.0584 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | TRIB SW3 | 0.9796 | 0.896 | -0.0836 |  | 0.9 | 1.05 | 0.05824 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | LIBERTY3 | 0.97 | 0.896 | -0.074 |  | 0.9 | 1.05 | 0.0584 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | MANNING3 | 0.9637 | 0.896 | -0.0677 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | MANNING3 | 0.9792 | 0.896 | -0.0832 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | TRIB SW3 | 0.9796 | 0.896 | -0.0836 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | LIBERTY3 | 0.97 | 0.896 | -0.074 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | MANNING3 | 0.9637 | 0.896 | -0.0677 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | MANNING3 | 0.9792 | 0.896 | -0.0832 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | TRIB SW3 | 0.9796 | 0.896 | -0.0836 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | LIBERTY3 | 0.97 | 0.896 | -0.074 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | MANNING3 | 0.9637 | 0.896 | -0.0677 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | MANNING3 | 0.9792 | 0.896 | -0.0832 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | TRIB SW3 | 0.9796 | 0.896 | -0.0836 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | LIBERTY3 | 0.97 | 0.896 | -0.074 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | MANNING3 | 0.9637 | 0.896 | -0.0677 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | MANNING3 | 0.9792 | 0.896 | -0.0832 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | TRIB SW3 | 0.9796 | 0.896 | -0.0836 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | LIBERTY3 | 0.97 | 0.896 | -0.074 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | MANNING3 | 0.9637 | 0.896 | -0.0677 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | MANNING3 | 0.9792 | 0.896 | -0.0832 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | TRIB SW3 | 0.9796 | 0.896 | -0.0836 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | LIBERTY3 | 0.97 | 0.896 | -0.074 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | MANNING3 | 0.9637 | 0.896 | -0.0677 |  | 0.9 | 1.05 | 0.04781 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | MANNING3 | 0.9792 | 0.896 | -0.0832 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | TRIB SW3 | 0.9796 | 0.896 | -0.0836 |  | 0.9 | 1.05 | 0.04773 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | LIBERTY3 | 0.97 | 0.896 | -0.074 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | MANNING3 | 0.9637 | 0.896 | -0.0677 |  | 0.9 | 1.05 | 0.05112 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | MANNING3 | 0.9792 | 0.896 | -0.0832 |  | 0.9 | 1.05 | 0.05126 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | TRIB SW3 | 0.9796 | 0.896 | -0.0836 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | LIBERTY3 | 0.97 | 0.896 | -0.074 |  | 0.9 | 1.05 | 0.05126 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | MANNING3 | 0.9637 | 0.896 | -0.0677 |  | 0.9 | 1.05 | 0.03494 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | MANNING3 | 0.9792 | 0.896 | -0.0832 |  | 0.9 | 1.05 | 0.0351 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | TRIB SW3 | 0.9796 | 0.896 | -0.0836 |  | 0.9 | 1.05 | 0.0348 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | LIBERTY3 | 0.97 | 0.896 | -0.074 |  | 0.9 | 1.05 | 0.0351 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | MANNING3 | 0.9637 | 0.896 | -0.0677 |  | 0.9 | 1.05 | 0.04759 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | MANNING3 | 0.9792 | 0.896 | -0.0832 |  | 0.9 | 1.05 | 0.04774 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | TRIB SW3 | 0.9796 | 0.896 | -0.0836 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | LIBERTY3 | 0.97 | 0.896 | -0.074 |  | 0.9 | 1.05 | 0.04774 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | MANNING3 | 0.9637 | 0.896 | -0.0677 |  | 0.9 | 1.05 | 0.05002 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | MANNING3 | 0.9792 | 0.896 | -0.0832 |  | 0.9 | 1.05 | 0.05016 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | TRIB SW3 | 0.9796 | 0.896 | -0.0836 |  | 0.9 | 1.05 | 0.04996 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | LIBERTY3 | 0.97 | 0.896 | -0.074 |  | 0.9 | 1.05 | 0.05016 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | MANNING3 | 0.9637 | 0.896 | -0.0677 |  | 0.9 | 1.05 | 0.04842 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | MANNING3 | 0.9792 | 0.896 | -0.0832 |  | 0.9 | 1.05 | 0.04857 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | TRIB SW3 | 0.9796 | 0.896 | -0.0836 |  | 0.9 | 1.05 | 0.04835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | LIBERTY3 | 0.97 | 0.896 | -0.074 |  | 0.9 | 1.05 | 0.04857 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | MANNING3 | 0.9637 | 0.896 | -0.0677 |  | 0.9 | 1.05 | 0.05452 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | MANNING3 | 0.9792 | 0.896 | -0.0832 |  | 0.9 | 1.05 | 0.05466 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | TRIB SW3 | 0.9796 | 0.896 | -0.0836 |  | 0.9 | 1.05 | 0.05448 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | LIBERTY3 | 0.97 | 0.896 | -0.074 |  | 0.9 | 1.05 | 0.05466 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | MANNING3 | 0.9637 | 0.896 | -0.0677 |  | 0.9 | 1.05 | 0.05387 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | MANNING3 | 0.9792 | 0.896 | -0.0832 |  | 0.9 | 1.05 | 0.05401 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | TRIB SW3 | 0.9796 | 0.896 | -0.0836 |  | 0.9 | 1.05 | 0.05382 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | LIBERTY3 | 0.97 | 0.896 | -0.074 |  | 0.9 | 1.05 | 0.05401 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | MANNING3 | 0.9637 | 0.896 | -0.0677 |  | 0.9 | 1.05 | 0.03786 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | MANNING3 | 0.9792 | 0.896 | -0.0832 |  | 0.9 | 1.05 | 0.03802 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | TRIB SW3 | 0.9796 | 0.896 | -0.0836 |  | 0.9 | 1.05 | 0.03774 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | LIBERTY3 | 0.97 | 0.896 | -0.074 |  | 0.9 | 1.05 | 0.03802 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | MANNING3 | 0.9637 | 0.896 | -0.0677 |  | 0.9 | 1.05 | 0.04954 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | MANNING3 | 0.9792 | 0.896 | -0.0832 |  | 0.9 | 1.05 | 0.04968 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | TRIB SW3 | 0.9796 | 0.896 | -0.0836 |  | 0.9 | 1.05 | 0.04948 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | LIBERTY3 | 0.97 | 0.896 | -0.074 |  | 0.9 | 1.05 | 0.04968 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | MANNING3 | 0.9637 | 0.896 | -0.0677 |  | 0.9 | 1.05 | 0.04065 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | MANNING3 | 0.9792 | 0.896 | -0.0832 |  | 0.9 | 1.05 | 0.04081 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | TRIB SW3 | 0.9796 | 0.896 | -0.0836 |  | 0.9 | 1.05 | 0.04054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | LIBERTY3 | 0.97 | 0.896 | -0.074 |  | 0.9 | 1.05 | 0.04081 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | BVERVLLY | 0.9719 | 0.8962 | -0.0757 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | BVERVLLY | 0.9755 | 0.8962 | -0.0793 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | BVERVLLY | 0.9719 | 0.8962 | -0.0757 |  | 0.9 | 1.05 | 0.04915 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | BVERVLLY | 0.9755 | 0.8962 | -0.0793 |  | 0.9 | 1.05 | 0.04915 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | BVERVLLY | 0.9719 | 0.8962 | -0.0757 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | BVERVLLY | 0.9755 | 0.8962 | -0.0793 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | BVERVLLY | 0.9719 | 0.8962 | -0.0757 |  | 0.9 | 1.05 | 0.0427 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | BVERVLLY | 0.9755 | 0.8962 | -0.0793 |  | 0.9 | 1.05 | 0.0427 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | BVERVLLY | 0.9719 | 0.8962 | -0.0757 |  | 0.9 | 1.05 | 0.06281 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | BVERVLLY | 0.9755 | 0.8962 | -0.0793 |  | 0.9 | 1.05 | 0.06281 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | BVERVLLY | 0.9719 | 0.8962 | -0.0757 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | BVERVLLY | 0.9755 | 0.8962 | -0.0793 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | BVERVLLY | 0.9719 | 0.8962 | -0.0757 |  | 0.9 | 1.05 | 0.05054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | BVERVLLY | 0.9755 | 0.8962 | -0.0793 |  | 0.9 | 1.05 | 0.05054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | BVERVLLY | 0.9719 | 0.8962 | -0.0757 |  | 0.9 | 1.05 | 0.05303 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | BVERVLLY | 0.9755 | 0.8962 | -0.0793 |  | 0.9 | 1.05 | 0.05303 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | BVERVLLY | 0.9719 | 0.8962 | -0.0757 |  | 0.9 | 1.05 | 0.04451 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | BVERVLLY | 0.9755 | 0.8962 | -0.0793 |  | 0.9 | 1.05 | 0.04451 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | BVERVLLY | 0.9719 | 0.8962 | -0.0757 |  | 0.9 | 1.05 | 0.04798 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | BVERVLLY | 0.9755 | 0.8962 | -0.0793 |  | 0.9 | 1.05 | 0.04798 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | BVERVLLY | 0.9719 | 0.8962 | -0.0757 |  | 0.9 | 1.05 | 0.05835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | BVERVLLY | 0.9755 | 0.8962 | -0.0793 |  | 0.9 | 1.05 | 0.05835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | BVERVLLY | 0.9719 | 0.8962 | -0.0757 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | BVERVLLY | 0.9755 | 0.8962 | -0.0793 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | BVERVLLY | 0.9719 | 0.8962 | -0.0757 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | BVERVLLY | 0.9755 | 0.8962 | -0.0793 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | BVERVLLY | 0.9719 | 0.8962 | -0.0757 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | BVERVLLY | 0.9755 | 0.8962 | -0.0793 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | BVERVLLY | 0.9719 | 0.8962 | -0.0757 |  | 0.9 | 1.05 | 0.04739 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | BVERVLLY | 0.9755 | 0.8962 | -0.0793 |  | 0.9 | 1.05 | 0.04739 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | BVERVLLY | 0.9719 | 0.8962 | -0.0757 |  | 0.9 | 1.05 | 0.04778 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | BVERVLLY | 0.9755 | 0.8962 | -0.0793 |  | 0.9 | 1.05 | 0.04778 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | BVERVLLY | 0.9719 | 0.8962 | -0.0757 |  | 0.9 | 1.05 | 0.04783 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | BVERVLLY | 0.9755 | 0.8962 | -0.0793 |  | 0.9 | 1.05 | 0.04783 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | BVERVLLY | 0.9719 | 0.8962 | -0.0757 |  | 0.9 | 1.05 | 0.05118 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | BVERVLLY | 0.9755 | 0.8962 | -0.0793 |  | 0.9 | 1.05 | 0.05118 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | BVERVLLY | 0.9719 | 0.8962 | -0.0757 |  | 0.9 | 1.05 | 0.03488 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | BVERVLLY | 0.9755 | 0.8962 | -0.0793 |  | 0.9 | 1.05 | 0.03488 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | BVERVLLY | 0.9719 | 0.8962 | -0.0757 |  | 0.9 | 1.05 | 0.04762 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | BVERVLLY | 0.9755 | 0.8962 | -0.0793 |  | 0.9 | 1.05 | 0.04762 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | BVERVLLY | 0.9719 | 0.8962 | -0.0757 |  | 0.9 | 1.05 | 0.05006 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | BVERVLLY | 0.9755 | 0.8962 | -0.0793 |  | 0.9 | 1.05 | 0.05006 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | BVERVLLY | 0.9719 | 0.8962 | -0.0757 |  | 0.9 | 1.05 | 0.04845 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | BVERVLLY | 0.9755 | 0.8962 | -0.0793 |  | 0.9 | 1.05 | 0.04845 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | BVERVLLY | 0.9719 | 0.8962 | -0.0757 |  | 0.9 | 1.05 | 0.05459 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | BVERVLLY | 0.9755 | 0.8962 | -0.0793 |  | 0.9 | 1.05 | 0.05459 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | BVERVLLY | 0.9719 | 0.8962 | -0.0757 |  | 0.9 | 1.05 | 0.05393 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | BVERVLLY | 0.9755 | 0.8962 | -0.0793 |  | 0.9 | 1.05 | 0.05393 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | BVERVLLY | 0.9719 | 0.8962 | -0.0757 |  | 0.9 | 1.05 | 0.03782 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | BVERVLLY | 0.9755 | 0.8962 | -0.0793 |  | 0.9 | 1.05 | 0.03782 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | BVERVLLY | 0.9719 | 0.8962 | -0.0757 |  | 0.9 | 1.05 | 0.04958 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | BVERVLLY | 0.9755 | 0.8962 | -0.0793 |  | 0.9 | 1.05 | 0.04958 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | BVERVLLY | 0.9719 | 0.8962 | -0.0757 |  | 0.9 | 1.05 | 0.04062 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | BVERVLLY | 0.9755 | 0.8962 | -0.0793 |  | 0.9 | 1.05 | 0.04062 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | MCDONLD3 | 0.9709 | 0.8965 | -0.0744 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | MCDONLD3 | 0.9709 | 0.8965 | -0.0744 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | MCDONLD3 | 0.9709 | 0.8965 | -0.0744 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | MCDONLD3 | 0.9709 | 0.8965 | -0.0744 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | MCDONLD3 | 0.9709 | 0.8965 | -0.0744 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | MCDONLD3 | 0.9709 | 0.8965 | -0.0744 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | MCDONLD3 | 0.9709 | 0.8965 | -0.0744 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | MCDONLD3 | 0.9709 | 0.8965 | -0.0744 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | MCDONLD3 | 0.9709 | 0.8965 | -0.0744 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | MCDONLD3 | 0.9709 | 0.8965 | -0.0744 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | MCDONLD3 | 0.9709 | 0.8965 | -0.0744 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | MCDONLD3 | 0.9709 | 0.8965 | -0.0744 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | MCDONLD3 | 0.9709 | 0.8965 | -0.0744 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | MCDONLD3 | 0.9709 | 0.8965 | -0.0744 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | MCDONLD3 | 0.9709 | 0.8965 | -0.0744 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | MCDONLD3 | 0.9709 | 0.8965 | -0.0744 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | MCDONLD3 | 0.9709 | 0.8965 | -0.0744 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | MCDONLD3 | 0.9709 | 0.8965 | -0.0744 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | MCDONLD3 | 0.9709 | 0.8965 | -0.0744 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | MCDONLD3 | 0.9709 | 0.8965 | -0.0744 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | MCDONLD3 | 0.9709 | 0.8965 | -0.0744 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | MCDONLD3 | 0.9709 | 0.8965 | -0.0744 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | MCDONLD3 | 0.9709 | 0.8965 | -0.0744 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | MCDONLD3 | 0.9709 | 0.8965 | -0.0744 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | MCDONLD3 | 0.9709 | 0.8965 | -0.0744 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | MCDONLD3 | 0.9709 | 0.8965 | -0.0744 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | MCDONLD3 | 0.9709 | 0.8965 | -0.0744 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | BIRDCTY3 | 0.9856 | 0.897 | -0.0886 |  | 0.9 | 1.05 | 0.05095 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | BIRDCTY3 | 0.9856 | 0.897 | -0.0886 |  | 0.9 | 1.05 | 0.04905 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | BIRDCTY3 | 0.9856 | 0.897 | -0.0886 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | BIRDCTY3 | 0.9856 | 0.897 | -0.0886 |  | 0.9 | 1.05 | 0.04262 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | BIRDCTY3 | 0.9856 | 0.897 | -0.0886 |  | 0.9 | 1.05 | 0.0627 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | BIRDCTY3 | 0.9856 | 0.897 | -0.0886 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | BIRDCTY3 | 0.9856 | 0.897 | -0.0886 |  | 0.9 | 1.05 | 0.05043 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | BIRDCTY3 | 0.9856 | 0.897 | -0.0886 |  | 0.9 | 1.05 | 0.05292 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | BIRDCTY3 | 0.9856 | 0.897 | -0.0886 |  | 0.9 | 1.05 | 0.0444 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | BIRDCTY3 | 0.9856 | 0.897 | -0.0886 |  | 0.9 | 1.05 | 0.04788 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | BIRDCTY3 | 0.9856 | 0.897 | -0.0886 |  | 0.9 | 1.05 | 0.05824 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | BIRDCTY3 | 0.9856 | 0.897 | -0.0886 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | BIRDCTY3 | 0.9856 | 0.897 | -0.0886 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | BIRDCTY3 | 0.9856 | 0.897 | -0.0886 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | BIRDCTY3 | 0.9856 | 0.897 | -0.0886 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | BIRDCTY3 | 0.9856 | 0.897 | -0.0886 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | BIRDCTY3 | 0.9856 | 0.897 | -0.0886 |  | 0.9 | 1.05 | 0.04773 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | BIRDCTY3 | 0.9856 | 0.897 | -0.0886 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | BIRDCTY3 | 0.9856 | 0.897 | -0.0886 |  | 0.9 | 1.05 | 0.0348 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | BIRDCTY3 | 0.9856 | 0.897 | -0.0886 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | BIRDCTY3 | 0.9856 | 0.897 | -0.0886 |  | 0.9 | 1.05 | 0.04996 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | BIRDCTY3 | 0.9856 | 0.897 | -0.0886 |  | 0.9 | 1.05 | 0.04835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | BIRDCTY3 | 0.9856 | 0.897 | -0.0886 |  | 0.9 | 1.05 | 0.05448 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | BIRDCTY3 | 0.9856 | 0.897 | -0.0886 |  | 0.9 | 1.05 | 0.05382 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | BIRDCTY3 | 0.9856 | 0.897 | -0.0886 |  | 0.9 | 1.05 | 0.03774 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | BIRDCTY3 | 0.9856 | 0.897 | -0.0886 |  | 0.9 | 1.05 | 0.04948 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | BIRDCTY3 | 0.9856 | 0.897 | -0.0886 |  | 0.9 | 1.05 | 0.04054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | MANNGT 3 | 0.9648 | 0.8971 | -0.0677 |  | 0.9 | 1.05 | 0.05101 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | MANNGT 3 | 0.9803 | 0.8971 | -0.0832 |  | 0.9 | 1.05 | 0.05115 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | MANNGT 3 | 0.9648 | 0.8971 | -0.0677 |  | 0.9 | 1.05 | 0.04911 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | MANNGT 3 | 0.9803 | 0.8971 | -0.0832 |  | 0.9 | 1.05 | 0.04926 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | MANNGT 3 | 0.9648 | 0.8971 | -0.0677 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | MANNGT 3 | 0.9803 | 0.8971 | -0.0832 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | MANNGT 3 | 0.9648 | 0.8971 | -0.0677 |  | 0.9 | 1.05 | 0.04272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | MANNGT 3 | 0.9803 | 0.8971 | -0.0832 |  | 0.9 | 1.05 | 0.04287 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | MANNGT 3 | 0.9648 | 0.8971 | -0.0677 |  | 0.9 | 1.05 | 0.06272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | MANNGT 3 | 0.9803 | 0.8971 | -0.0832 |  | 0.9 | 1.05 | 0.06285 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | MANNGT 3 | 0.9648 | 0.8971 | -0.0677 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | MANNGT 3 | 0.9803 | 0.8971 | -0.0832 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | MANNGT 3 | 0.9648 | 0.8971 | -0.0677 |  | 0.9 | 1.05 | 0.05049 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | MANNGT 3 | 0.9803 | 0.8971 | -0.0832 |  | 0.9 | 1.05 | 0.05063 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | MANNGT 3 | 0.9648 | 0.8971 | -0.0677 |  | 0.9 | 1.05 | 0.05297 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | MANNGT 3 | 0.9803 | 0.8971 | -0.0832 |  | 0.9 | 1.05 | 0.05311 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | MANNGT 3 | 0.9648 | 0.8971 | -0.0677 |  | 0.9 | 1.05 | 0.04447 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | MANNGT 3 | 0.9803 | 0.8971 | -0.0832 |  | 0.9 | 1.05 | 0.04461 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | MANNGT 3 | 0.9648 | 0.8971 | -0.0677 |  | 0.9 | 1.05 | 0.04795 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | MANNGT 3 | 0.9803 | 0.8971 | -0.0832 |  | 0.9 | 1.05 | 0.0481 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | MANNGT 3 | 0.9648 | 0.8971 | -0.0677 |  | 0.9 | 1.05 | 0.05827 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | MANNGT 3 | 0.9803 | 0.8971 | -0.0832 |  | 0.9 | 1.05 | 0.0584 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | MANNGT 3 | 0.9648 | 0.8971 | -0.0677 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | MANNGT 3 | 0.9803 | 0.8971 | -0.0832 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | MANNGT 3 | 0.9648 | 0.8971 | -0.0677 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | MANNGT 3 | 0.9803 | 0.8971 | -0.0832 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | MANNGT 3 | 0.9648 | 0.8971 | -0.0677 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | MANNGT 3 | 0.9803 | 0.8971 | -0.0832 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | MANNGT 3 | 0.9648 | 0.8971 | -0.0677 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | MANNGT 3 | 0.9803 | 0.8971 | -0.0832 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | MANNGT 3 | 0.9648 | 0.8971 | -0.0677 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | MANNGT 3 | 0.9803 | 0.8971 | -0.0832 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | MANNGT 3 | 0.9648 | 0.8971 | -0.0677 |  | 0.9 | 1.05 | 0.04781 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | MANNGT 3 | 0.9803 | 0.8971 | -0.0832 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | MANNGT 3 | 0.9648 | 0.8971 | -0.0677 |  | 0.9 | 1.05 | 0.05112 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | MANNGT 3 | 0.9803 | 0.8971 | -0.0832 |  | 0.9 | 1.05 | 0.05126 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | MANNGT 3 | 0.9648 | 0.8971 | -0.0677 |  | 0.9 | 1.05 | 0.03494 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | MANNGT 3 | 0.9803 | 0.8971 | -0.0832 |  | 0.9 | 1.05 | 0.0351 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | MANNGT 3 | 0.9648 | 0.8971 | -0.0677 |  | 0.9 | 1.05 | 0.04759 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | MANNGT 3 | 0.9803 | 0.8971 | -0.0832 |  | 0.9 | 1.05 | 0.04774 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | MANNGT 3 | 0.9648 | 0.8971 | -0.0677 |  | 0.9 | 1.05 | 0.05002 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | MANNGT 3 | 0.9803 | 0.8971 | -0.0832 |  | 0.9 | 1.05 | 0.05016 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | MANNGT 3 | 0.9648 | 0.8971 | -0.0677 |  | 0.9 | 1.05 | 0.04842 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | MANNGT 3 | 0.9803 | 0.8971 | -0.0832 |  | 0.9 | 1.05 | 0.04857 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | MANNGT 3 | 0.9648 | 0.8971 | -0.0677 |  | 0.9 | 1.05 | 0.05452 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | MANNGT 3 | 0.9803 | 0.8971 | -0.0832 |  | 0.9 | 1.05 | 0.05466 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | MANNGT 3 | 0.9648 | 0.8971 | -0.0677 |  | 0.9 | 1.05 | 0.05387 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | MANNGT 3 | 0.9803 | 0.8971 | -0.0832 |  | 0.9 | 1.05 | 0.05401 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | MANNGT 3 | 0.9648 | 0.8971 | -0.0677 |  | 0.9 | 1.05 | 0.03786 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | MANNGT 3 | 0.9803 | 0.8971 | -0.0832 |  | 0.9 | 1.05 | 0.03802 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | MANNGT 3 | 0.9648 | 0.8971 | -0.0677 |  | 0.9 | 1.05 | 0.04954 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | MANNGT 3 | 0.9803 | 0.8971 | -0.0832 |  | 0.9 | 1.05 | 0.04968 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | MANNGT 3 | 0.9648 | 0.8971 | -0.0677 |  | 0.9 | 1.05 | 0.04065 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | MANNGT 3 | 0.9803 | 0.8971 | -0.0832 |  | 0.9 | 1.05 | 0.04081 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | DIGHTON3 | 0.9618 | 0.8973 | -0.0645 |  | 0.9 | 1.05 | 0.05101 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | DIGHTON3 | 0.9618 | 0.8973 | -0.0645 |  | 0.9 | 1.05 | 0.04911 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | DIGHTON3 | 0.9618 | 0.8973 | -0.0645 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | DIGHTON3 | 0.9618 | 0.8973 | -0.0645 |  | 0.9 | 1.05 | 0.04272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | DIGHTON3 | 0.9618 | 0.8973 | -0.0645 |  | 0.9 | 1.05 | 0.06272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | DIGHTON3 | 0.9618 | 0.8973 | -0.0645 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | DIGHTON3 | 0.9618 | 0.8973 | -0.0645 |  | 0.9 | 1.05 | 0.05049 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | DIGHTON3 | 0.9618 | 0.8973 | -0.0645 |  | 0.9 | 1.05 | 0.05297 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | DIGHTON3 | 0.9618 | 0.8973 | -0.0645 |  | 0.9 | 1.05 | 0.04447 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | DIGHTON3 | 0.9618 | 0.8973 | -0.0645 |  | 0.9 | 1.05 | 0.04795 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | DIGHTON3 | 0.9618 | 0.8973 | -0.0645 |  | 0.9 | 1.05 | 0.05827 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | DIGHTON3 | 0.9618 | 0.8973 | -0.0645 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | DIGHTON3 | 0.9618 | 0.8973 | -0.0645 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | DIGHTON3 | 0.9618 | 0.8973 | -0.0645 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | DIGHTON3 | 0.9618 | 0.8973 | -0.0645 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | DIGHTON3 | 0.9618 | 0.8973 | -0.0645 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | DIGHTON3 | 0.9618 | 0.8973 | -0.0645 |  | 0.9 | 1.05 | 0.04781 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | DIGHTON3 | 0.9618 | 0.8973 | -0.0645 |  | 0.9 | 1.05 | 0.05112 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | DIGHTON3 | 0.9618 | 0.8973 | -0.0645 |  | 0.9 | 1.05 | 0.03494 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | DIGHTON3 | 0.9618 | 0.8973 | -0.0645 |  | 0.9 | 1.05 | 0.04759 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | DIGHTON3 | 0.9618 | 0.8973 | -0.0645 |  | 0.9 | 1.05 | 0.05002 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | DIGHTON3 | 0.9618 | 0.8973 | -0.0645 |  | 0.9 | 1.05 | 0.04842 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | DIGHTON3 | 0.9618 | 0.8973 | -0.0645 |  | 0.9 | 1.05 | 0.05452 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | DIGHTON3 | 0.9618 | 0.8973 | -0.0645 |  | 0.9 | 1.05 | 0.05387 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | DIGHTON3 | 0.9618 | 0.8973 | -0.0645 |  | 0.9 | 1.05 | 0.03786 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | DIGHTON3 | 0.9618 | 0.8973 | -0.0645 |  | 0.9 | 1.05 | 0.04954 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | DIGHTON3 | 0.9618 | 0.8973 | -0.0645 |  | 0.9 | 1.05 | 0.04065 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | TRIBUNE3 | 0.9797 | 0.8974 | -0.0823 |  | 0.9 | 1.05 | 0.05095 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | TRIBUNE3 | 0.9797 | 0.8974 | -0.0823 |  | 0.9 | 1.05 | 0.04905 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | TRIBUNE3 | 0.9797 | 0.8974 | -0.0823 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | TRIBUNE3 | 0.9797 | 0.8974 | -0.0823 |  | 0.9 | 1.05 | 0.04262 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | TRIBUNE3 | 0.9797 | 0.8974 | -0.0823 |  | 0.9 | 1.05 | 0.0627 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | TRIBUNE3 | 0.9797 | 0.8974 | -0.0823 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | TRIBUNE3 | 0.9797 | 0.8974 | -0.0823 |  | 0.9 | 1.05 | 0.05043 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | TRIBUNE3 | 0.9797 | 0.8974 | -0.0823 |  | 0.9 | 1.05 | 0.05292 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | TRIBUNE3 | 0.9797 | 0.8974 | -0.0823 |  | 0.9 | 1.05 | 0.0444 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | TRIBUNE3 | 0.9797 | 0.8974 | -0.0823 |  | 0.9 | 1.05 | 0.04788 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | TRIBUNE3 | 0.9797 | 0.8974 | -0.0823 |  | 0.9 | 1.05 | 0.05824 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | TRIBUNE3 | 0.9797 | 0.8974 | -0.0823 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | TRIBUNE3 | 0.9797 | 0.8974 | -0.0823 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | TRIBUNE3 | 0.9797 | 0.8974 | -0.0823 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | TRIBUNE3 | 0.9797 | 0.8974 | -0.0823 |  | 0.9 | 1.05 | 0.0473 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | TRIBUNE3 | 0.9797 | 0.8974 | -0.0823 |  | 0.9 | 1.05 | 0.04769 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | TRIBUNE3 | 0.9797 | 0.8974 | -0.0823 |  | 0.9 | 1.05 | 0.04773 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | TRIBUNE3 | 0.9797 | 0.8974 | -0.0823 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | TRIBUNE3 | 0.9797 | 0.8974 | -0.0823 |  | 0.9 | 1.05 | 0.0348 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | TRIBUNE3 | 0.9797 | 0.8974 | -0.0823 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | TRIBUNE3 | 0.9797 | 0.8974 | -0.0823 |  | 0.9 | 1.05 | 0.04996 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | TRIBUNE3 | 0.9797 | 0.8974 | -0.0823 |  | 0.9 | 1.05 | 0.04835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | TRIBUNE3 | 0.9797 | 0.8974 | -0.0823 |  | 0.9 | 1.05 | 0.05448 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | TRIBUNE3 | 0.9797 | 0.8974 | -0.0823 |  | 0.9 | 1.05 | 0.05382 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | TRIBUNE3 | 0.9797 | 0.8974 | -0.0823 |  | 0.9 | 1.05 | 0.03774 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | TRIBUNE3 | 0.9797 | 0.8974 | -0.0823 |  | 0.9 | 1.05 | 0.04948 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | TRIBUNE3 | 0.9797 | 0.8974 | -0.0823 |  | 0.9 | 1.05 | 0.04054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | SELKIRK3 | 0.9701 | 0.8976 | -0.0725 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | SELKIRK3 | 0.9701 | 0.8976 | -0.0725 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | SELKIRK3 | 0.9701 | 0.8976 | -0.0725 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | SELKIRK3 | 0.9701 | 0.8976 | -0.0725 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | SELKIRK3 | 0.9701 | 0.8976 | -0.0725 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | SELKIRK3 | 0.9701 | 0.8976 | -0.0725 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | SELKIRK3 | 0.9701 | 0.8976 | -0.0725 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | SELKIRK3 | 0.9701 | 0.8976 | -0.0725 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | SELKIRK3 | 0.9701 | 0.8976 | -0.0725 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | SELKIRK3 | 0.9701 | 0.8976 | -0.0725 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | SELKIRK3 | 0.9701 | 0.8976 | -0.0725 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | SELKIRK3 | 0.9701 | 0.8976 | -0.0725 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | SELKIRK3 | 0.9701 | 0.8976 | -0.0725 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | SELKIRK3 | 0.9701 | 0.8976 | -0.0725 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | SELKIRK3 | 0.9701 | 0.8976 | -0.0725 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | SELKIRK3 | 0.9701 | 0.8976 | -0.0725 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | SELKIRK3 | 0.9701 | 0.8976 | -0.0725 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | SELKIRK3 | 0.9701 | 0.8976 | -0.0725 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | SELKIRK3 | 0.9701 | 0.8976 | -0.0725 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | SELKIRK3 | 0.9701 | 0.8976 | -0.0725 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | SELKIRK3 | 0.9701 | 0.8976 | -0.0725 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | SELKIRK3 | 0.9701 | 0.8976 | -0.0725 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | SELKIRK3 | 0.9701 | 0.8976 | -0.0725 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | SELKIRK3 | 0.9701 | 0.8976 | -0.0725 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | SELKIRK3 | 0.9701 | 0.8976 | -0.0725 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | SELKIRK3 | 0.9701 | 0.8976 | -0.0725 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | SELKIRK3 | 0.9701 | 0.8976 | -0.0725 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | GRANT 3 | 1.0098 | 0.8979 | -0.1119 |  | 0.9 | 1.05 | 0.10414 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | DIGHTON3 | 0.9767 | 0.8979 | -0.0788 |  | 0.9 | 1.05 | 0.05115 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | GRANT 3 | 1.0098 | 0.8979 | -0.1119 |  | 0.9 | 1.05 | 0.0987 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | DIGHTON3 | 0.9767 | 0.8979 | -0.0788 |  | 0.9 | 1.05 | 0.04926 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | GRANT 3 | 1.0098 | 0.8979 | -0.1119 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | DIGHTON3 | 0.9767 | 0.8979 | -0.0788 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | GRANT 3 | 1.0098 | 0.8979 | -0.1119 |  | 0.9 | 1.05 | 0.08024 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | DIGHTON3 | 0.9767 | 0.8979 | -0.0788 |  | 0.9 | 1.05 | 0.04287 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | GRANT 3 | 1.0098 | 0.8979 | -0.1119 |  | 0.9 | 1.05 | 0.14298 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | DIGHTON3 | 0.9767 | 0.8979 | -0.0788 |  | 0.9 | 1.05 | 0.06285 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | GRANT 3 | 1.0098 | 0.8979 | -0.1119 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | DIGHTON3 | 0.9767 | 0.8979 | -0.0788 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | GRANT 3 | 1.0098 | 0.8979 | -0.1119 |  | 0.9 | 1.05 | 0.10266 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | DIGHTON3 | 0.9767 | 0.8979 | -0.0788 |  | 0.9 | 1.05 | 0.05063 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | GRANT 3 | 1.0098 | 0.8979 | -0.1119 |  | 0.9 | 1.05 | 0.11064 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | DIGHTON3 | 0.9767 | 0.8979 | -0.0788 |  | 0.9 | 1.05 | 0.05311 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | GRANT 3 | 1.0098 | 0.8979 | -0.1119 |  | 0.9 | 1.05 | 0.08095 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | DIGHTON3 | 0.9767 | 0.8979 | -0.0788 |  | 0.9 | 1.05 | 0.04461 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | GRANT 3 | 1.0098 | 0.8979 | -0.1119 |  | 0.9 | 1.05 | 0.09571 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | DIGHTON3 | 0.9767 | 0.8979 | -0.0788 |  | 0.9 | 1.05 | 0.0481 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | GRANT 3 | 1.0098 | 0.8979 | -0.1119 |  | 0.9 | 1.05 | 0.12796 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | DIGHTON3 | 0.9767 | 0.8979 | -0.0788 |  | 0.9 | 1.05 | 0.0584 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | GRANT 3 | 1.0098 | 0.8979 | -0.1119 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | DIGHTON3 | 0.9767 | 0.8979 | -0.0788 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | GRANT 3 | 1.0098 | 0.8979 | -0.1119 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | DIGHTON3 | 0.9767 | 0.8979 | -0.0788 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | GRANT 3 | 1.0098 | 0.8979 | -0.1119 |  | 0.9 | 1.05 | 0.09379 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | DIGHTON3 | 0.9767 | 0.8979 | -0.0788 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | GRANT 3 | 1.0098 | 0.8979 | -0.1119 |  | 0.9 | 1.05 | 0.09379 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | DIGHTON3 | 0.9767 | 0.8979 | -0.0788 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | GRANT 3 | 1.0098 | 0.8979 | -0.1119 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | DIGHTON3 | 0.9767 | 0.8979 | -0.0788 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | GRANT 3 | 1.0098 | 0.8979 | -0.1119 |  | 0.9 | 1.05 | 0.09507 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | DIGHTON3 | 0.9767 | 0.8979 | -0.0788 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | GRANT 3 | 1.0098 | 0.8979 | -0.1119 |  | 0.9 | 1.05 | 0.10446 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | DIGHTON3 | 0.9767 | 0.8979 | -0.0788 |  | 0.9 | 1.05 | 0.05126 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | GRANT 3 | 1.0098 | 0.8979 | -0.1119 |  | 0.9 | 1.05 | 0.05698 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | DIGHTON3 | 0.9767 | 0.8979 | -0.0788 |  | 0.9 | 1.05 | 0.0351 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | GRANT 3 | 1.0098 | 0.8979 | -0.1119 |  | 0.9 | 1.05 | 0.09445 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | DIGHTON3 | 0.9767 | 0.8979 | -0.0788 |  | 0.9 | 1.05 | 0.04774 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | GRANT 3 | 1.0098 | 0.8979 | -0.1119 |  | 0.9 | 1.05 | 0.10129 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | DIGHTON3 | 0.9767 | 0.8979 | -0.0788 |  | 0.9 | 1.05 | 0.05016 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | GRANT 3 | 1.0098 | 0.8979 | -0.1119 |  | 0.9 | 1.05 | 0.0967 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | DIGHTON3 | 0.9767 | 0.8979 | -0.0788 |  | 0.9 | 1.05 | 0.04857 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | GRANT 3 | 1.0098 | 0.8979 | -0.1119 |  | 0.9 | 1.05 | 0.11534 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | DIGHTON3 | 0.9767 | 0.8979 | -0.0788 |  | 0.9 | 1.05 | 0.05466 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | GRANT 3 | 1.0098 | 0.8979 | -0.1119 |  | 0.9 | 1.05 | 0.11336 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | DIGHTON3 | 0.9767 | 0.8979 | -0.0788 |  | 0.9 | 1.05 | 0.05401 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | GRANT 3 | 1.0098 | 0.8979 | -0.1119 |  | 0.9 | 1.05 | 0.06542 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | DIGHTON3 | 0.9767 | 0.8979 | -0.0788 |  | 0.9 | 1.05 | 0.03802 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | GRANT 3 | 1.0098 | 0.8979 | -0.1119 |  | 0.9 | 1.05 | 0.09991 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | DIGHTON3 | 0.9767 | 0.8979 | -0.0788 |  | 0.9 | 1.05 | 0.04968 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | GRANT 3 | 1.0098 | 0.8979 | -0.1119 |  | 0.9 | 1.05 | 0.0742 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | DIGHTON3 | 0.9767 | 0.8979 | -0.0788 |  | 0.9 | 1.05 | 0.04081 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | JAGGER 3 | 0.9624 | 0.898 | -0.0644 |  | 0.9 | 1.05 | 0.05101 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | GOVE 3 | 0.9933 | 0.898 | -0.0953 |  | 0.9 | 1.05 | 0.05095 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | GOVE 3 | 0.9972 | 0.898 | -0.0992 |  | 0.9 | 1.05 | 0.05095 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | SCOTCTY3 | 0.9841 | 0.898 | -0.0861 |  | 0.9 | 1.05 | 0.05115 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | JAGGER 3 | 0.9624 | 0.898 | -0.0644 |  | 0.9 | 1.05 | 0.04911 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | GOVE 3 | 0.9933 | 0.898 | -0.0953 |  | 0.9 | 1.05 | 0.04905 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | GOVE 3 | 0.9972 | 0.898 | -0.0992 |  | 0.9 | 1.05 | 0.04905 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | SCOTCTY3 | 0.9841 | 0.898 | -0.0861 |  | 0.9 | 1.05 | 0.04926 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | JAGGER 3 | 0.9624 | 0.898 | -0.0644 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | GOVE 3 | 0.9933 | 0.898 | -0.0953 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | GOVE 3 | 0.9972 | 0.898 | -0.0992 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | SCOTCTY3 | 0.9841 | 0.898 | -0.0861 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | JAGGER 3 | 0.9624 | 0.898 | -0.0644 |  | 0.9 | 1.05 | 0.04272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | GOVE 3 | 0.9933 | 0.898 | -0.0953 |  | 0.9 | 1.05 | 0.04262 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | GOVE 3 | 0.9972 | 0.898 | -0.0992 |  | 0.9 | 1.05 | 0.04262 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | SCOTCTY3 | 0.9841 | 0.898 | -0.0861 |  | 0.9 | 1.05 | 0.04287 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | JAGGER 3 | 0.9624 | 0.898 | -0.0644 |  | 0.9 | 1.05 | 0.06272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | GOVE 3 | 0.9933 | 0.898 | -0.0953 |  | 0.9 | 1.05 | 0.0627 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | GOVE 3 | 0.9972 | 0.898 | -0.0992 |  | 0.9 | 1.05 | 0.0627 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | SCOTCTY3 | 0.9841 | 0.898 | -0.0861 |  | 0.9 | 1.05 | 0.06285 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | JAGGER 3 | 0.9624 | 0.898 | -0.0644 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | GOVE 3 | 0.9933 | 0.898 | -0.0953 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | GOVE 3 | 0.9972 | 0.898 | -0.0992 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | SCOTCTY3 | 0.9841 | 0.898 | -0.0861 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | JAGGER 3 | 0.9624 | 0.898 | -0.0644 |  | 0.9 | 1.05 | 0.05049 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | GOVE 3 | 0.9933 | 0.898 | -0.0953 |  | 0.9 | 1.05 | 0.05043 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | GOVE 3 | 0.9972 | 0.898 | -0.0992 |  | 0.9 | 1.05 | 0.05043 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | SCOTCTY3 | 0.9841 | 0.898 | -0.0861 |  | 0.9 | 1.05 | 0.05063 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | JAGGER 3 | 0.9624 | 0.898 | -0.0644 |  | 0.9 | 1.05 | 0.05297 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | GOVE 3 | 0.9933 | 0.898 | -0.0953 |  | 0.9 | 1.05 | 0.05292 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | GOVE 3 | 0.9972 | 0.898 | -0.0992 |  | 0.9 | 1.05 | 0.05292 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | SCOTCTY3 | 0.9841 | 0.898 | -0.0861 |  | 0.9 | 1.05 | 0.05311 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | JAGGER 3 | 0.9624 | 0.898 | -0.0644 |  | 0.9 | 1.05 | 0.04447 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | GOVE 3 | 0.9933 | 0.898 | -0.0953 |  | 0.9 | 1.05 | 0.0444 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | GOVE 3 | 0.9972 | 0.898 | -0.0992 |  | 0.9 | 1.05 | 0.0444 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | SCOTCTY3 | 0.9841 | 0.898 | -0.0861 |  | 0.9 | 1.05 | 0.04461 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | JAGGER 3 | 0.9624 | 0.898 | -0.0644 |  | 0.9 | 1.05 | 0.04795 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | GOVE 3 | 0.9933 | 0.898 | -0.0953 |  | 0.9 | 1.05 | 0.04788 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | GOVE 3 | 0.9972 | 0.898 | -0.0992 |  | 0.9 | 1.05 | 0.04788 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | SCOTCTY3 | 0.9841 | 0.898 | -0.0861 |  | 0.9 | 1.05 | 0.0481 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | JAGGER 3 | 0.9624 | 0.898 | -0.0644 |  | 0.9 | 1.05 | 0.05827 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | GOVE 3 | 0.9933 | 0.898 | -0.0953 |  | 0.9 | 1.05 | 0.05824 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | GOVE 3 | 0.9972 | 0.898 | -0.0992 |  | 0.9 | 1.05 | 0.05824 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | SCOTCTY3 | 0.9841 | 0.898 | -0.0861 |  | 0.9 | 1.05 | 0.0584 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | JAGGER 3 | 0.9624 | 0.898 | -0.0644 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | GOVE 3 | 0.9933 | 0.898 | -0.0953 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | GOVE 3 | 0.9972 | 0.898 | -0.0992 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | SCOTCTY3 | 0.9841 | 0.898 | -0.0861 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | JAGGER 3 | 0.9624 | 0.898 | -0.0644 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | GOVE 3 | 0.9933 | 0.898 | -0.0953 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | GOVE 3 | 0.9972 | 0.898 | -0.0992 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | SCOTCTY3 | 0.9841 | 0.898 | -0.0861 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | JAGGER 3 | 0.9624 | 0.898 | -0.0644 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | GOVE 3 | 0.9933 | 0.898 | -0.0953 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | GOVE 3 | 0.9972 | 0.898 | -0.0992 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | SCOTCTY3 | 0.9841 | 0.898 | -0.0861 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | JAGGER 3 | 0.9624 | 0.898 | -0.0644 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | GOVE 3 | 0.9933 | 0.898 | -0.0953 |  | 0.9 | 1.05 | 0.0473 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | GOVE 3 | 0.9972 | 0.898 | -0.0992 |  | 0.9 | 1.05 | 0.0473 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | SCOTCTY3 | 0.9841 | 0.898 | -0.0861 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | JAGGER 3 | 0.9624 | 0.898 | -0.0644 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | GOVE 3 | 0.9933 | 0.898 | -0.0953 |  | 0.9 | 1.05 | 0.04769 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | GOVE 3 | 0.9972 | 0.898 | -0.0992 |  | 0.9 | 1.05 | 0.04769 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | SCOTCTY3 | 0.9841 | 0.898 | -0.0861 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | JAGGER 3 | 0.9624 | 0.898 | -0.0644 |  | 0.9 | 1.05 | 0.04781 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | GOVE 3 | 0.9933 | 0.898 | -0.0953 |  | 0.9 | 1.05 | 0.04773 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | GOVE 3 | 0.9972 | 0.898 | -0.0992 |  | 0.9 | 1.05 | 0.04773 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | SCOTCTY3 | 0.9841 | 0.898 | -0.0861 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | JAGGER 3 | 0.9624 | 0.898 | -0.0644 |  | 0.9 | 1.05 | 0.05112 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | GOVE 3 | 0.9933 | 0.898 | -0.0953 |  | 0.9 | 1.05 | 0.05106 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | GOVE 3 | 0.9972 | 0.898 | -0.0992 |  | 0.9 | 1.05 | 0.05106 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | SCOTCTY3 | 0.9841 | 0.898 | -0.0861 |  | 0.9 | 1.05 | 0.05126 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | JAGGER 3 | 0.9624 | 0.898 | -0.0644 |  | 0.9 | 1.05 | 0.03494 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | GOVE 3 | 0.9933 | 0.898 | -0.0953 |  | 0.9 | 1.05 | 0.0348 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | GOVE 3 | 0.9972 | 0.898 | -0.0992 |  | 0.9 | 1.05 | 0.0348 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | SCOTCTY3 | 0.9841 | 0.898 | -0.0861 |  | 0.9 | 1.05 | 0.0351 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | JAGGER 3 | 0.9624 | 0.898 | -0.0644 |  | 0.9 | 1.05 | 0.04759 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | GOVE 3 | 0.9933 | 0.898 | -0.0953 |  | 0.9 | 1.05 | 0.04752 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | GOVE 3 | 0.9972 | 0.898 | -0.0992 |  | 0.9 | 1.05 | 0.04752 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | SCOTCTY3 | 0.9841 | 0.898 | -0.0861 |  | 0.9 | 1.05 | 0.04774 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | JAGGER 3 | 0.9624 | 0.898 | -0.0644 |  | 0.9 | 1.05 | 0.05002 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | GOVE 3 | 0.9933 | 0.898 | -0.0953 |  | 0.9 | 1.05 | 0.04996 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | GOVE 3 | 0.9972 | 0.898 | -0.0992 |  | 0.9 | 1.05 | 0.04996 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | SCOTCTY3 | 0.9841 | 0.898 | -0.0861 |  | 0.9 | 1.05 | 0.05016 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | JAGGER 3 | 0.9624 | 0.898 | -0.0644 |  | 0.9 | 1.05 | 0.04842 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | GOVE 3 | 0.9933 | 0.898 | -0.0953 |  | 0.9 | 1.05 | 0.04835 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | GOVE 3 | 0.9972 | 0.898 | -0.0992 |  | 0.9 | 1.05 | 0.04835 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | SCOTCTY3 | 0.9841 | 0.898 | -0.0861 |  | 0.9 | 1.05 | 0.04857 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | JAGGER 3 | 0.9624 | 0.898 | -0.0644 |  | 0.9 | 1.05 | 0.05452 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | GOVE 3 | 0.9933 | 0.898 | -0.0953 |  | 0.9 | 1.05 | 0.05448 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | GOVE 3 | 0.9972 | 0.898 | -0.0992 |  | 0.9 | 1.05 | 0.05448 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | SCOTCTY3 | 0.9841 | 0.898 | -0.0861 |  | 0.9 | 1.05 | 0.05466 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | JAGGER 3 | 0.9624 | 0.898 | -0.0644 |  | 0.9 | 1.05 | 0.05387 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | GOVE 3 | 0.9933 | 0.898 | -0.0953 |  | 0.9 | 1.05 | 0.05382 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | GOVE 3 | 0.9972 | 0.898 | -0.0992 |  | 0.9 | 1.05 | 0.05382 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | SCOTCTY3 | 0.9841 | 0.898 | -0.0861 |  | 0.9 | 1.05 | 0.05401 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | JAGGER 3 | 0.9624 | 0.898 | -0.0644 |  | 0.9 | 1.05 | 0.03786 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | GOVE 3 | 0.9933 | 0.898 | -0.0953 |  | 0.9 | 1.05 | 0.03774 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | GOVE 3 | 0.9972 | 0.898 | -0.0992 |  | 0.9 | 1.05 | 0.03774 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | SCOTCTY3 | 0.9841 | 0.898 | -0.0861 |  | 0.9 | 1.05 | 0.03802 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | JAGGER 3 | 0.9624 | 0.898 | -0.0644 |  | 0.9 | 1.05 | 0.04954 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | GOVE 3 | 0.9933 | 0.898 | -0.0953 |  | 0.9 | 1.05 | 0.04948 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | GOVE 3 | 0.9972 | 0.898 | -0.0992 |  | 0.9 | 1.05 | 0.04948 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | SCOTCTY3 | 0.9841 | 0.898 | -0.0861 |  | 0.9 | 1.05 | 0.04968 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | JAGGER 3 | 0.9624 | 0.898 | -0.0644 |  | 0.9 | 1.05 | 0.04065 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | GOVE 3 | 0.9933 | 0.898 | -0.0953 |  | 0.9 | 1.05 | 0.04054 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | GOVE 3 | 0.9972 | 0.898 | -0.0992 |  | 0.9 | 1.05 | 0.04054 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | SCOTCTY3 | 0.9841 | 0.898 | -0.0861 |  | 0.9 | 1.05 | 0.04081 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | CSTFRAN3 | 0.9621 | 0.8981 | -0.064 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | CSTFRAN3 | 0.9621 | 0.8981 | -0.064 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | CSTFRAN3 | 0.9621 | 0.8981 | -0.064 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | CSTFRAN3 | 0.9621 | 0.8981 | -0.064 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | CSTFRAN3 | 0.9621 | 0.8981 | -0.064 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | CSTFRAN3 | 0.9621 | 0.8981 | -0.064 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | CSTFRAN3 | 0.9621 | 0.8981 | -0.064 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | CSTFRAN3 | 0.9621 | 0.8981 | -0.064 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | CSTFRAN3 | 0.9621 | 0.8981 | -0.064 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | CSTFRAN3 | 0.9621 | 0.8981 | -0.064 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | CSTFRAN3 | 0.9621 | 0.8981 | -0.064 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | CSTFRAN3 | 0.9621 | 0.8981 | -0.064 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | CSTFRAN3 | 0.9621 | 0.8981 | -0.064 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | CSTFRAN3 | 0.9621 | 0.8981 | -0.064 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | CSTFRAN3 | 0.9621 | 0.8981 | -0.064 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | CSTFRAN3 | 0.9621 | 0.8981 | -0.064 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | CSTFRAN3 | 0.9621 | 0.8981 | -0.064 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | CSTFRAN3 | 0.9621 | 0.8981 | -0.064 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | CSTFRAN3 | 0.9621 | 0.8981 | -0.064 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | CSTFRAN3 | 0.9621 | 0.8981 | -0.064 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | CSTFRAN3 | 0.9621 | 0.8981 | -0.064 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | CSTFRAN3 | 0.9621 | 0.8981 | -0.064 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | CSTFRAN3 | 0.9621 | 0.8981 | -0.064 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | CSTFRAN3 | 0.9621 | 0.8981 | -0.064 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | CSTFRAN3 | 0.9621 | 0.8981 | -0.064 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | CSTFRAN3 | 0.9621 | 0.8981 | -0.064 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | CSTFRAN3 | 0.9621 | 0.8981 | -0.064 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | STFRANT3 | 0.9622 | 0.8982 | -0.064 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | GRANTTP3 | 1.01 | 0.8982 | -0.1118 |  | 0.9 | 1.05 | 0.10414 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | STFRANT3 | 0.9622 | 0.8982 | -0.064 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | GRANTTP3 | 1.01 | 0.8982 | -0.1118 |  | 0.9 | 1.05 | 0.0987 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | STFRANT3 | 0.9622 | 0.8982 | -0.064 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | GRANTTP3 | 1.01 | 0.8982 | -0.1118 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | STFRANT3 | 0.9622 | 0.8982 | -0.064 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | GRANTTP3 | 1.01 | 0.8982 | -0.1118 |  | 0.9 | 1.05 | 0.08024 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | STFRANT3 | 0.9622 | 0.8982 | -0.064 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | GRANTTP3 | 1.01 | 0.8982 | -0.1118 |  | 0.9 | 1.05 | 0.14298 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | STFRANT3 | 0.9622 | 0.8982 | -0.064 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | GRANTTP3 | 1.01 | 0.8982 | -0.1118 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | STFRANT3 | 0.9622 | 0.8982 | -0.064 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | GRANTTP3 | 1.01 | 0.8982 | -0.1118 |  | 0.9 | 1.05 | 0.10266 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | STFRANT3 | 0.9622 | 0.8982 | -0.064 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | GRANTTP3 | 1.01 | 0.8982 | -0.1118 |  | 0.9 | 1.05 | 0.11064 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | STFRANT3 | 0.9622 | 0.8982 | -0.064 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | GRANTTP3 | 1.01 | 0.8982 | -0.1118 |  | 0.9 | 1.05 | 0.08095 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | STFRANT3 | 0.9622 | 0.8982 | -0.064 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | GRANTTP3 | 1.01 | 0.8982 | -0.1118 |  | 0.9 | 1.05 | 0.09571 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | STFRANT3 | 0.9622 | 0.8982 | -0.064 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | GRANTTP3 | 1.01 | 0.8982 | -0.1118 |  | 0.9 | 1.05 | 0.12796 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | STFRANT3 | 0.9622 | 0.8982 | -0.064 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | GRANTTP3 | 1.01 | 0.8982 | -0.1118 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | STFRANT3 | 0.9622 | 0.8982 | -0.064 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | GRANTTP3 | 1.01 | 0.8982 | -0.1118 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | STFRANT3 | 0.9622 | 0.8982 | -0.064 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | GRANTTP3 | 1.01 | 0.8982 | -0.1118 |  | 0.9 | 1.05 | 0.09379 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | STFRANT3 | 0.9622 | 0.8982 | -0.064 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | GRANTTP3 | 1.01 | 0.8982 | -0.1118 |  | 0.9 | 1.05 | 0.09379 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | STFRANT3 | 0.9622 | 0.8982 | -0.064 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | GRANTTP3 | 1.01 | 0.8982 | -0.1118 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | STFRANT3 | 0.9622 | 0.8982 | -0.064 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | GRANTTP3 | 1.01 | 0.8982 | -0.1118 |  | 0.9 | 1.05 | 0.09507 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | STFRANT3 | 0.9622 | 0.8982 | -0.064 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | GRANTTP3 | 1.01 | 0.8982 | -0.1118 |  | 0.9 | 1.05 | 0.10446 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | STFRANT3 | 0.9622 | 0.8982 | -0.064 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | GRANTTP3 | 1.01 | 0.8982 | -0.1118 |  | 0.9 | 1.05 | 0.05698 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | STFRANT3 | 0.9622 | 0.8982 | -0.064 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | GRANTTP3 | 1.01 | 0.8982 | -0.1118 |  | 0.9 | 1.05 | 0.09445 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | STFRANT3 | 0.9622 | 0.8982 | -0.064 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | GRANTTP3 | 1.01 | 0.8982 | -0.1118 |  | 0.9 | 1.05 | 0.10129 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | STFRANT3 | 0.9622 | 0.8982 | -0.064 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | GRANTTP3 | 1.01 | 0.8982 | -0.1118 |  | 0.9 | 1.05 | 0.0967 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | STFRANT3 | 0.9622 | 0.8982 | -0.064 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | GRANTTP3 | 1.01 | 0.8982 | -0.1118 |  | 0.9 | 1.05 | 0.11534 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | STFRANT3 | 0.9622 | 0.8982 | -0.064 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | GRANTTP3 | 1.01 | 0.8982 | -0.1118 |  | 0.9 | 1.05 | 0.11336 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | STFRANT3 | 0.9622 | 0.8982 | -0.064 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | GRANTTP3 | 1.01 | 0.8982 | -0.1118 |  | 0.9 | 1.05 | 0.06542 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | STFRANT3 | 0.9622 | 0.8982 | -0.064 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | GRANTTP3 | 1.01 | 0.8982 | -0.1118 |  | 0.9 | 1.05 | 0.09991 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | STFRANT3 | 0.9622 | 0.8982 | -0.064 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | GRANTTP3 | 1.01 | 0.8982 | -0.1118 |  | 0.9 | 1.05 | 0.0742 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | SCOTCTY3 | 0.9681 | 0.8984 | -0.0697 |  | 0.9 | 1.05 | 0.05101 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | SCOTCTY3 | 0.9681 | 0.8984 | -0.0697 |  | 0.9 | 1.05 | 0.04911 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | SCOTCTY3 | 0.9681 | 0.8984 | -0.0697 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | SCOTCTY3 | 0.9681 | 0.8984 | -0.0697 |  | 0.9 | 1.05 | 0.04272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | SCOTCTY3 | 0.9681 | 0.8984 | -0.0697 |  | 0.9 | 1.05 | 0.06272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | SCOTCTY3 | 0.9681 | 0.8984 | -0.0697 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | SCOTCTY3 | 0.9681 | 0.8984 | -0.0697 |  | 0.9 | 1.05 | 0.05049 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | SCOTCTY3 | 0.9681 | 0.8984 | -0.0697 |  | 0.9 | 1.05 | 0.05297 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | SCOTCTY3 | 0.9681 | 0.8984 | -0.0697 |  | 0.9 | 1.05 | 0.04447 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | SCOTCTY3 | 0.9681 | 0.8984 | -0.0697 |  | 0.9 | 1.05 | 0.04795 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | SCOTCTY3 | 0.9681 | 0.8984 | -0.0697 |  | 0.9 | 1.05 | 0.05827 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | SCOTCTY3 | 0.9681 | 0.8984 | -0.0697 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | SCOTCTY3 | 0.9681 | 0.8984 | -0.0697 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | SCOTCTY3 | 0.9681 | 0.8984 | -0.0697 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | SCOTCTY3 | 0.9681 | 0.8984 | -0.0697 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | SCOTCTY3 | 0.9681 | 0.8984 | -0.0697 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | SCOTCTY3 | 0.9681 | 0.8984 | -0.0697 |  | 0.9 | 1.05 | 0.04781 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | SCOTCTY3 | 0.9681 | 0.8984 | -0.0697 |  | 0.9 | 1.05 | 0.05112 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | SCOTCTY3 | 0.9681 | 0.8984 | -0.0697 |  | 0.9 | 1.05 | 0.03494 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | SCOTCTY3 | 0.9681 | 0.8984 | -0.0697 |  | 0.9 | 1.05 | 0.04759 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | SCOTCTY3 | 0.9681 | 0.8984 | -0.0697 |  | 0.9 | 1.05 | 0.05002 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | SCOTCTY3 | 0.9681 | 0.8984 | -0.0697 |  | 0.9 | 1.05 | 0.04842 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | SCOTCTY3 | 0.9681 | 0.8984 | -0.0697 |  | 0.9 | 1.05 | 0.05452 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | SCOTCTY3 | 0.9681 | 0.8984 | -0.0697 |  | 0.9 | 1.05 | 0.05387 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | SCOTCTY3 | 0.9681 | 0.8984 | -0.0697 |  | 0.9 | 1.05 | 0.03786 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | SCOTCTY3 | 0.9681 | 0.8984 | -0.0697 |  | 0.9 | 1.05 | 0.04954 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | SCOTCTY3 | 0.9681 | 0.8984 | -0.0697 |  | 0.9 | 1.05 | 0.04065 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | LIBERTY3 | 0.956 | 0.8985 | -0.0575 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | LIBERTY3 | 0.956 | 0.8985 | -0.0575 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | LIBERTY3 | 0.956 | 0.8985 | -0.0575 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | LIBERTY3 | 0.956 | 0.8985 | -0.0575 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | LIBERTY3 | 0.956 | 0.8985 | -0.0575 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | LIBERTY3 | 0.956 | 0.8985 | -0.0575 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | LIBERTY3 | 0.956 | 0.8985 | -0.0575 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | LIBERTY3 | 0.956 | 0.8985 | -0.0575 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | LIBERTY3 | 0.956 | 0.8985 | -0.0575 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | LIBERTY3 | 0.956 | 0.8985 | -0.0575 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | LIBERTY3 | 0.956 | 0.8985 | -0.0575 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | LIBERTY3 | 0.956 | 0.8985 | -0.0575 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | LIBERTY3 | 0.956 | 0.8985 | -0.0575 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | LIBERTY3 | 0.956 | 0.8985 | -0.0575 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | LIBERTY3 | 0.956 | 0.8985 | -0.0575 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | LIBERTY3 | 0.956 | 0.8985 | -0.0575 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | LIBERTY3 | 0.956 | 0.8985 | -0.0575 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | LIBERTY3 | 0.956 | 0.8985 | -0.0575 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | LIBERTY3 | 0.956 | 0.8985 | -0.0575 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | LIBERTY3 | 0.956 | 0.8985 | -0.0575 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | LIBERTY3 | 0.956 | 0.8985 | -0.0575 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | LIBERTY3 | 0.956 | 0.8985 | -0.0575 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | LIBERTY3 | 0.956 | 0.8985 | -0.0575 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | LIBERTY3 | 0.956 | 0.8985 | -0.0575 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | LIBERTY3 | 0.956 | 0.8985 | -0.0575 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | LIBERTY3 | 0.956 | 0.8985 | -0.0575 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | LIBERTY3 | 0.956 | 0.8985 | -0.0575 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | JAGGER 3 | 0.9774 | 0.8986 | -0.0788 |  | 0.9 | 1.05 | 0.05115 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.10463 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.10463 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | JAGGER 3 | 0.9774 | 0.8986 | -0.0788 |  | 0.9 | 1.05 | 0.04926 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.09917 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.09917 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | JAGGER 3 | 0.9774 | 0.8986 | -0.0788 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.09545 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | JAGGER 3 | 0.9774 | 0.8986 | -0.0788 |  | 0.9 | 1.05 | 0.04287 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.08062 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.08062 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | JAGGER 3 | 0.9774 | 0.8986 | -0.0788 |  | 0.9 | 1.05 | 0.06285 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.1436 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.1436 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | JAGGER 3 | 0.9774 | 0.8986 | -0.0788 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.09545 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | JAGGER 3 | 0.9774 | 0.8986 | -0.0788 |  | 0.9 | 1.05 | 0.05063 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.10316 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.10316 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | JAGGER 3 | 0.9774 | 0.8986 | -0.0788 |  | 0.9 | 1.05 | 0.05311 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.11116 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.11116 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | JAGGER 3 | 0.9774 | 0.8986 | -0.0788 |  | 0.9 | 1.05 | 0.04461 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.0814 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.0814 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | JAGGER 3 | 0.9774 | 0.8986 | -0.0788 |  | 0.9 | 1.05 | 0.0481 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.09616 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.09616 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | JAGGER 3 | 0.9774 | 0.8986 | -0.0788 |  | 0.9 | 1.05 | 0.0584 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.12853 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.12853 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | JAGGER 3 | 0.9774 | 0.8986 | -0.0788 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.09545 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | JAGGER 3 | 0.9774 | 0.8986 | -0.0788 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.09545 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | JAGGER 3 | 0.9774 | 0.8986 | -0.0788 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.09424 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.09424 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | JAGGER 3 | 0.9774 | 0.8986 | -0.0788 |  | 0.9 | 1.05 | 0.04752 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.09424 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.09424 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | JAGGER 3 | 0.9774 | 0.8986 | -0.0788 |  | 0.9 | 1.05 | 0.04791 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.09545 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | JAGGER 3 | 0.9774 | 0.8986 | -0.0788 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.09553 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.09553 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | JAGGER 3 | 0.9774 | 0.8986 | -0.0788 |  | 0.9 | 1.05 | 0.05126 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.10494 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.10494 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | JAGGER 3 | 0.9774 | 0.8986 | -0.0788 |  | 0.9 | 1.05 | 0.0351 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.0573 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.0573 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | JAGGER 3 | 0.9774 | 0.8986 | -0.0788 |  | 0.9 | 1.05 | 0.04774 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.0949 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.0949 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | JAGGER 3 | 0.9774 | 0.8986 | -0.0788 |  | 0.9 | 1.05 | 0.05016 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.10178 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.10178 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | JAGGER 3 | 0.9774 | 0.8986 | -0.0788 |  | 0.9 | 1.05 | 0.04857 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.09717 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.09717 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | JAGGER 3 | 0.9774 | 0.8986 | -0.0788 |  | 0.9 | 1.05 | 0.05466 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.11588 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.11588 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | JAGGER 3 | 0.9774 | 0.8986 | -0.0788 |  | 0.9 | 1.05 | 0.05401 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.11389 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.11389 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | JAGGER 3 | 0.9774 | 0.8986 | -0.0788 |  | 0.9 | 1.05 | 0.03802 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.06575 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.06575 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | JAGGER 3 | 0.9774 | 0.8986 | -0.0788 |  | 0.9 | 1.05 | 0.04968 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.10039 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.10039 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | JAGGER 3 | 0.9774 | 0.8986 | -0.0788 |  | 0.9 | 1.05 | 0.04081 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.07455 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | ROLLA 3 | 1.0023 | 0.8986 | -0.1037 |  | 0.9 | 1.05 | 0.07455 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.10463 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.10463 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.09917 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.09917 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.09545 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.08062 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.08062 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.1436 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.1436 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.09545 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.10316 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.10316 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.11116 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.11116 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.0814 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.0814 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.09616 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.09616 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.12853 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.12853 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.09545 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.09545 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.09424 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.09424 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.09424 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.09424 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.09545 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.09553 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.09553 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.10494 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.10494 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.0573 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.0573 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.0949 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.0949 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.10178 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.10178 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.09717 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.09717 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.11588 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.11588 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.11389 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.11389 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.06575 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.06575 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.10039 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.10039 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.07455 | P23:345:SUNC:HLC_BRK188:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | HUGOTON3 | 1.004 | 0.8987 | -0.1053 |  | 0.9 | 1.05 | 0.07455 | Potential P4 Event - POI 531449_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | LIBERTYT | 0.9601 | 0.8989 | -0.0612 |  | 0.9 | 1.05 | 0.05101 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | LIBERTYT | 0.9601 | 0.8989 | -0.0612 |  | 0.9 | 1.05 | 0.04911 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | LIBERTYT | 0.9601 | 0.8989 | -0.0612 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | LIBERTYT | 0.9601 | 0.8989 | -0.0612 |  | 0.9 | 1.05 | 0.04272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | LIBERTYT | 0.9601 | 0.8989 | -0.0612 |  | 0.9 | 1.05 | 0.06272 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | LIBERTYT | 0.9601 | 0.8989 | -0.0612 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | LIBERTYT | 0.9601 | 0.8989 | -0.0612 |  | 0.9 | 1.05 | 0.05049 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | LIBERTYT | 0.9601 | 0.8989 | -0.0612 |  | 0.9 | 1.05 | 0.05297 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | LIBERTYT | 0.9601 | 0.8989 | -0.0612 |  | 0.9 | 1.05 | 0.04447 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | LIBERTYT | 0.9601 | 0.8989 | -0.0612 |  | 0.9 | 1.05 | 0.04795 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | LIBERTYT | 0.9601 | 0.8989 | -0.0612 |  | 0.9 | 1.05 | 0.05827 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | LIBERTYT | 0.9601 | 0.8989 | -0.0612 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | LIBERTYT | 0.9601 | 0.8989 | -0.0612 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | LIBERTYT | 0.9601 | 0.8989 | -0.0612 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | LIBERTYT | 0.9601 | 0.8989 | -0.0612 |  | 0.9 | 1.05 | 0.04737 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | LIBERTYT | 0.9601 | 0.8989 | -0.0612 |  | 0.9 | 1.05 | 0.04776 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | LIBERTYT | 0.9601 | 0.8989 | -0.0612 |  | 0.9 | 1.05 | 0.04781 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | LIBERTYT | 0.9601 | 0.8989 | -0.0612 |  | 0.9 | 1.05 | 0.05112 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | LIBERTYT | 0.9601 | 0.8989 | -0.0612 |  | 0.9 | 1.05 | 0.03494 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | LIBERTYT | 0.9601 | 0.8989 | -0.0612 |  | 0.9 | 1.05 | 0.04759 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | LIBERTYT | 0.9601 | 0.8989 | -0.0612 |  | 0.9 | 1.05 | 0.05002 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | LIBERTYT | 0.9601 | 0.8989 | -0.0612 |  | 0.9 | 1.05 | 0.04842 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | LIBERTYT | 0.9601 | 0.8989 | -0.0612 |  | 0.9 | 1.05 | 0.05452 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | LIBERTYT | 0.9601 | 0.8989 | -0.0612 |  | 0.9 | 1.05 | 0.05387 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | LIBERTYT | 0.9601 | 0.8989 | -0.0612 |  | 0.9 | 1.05 | 0.03786 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | LIBERTYT | 0.9601 | 0.8989 | -0.0612 |  | 0.9 | 1.05 | 0.04954 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | LIBERTYT | 0.9601 | 0.8989 | -0.0612 |  | 0.9 | 1.05 | 0.04065 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | STFRAN 3 | 0.9618 | 0.8991 | -0.0627 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | STFRAN 3 | 0.9618 | 0.8991 | -0.0627 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | STFRAN 3 | 0.9618 | 0.8991 | -0.0627 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | STFRAN 3 | 0.9618 | 0.8991 | -0.0627 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | STFRAN 3 | 0.9618 | 0.8991 | -0.0627 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | STFRAN 3 | 0.9618 | 0.8991 | -0.0627 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | STFRAN 3 | 0.9618 | 0.8991 | -0.0627 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | STFRAN 3 | 0.9618 | 0.8991 | -0.0627 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | STFRAN 3 | 0.9618 | 0.8991 | -0.0627 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | STFRAN 3 | 0.9618 | 0.8991 | -0.0627 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | STFRAN 3 | 0.9618 | 0.8991 | -0.0627 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | STFRAN 3 | 0.9618 | 0.8991 | -0.0627 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | STFRAN 3 | 0.9618 | 0.8991 | -0.0627 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | STFRAN 3 | 0.9618 | 0.8991 | -0.0627 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | STFRAN 3 | 0.9618 | 0.8991 | -0.0627 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | STFRAN 3 | 0.9618 | 0.8991 | -0.0627 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | STFRAN 3 | 0.9618 | 0.8991 | -0.0627 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | STFRAN 3 | 0.9618 | 0.8991 | -0.0627 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | STFRAN 3 | 0.9618 | 0.8991 | -0.0627 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | STFRAN 3 | 0.9618 | 0.8991 | -0.0627 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | STFRAN 3 | 0.9618 | 0.8991 | -0.0627 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | STFRAN 3 | 0.9618 | 0.8991 | -0.0627 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | STFRAN 3 | 0.9618 | 0.8991 | -0.0627 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | STFRAN 3 | 0.9618 | 0.8991 | -0.0627 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | STFRAN 3 | 0.9618 | 0.8991 | -0.0627 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | STFRAN 3 | 0.9618 | 0.8991 | -0.0627 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | STFRAN 3 | 0.9618 | 0.8991 | -0.0627 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531465_1 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | KANARAD3 | 0.9653 | 0.8992 | -0.0661 |  | 0.9 | 1.05 | 0.05101 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | KANARAD3 | 0.9653 | 0.8992 | -0.0661 |  | 0.9 | 1.05 | 0.04911 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | KANARAD3 | 0.9653 | 0.8992 | -0.0661 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | KANARAD3 | 0.9653 | 0.8992 | -0.0661 |  | 0.9 | 1.05 | 0.04272 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | KANARAD3 | 0.9653 | 0.8992 | -0.0661 |  | 0.9 | 1.05 | 0.06272 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | KANARAD3 | 0.9653 | 0.8992 | -0.0661 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | KANARAD3 | 0.9653 | 0.8992 | -0.0661 |  | 0.9 | 1.05 | 0.05049 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | KANARAD3 | 0.9653 | 0.8992 | -0.0661 |  | 0.9 | 1.05 | 0.05297 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | KANARAD3 | 0.9653 | 0.8992 | -0.0661 |  | 0.9 | 1.05 | 0.04447 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | KANARAD3 | 0.9653 | 0.8992 | -0.0661 |  | 0.9 | 1.05 | 0.04795 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | KANARAD3 | 0.9653 | 0.8992 | -0.0661 |  | 0.9 | 1.05 | 0.05827 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | KANARAD3 | 0.9653 | 0.8992 | -0.0661 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | KANARAD3 | 0.9653 | 0.8992 | -0.0661 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | KANARAD3 | 0.9653 | 0.8992 | -0.0661 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | KANARAD3 | 0.9653 | 0.8992 | -0.0661 |  | 0.9 | 1.05 | 0.04737 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | KANARAD3 | 0.9653 | 0.8992 | -0.0661 |  | 0.9 | 1.05 | 0.04776 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | KANARAD3 | 0.9653 | 0.8992 | -0.0661 |  | 0.9 | 1.05 | 0.04781 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | KANARAD3 | 0.9653 | 0.8992 | -0.0661 |  | 0.9 | 1.05 | 0.05112 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | KANARAD3 | 0.9653 | 0.8992 | -0.0661 |  | 0.9 | 1.05 | 0.03494 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | KANARAD3 | 0.9653 | 0.8992 | -0.0661 |  | 0.9 | 1.05 | 0.04759 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | KANARAD3 | 0.9653 | 0.8992 | -0.0661 |  | 0.9 | 1.05 | 0.05002 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | KANARAD3 | 0.9653 | 0.8992 | -0.0661 |  | 0.9 | 1.05 | 0.04842 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | KANARAD3 | 0.9653 | 0.8992 | -0.0661 |  | 0.9 | 1.05 | 0.05452 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | KANARAD3 | 0.9653 | 0.8992 | -0.0661 |  | 0.9 | 1.05 | 0.05387 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | KANARAD3 | 0.9653 | 0.8992 | -0.0661 |  | 0.9 | 1.05 | 0.03786 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | KANARAD3 | 0.9653 | 0.8992 | -0.0661 |  | 0.9 | 1.05 | 0.04954 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | KANARAD3 | 0.9653 | 0.8992 | -0.0661 |  | 0.9 | 1.05 | 0.04065 | Potential P4 Event - POI 531449_4 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | GRANT 3 | 1.0101 | 0.8995 | -0.1106 |  | 0.9 | 1.05 | 0.10463 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | GRANT 3 | 1.0101 | 0.8995 | -0.1106 |  | 0.9 | 1.05 | 0.09917 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | GRANT 3 | 1.0101 | 0.8995 | -0.1106 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | GRANT 3 | 1.0101 | 0.8995 | -0.1106 |  | 0.9 | 1.05 | 0.08062 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | GRANT 3 | 1.0101 | 0.8995 | -0.1106 |  | 0.9 | 1.05 | 0.1436 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | GRANT 3 | 1.0101 | 0.8995 | -0.1106 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | GRANT 3 | 1.0101 | 0.8995 | -0.1106 |  | 0.9 | 1.05 | 0.10316 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | GRANT 3 | 1.0101 | 0.8995 | -0.1106 |  | 0.9 | 1.05 | 0.11116 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | GRANT 3 | 1.0101 | 0.8995 | -0.1106 |  | 0.9 | 1.05 | 0.0814 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | GRANT 3 | 1.0101 | 0.8995 | -0.1106 |  | 0.9 | 1.05 | 0.09616 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | GRANT 3 | 1.0101 | 0.8995 | -0.1106 |  | 0.9 | 1.05 | 0.12853 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | GRANT 3 | 1.0101 | 0.8995 | -0.1106 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | GRANT 3 | 1.0101 | 0.8995 | -0.1106 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | GRANT 3 | 1.0101 | 0.8995 | -0.1106 |  | 0.9 | 1.05 | 0.09424 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | GRANT 3 | 1.0101 | 0.8995 | -0.1106 |  | 0.9 | 1.05 | 0.09424 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | GRANT 3 | 1.0101 | 0.8995 | -0.1106 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | GRANT 3 | 1.0101 | 0.8995 | -0.1106 |  | 0.9 | 1.05 | 0.09553 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | GRANT 3 | 1.0101 | 0.8995 | -0.1106 |  | 0.9 | 1.05 | 0.10494 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | GRANT 3 | 1.0101 | 0.8995 | -0.1106 |  | 0.9 | 1.05 | 0.0573 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | GRANT 3 | 1.0101 | 0.8995 | -0.1106 |  | 0.9 | 1.05 | 0.0949 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | GRANT 3 | 1.0101 | 0.8995 | -0.1106 |  | 0.9 | 1.05 | 0.10178 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | GRANT 3 | 1.0101 | 0.8995 | -0.1106 |  | 0.9 | 1.05 | 0.09717 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | GRANT 3 | 1.0101 | 0.8995 | -0.1106 |  | 0.9 | 1.05 | 0.11588 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | GRANT 3 | 1.0101 | 0.8995 | -0.1106 |  | 0.9 | 1.05 | 0.11389 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | GRANT 3 | 1.0101 | 0.8995 | -0.1106 |  | 0.9 | 1.05 | 0.06575 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | GRANT 3 | 1.0101 | 0.8995 | -0.1106 |  | 0.9 | 1.05 | 0.10039 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | GRANT 3 | 1.0101 | 0.8995 | -0.1106 |  | 0.9 | 1.05 | 0.07455 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.10414 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.10414 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.0987 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.0987 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.08024 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.08024 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.14298 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.14298 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.10266 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.10266 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.11064 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.11064 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.08095 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.08095 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.09571 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.09571 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.12796 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.12796 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.09379 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.09379 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.09379 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.09379 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.09507 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.09507 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.10446 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.10446 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.05698 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.05698 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.09445 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.09445 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.10129 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.10129 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.0967 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.0967 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.11534 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.11534 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.11336 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.11336 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.06542 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.06542 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.09991 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.09991 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.0742 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | GRANT 3 | 1.0065 | 0.8996 | -0.1069 |  | 0.9 | 1.05 | 0.0742 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | ONEOK 3 | 0.971 | 0.8998 | -0.0712 |  | 0.9 | 1.05 | 0.05106 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | ASGI-2023-001 | GRANTTP3 | 1.0103 | 0.8998 | -0.1105 |  | 0.9 | 1.05 | 0.10463 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | ONEOK 3 | 0.971 | 0.8998 | -0.0712 |  | 0.9 | 1.05 | 0.04915 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-001 | GRANTTP3 | 1.0103 | 0.8998 | -0.1105 |  | 0.9 | 1.05 | 0.09917 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | ONEOK 3 | 0.971 | 0.8998 | -0.0712 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-005 | GRANTTP3 | 1.0103 | 0.8998 | -0.1105 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | ONEOK 3 | 0.971 | 0.8998 | -0.0712 |  | 0.9 | 1.05 | 0.0427 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-008 | GRANTTP3 | 1.0103 | 0.8998 | -0.1105 |  | 0.9 | 1.05 | 0.08062 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | ONEOK 3 | 0.971 | 0.8998 | -0.0712 |  | 0.9 | 1.05 | 0.06281 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-010 | GRANTTP3 | 1.0103 | 0.8998 | -0.1105 |  | 0.9 | 1.05 | 0.1436 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | ONEOK 3 | 0.971 | 0.8998 | -0.0712 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-060 | GRANTTP3 | 1.0103 | 0.8998 | -0.1105 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | ONEOK 3 | 0.971 | 0.8998 | -0.0712 |  | 0.9 | 1.05 | 0.05054 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-081 | GRANTTP3 | 1.0103 | 0.8998 | -0.1105 |  | 0.9 | 1.05 | 0.10316 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | ONEOK 3 | 0.971 | 0.8998 | -0.0712 |  | 0.9 | 1.05 | 0.05303 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-086 | GRANTTP3 | 1.0103 | 0.8998 | -0.1105 |  | 0.9 | 1.05 | 0.11116 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | ONEOK 3 | 0.971 | 0.8998 | -0.0712 |  | 0.9 | 1.05 | 0.04451 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-110 | GRANTTP3 | 1.0103 | 0.8998 | -0.1105 |  | 0.9 | 1.05 | 0.0814 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | ONEOK 3 | 0.971 | 0.8998 | -0.0712 |  | 0.9 | 1.05 | 0.04798 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-120 | GRANTTP3 | 1.0103 | 0.8998 | -0.1105 |  | 0.9 | 1.05 | 0.09616 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | ONEOK 3 | 0.971 | 0.8998 | -0.0712 |  | 0.9 | 1.05 | 0.05835 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-123 | GRANTTP3 | 1.0103 | 0.8998 | -0.1105 |  | 0.9 | 1.05 | 0.12853 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | ONEOK 3 | 0.971 | 0.8998 | -0.0712 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-142 | GRANTTP3 | 1.0103 | 0.8998 | -0.1105 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | ONEOK 3 | 0.971 | 0.8998 | -0.0712 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-143 | GRANTTP3 | 1.0103 | 0.8998 | -0.1105 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | ONEOK 3 | 0.971 | 0.8998 | -0.0712 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-158 | GRANTTP3 | 1.0103 | 0.8998 | -0.1105 |  | 0.9 | 1.05 | 0.09424 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | ONEOK 3 | 0.971 | 0.8998 | -0.0712 |  | 0.9 | 1.05 | 0.04739 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-159 | GRANTTP3 | 1.0103 | 0.8998 | -0.1105 |  | 0.9 | 1.05 | 0.09424 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | ONEOK 3 | 0.971 | 0.8998 | -0.0712 |  | 0.9 | 1.05 | 0.04778 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-176 | GRANTTP3 | 1.0103 | 0.8998 | -0.1105 |  | 0.9 | 1.05 | 0.09545 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | ONEOK 3 | 0.971 | 0.8998 | -0.0712 |  | 0.9 | 1.05 | 0.04783 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-178 | GRANTTP3 | 1.0103 | 0.8998 | -0.1105 |  | 0.9 | 1.05 | 0.09553 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | ONEOK 3 | 0.971 | 0.8998 | -0.0712 |  | 0.9 | 1.05 | 0.05118 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-184 | GRANTTP3 | 1.0103 | 0.8998 | -0.1105 |  | 0.9 | 1.05 | 0.10494 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | ONEOK 3 | 0.971 | 0.8998 | -0.0712 |  | 0.9 | 1.05 | 0.03488 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-188 | GRANTTP3 | 1.0103 | 0.8998 | -0.1105 |  | 0.9 | 1.05 | 0.0573 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | ONEOK 3 | 0.971 | 0.8998 | -0.0712 |  | 0.9 | 1.05 | 0.04762 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-195 | GRANTTP3 | 1.0103 | 0.8998 | -0.1105 |  | 0.9 | 1.05 | 0.0949 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | ONEOK 3 | 0.971 | 0.8998 | -0.0712 |  | 0.9 | 1.05 | 0.05006 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-201 | GRANTTP3 | 1.0103 | 0.8998 | -0.1105 |  | 0.9 | 1.05 | 0.10178 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | ONEOK 3 | 0.971 | 0.8998 | -0.0712 |  | 0.9 | 1.05 | 0.04845 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-203 | GRANTTP3 | 1.0103 | 0.8998 | -0.1105 |  | 0.9 | 1.05 | 0.09717 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | ONEOK 3 | 0.971 | 0.8998 | -0.0712 |  | 0.9 | 1.05 | 0.05459 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-208 | GRANTTP3 | 1.0103 | 0.8998 | -0.1105 |  | 0.9 | 1.05 | 0.11588 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | ONEOK 3 | 0.971 | 0.8998 | -0.0712 |  | 0.9 | 1.05 | 0.05393 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-209 | GRANTTP3 | 1.0103 | 0.8998 | -0.1105 |  | 0.9 | 1.05 | 0.11389 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | ONEOK 3 | 0.971 | 0.8998 | -0.0712 |  | 0.9 | 1.05 | 0.03782 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-228 | GRANTTP3 | 1.0103 | 0.8998 | -0.1105 |  | 0.9 | 1.05 | 0.06575 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | ONEOK 3 | 0.971 | 0.8998 | -0.0712 |  | 0.9 | 1.05 | 0.04958 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-236 | GRANTTP3 | 1.0103 | 0.8998 | -0.1105 |  | 0.9 | 1.05 | 0.10039 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | ONEOK 3 | 0.971 | 0.8998 | -0.0712 |  | 0.9 | 1.05 | 0.04062 | Potential P4 Event - POI 531465_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 27SP | GEN-2023-237 | GRANTTP3 | 1.0103 | 0.8998 | -0.1105 |  | 0.9 | 1.05 | 0.07455 | Potential P4 Event - POI 531449_2 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.10414 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | ASGI-2023-001 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.10414 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.0987 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-001 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.0987 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-005 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.08024 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-008 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.08024 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.14298 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-010 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.14298 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-060 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.10266 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-081 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.10266 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.11064 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-086 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.11064 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.08095 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-110 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.08095 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.09571 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-120 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.09571 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.12796 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-123 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.12796 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-142 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-143 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.09379 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-158 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.09379 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.09379 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-159 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.09379 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.095 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-176 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.095 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.09507 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-178 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.09507 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.10446 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-184 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.10446 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.05698 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-188 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.05698 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.09445 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-195 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.09445 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.10129 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-201 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.10129 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.0967 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-203 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.0967 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.11534 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-208 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.11534 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.11336 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-209 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.11336 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.06542 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-228 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.06542 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.09991 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-236 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.09991 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.0742 | P23:345:SUNC:HLC_BRK282:::EHV: | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 05ALL | 2 | 24SP | GEN-2023-237 | GRANTTP3 | 1.0068 | 0.8999 | -0.1069 |  | 0.9 | 1.05 | 0.0742 | Potential P4 Event - POI 531449_0 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
Voltage | DISIS-2023-001 | 00ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 | 00ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 | 00ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 | 04ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 | 04ALL | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 | 05ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 | 05ALL | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 | 00NR | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 | 00NR | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 | 00NR | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 | 04NR | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 | 05NR | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 CF | 00ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 CF | 00ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 CF | 00ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 CF | 04ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 CF | 04ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 CF | 04ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 CF | 04ALL | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 CF | 05ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 CF | 05ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 CF | 05ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 CF | 05ALL | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 CF | 00NR | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 CF | 00NR | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 CF | 00NR | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 CF | 04NR | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2023-001 CF | 05NR | 2 | 27L | N/A | None | [7 empty] | None | None

## Stability Analysis Results
Group | Study Name | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
01 NORTH | DISIS-2023-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_001 | 3 Phase fault on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV
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